## Sheet 2
Factory Name
Address
| Structural | Electrical | Fire
Inspection Date
Date Report Received

## Sheet1
Upload | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION SCOPE | Inspection Type | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | Item No | ACCORD INSPECTION OBSERVATION | Accord Action Plan | Accord Timeline | Final Action Plan | Final Timeline | Comments from Accord | Progress Status
Yes | 2 | 7 |  | 108 | 421 | 6 | 5 | 102422 | Accord Electrical Safety Inspection | Electrical | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | 1 | Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | 12 WEEKS
Yes | 2 | 7 |  | 109 | 421 | 6 | 5 | 102423 | Accord Electrical Safety Inspection | Electrical | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | 2 | Thermographic scanning of the entire electrical system has not been tested and recorded. | Thermographic scanning for the entire electrical system must be performed on a bi-annual basis and recorded. | 8 WEEKS
Yes | 2 | 7 |  | 110 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 3 | Insulation resistance test of electrical equipment is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | 8 WEEKS
Yes | 2 | 7 |  | 245 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 4 | Electrical safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personnel and staff must be initiated and recorded. | 8 WEEKS
Yes | 2 | 7 |  | 246 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 5 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this first aid and CPR instructions near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | 2 WEEKS
Yes | 2 | 7 |  | 247 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 6 | Accurate/detail maintenance records are unavailable. | Maintenance Manager or Safety Officer must keep accurate/detail records and ensure that they reflect actual factory day to day operations. | 2 WEEKS
Yes | 2 | 7 |  | 248 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 7 | Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test, this must be done twice a year and records kept. | 8 WEEKS
Yes | 2 | 7 |  | 249 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 8 | Lightning Protection System (LPS) is needed but has not been installed yet. | Design and install Lightning Protection System (LPS) in the factory; the LPS designs must be submitted to Accord before starting installation. | 16 WEEKS
Yes | 2 | 7 |  | 250 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 9 | Earth pit resistance record is unavailable. | Record earth pit resistances for all the earth pits, and do it once a year. | 8 WEEKS
Yes | 2 | 7 |  | 251 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 10 | Earth pits are not identifiable. | Clearly identify each earth pit, and mark it for periodic maintenance purposes. | 8 WEEKS
Yes | 2 | 7 |  | 252 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 11 | No separation between LT panels and HT units (transformer, HT switchgear). | Make a brick built separation between LT and HT units; ensure that after making separator you have adequate ventilation (cross ventilation) and working clearance around each electrical equipment. | 12 WEEKS
Yes | 2 | 7 |  | 253 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 12 | Lint and dust deposited on transformer top. | Ensure that transformer is always kept clean. | 4 WEEKS
Yes | 2 | 7 |  | 254 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 13 | Cable has inadequate support. | Provide vertical ladder to support cables. | 4 WEEKS
Yes | 2 | 7 |  | 255 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 14 | Transformer silica gel is discolored. | Replace silica gel by a new one; or dry it under sun and reuse it, if color regains. | 4 WEEKS
Yes | 2 | 7 |  | 256 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 15 | Transformer breather oil cup is empty. | Fill the transformer breather oil cup with transformer oil. | 4 WEEKS
Yes | 2 | 7 |  | 257 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 16 | Oil level in transformer oil tank is below minimum level. | Ensure minimum oil level in the oil level tank. Check this level periodically. | 2 WEEKS
Yes | 2 | 7 |  | 258 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 17 | Transformer Arcing horn has not been installed. | Install transformer arcing horn with proper alignment (keep at least a 2 inch gap between two horns). | 4 WEEKS
Yes | 2 | 7 |  | 259 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 18 | Buchholz relay has not been installed. | Install Buchholz relay if the transformer is over 1000 kVA. | 4 WEEKS
Yes | 2 | 7 |  | 260 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 19 | Inadequate working clearance around the generator/s. | Working clearance around each generator should be 1.07m. If multiple generators are installed then the gap between two generators must be equal to the width of bigger generator. | 12 WEEKS
Yes | 2 | 7 |  | 261 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 20 | Generator output cables (laid on floor) are not protected and supported. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. | 4 WEEKS
Yes | 2 | 7 |  | 262 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 21 | Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | 4 WEEKS
Yes | 2 | 7 |  | 263 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 22 | Batteries are kept on floor. | Use non-flammable case/shelf to store battery. | WEEKS
Yes | 2 | 7 |  | 264 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 23 | High earth loop impedance measured. | Reconnect wire and check the continuity of earthing wire (Until the value is within required level). | 4 WEEKS
Yes | 2 | 7 |  | 265 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 24 | Inappropriate temporary fan used for generator cooling purposes. | Stand/ceiling fans must not be used in generator room for cooling purposes; ensure there is adequate ventilation (cross ventilation) for the generator room, or if absolutely necessary appropriate industrial cooling system may be used. | 6 WEEKS
Yes | 2 | 7 |  | 266 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 25 | HT cables dropping from OH line, not supported to the pole. | HT cable dropping from HT pole must be firmly fixed to the pole with supports and clamps. | 4 WEEKS
Yes | 2 | 7 |  | 267 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 26 | Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables preventing any smoke form passing thorough the gap. | 6 WEEKS
Yes | 2 | 7 |  | 268 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 27 | HT service cable dropping from pole is not protected near the base of the pole, above ground level. | HT cable dropping from HT pole must be protected in steel pipe of required size at least 2m from the ground level to protect the cable from any physical damage. The cable should be supported on covered tray or ladder throughout its length up to the HT panel base-plate (except the part of the cable laid underground at a depth of at least 1 meter). | 6 WEEKS
Yes | 2 | 7 |  | 269 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 28 | Cable trench has excessive lint/dust. | Clean all the cable trenches. | 4 WEEKS
Yes | 2 | 7 |  | 270 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 29 | Power cables entering to or exiting Distribution board/panel are not properly fixed (Typical issue). | Power cables entering or exiting the distribution board/panel must be fixed through Panel base/top plate using cable glands (metal/PVC). Cable trays/ladders may be used to support the cables. | 6 WEEKS
Yes | 2 | 7 |  | 271 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 30 | BBT/cable duct installed very close to steam line. | BBT/cable duct installed near boiler steam lines must be protected from external heat and moisture. Keep atleast 0.9m distance. | 8 WEEKS
Yes | 2 | 7 |  | 272 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 31 | Drop out fuse is replaced by wire. | Install the drop out fuse. | 4 WEEKS
Yes | 2 | 7 |  | 273 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 32 | Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degrees. | 4 WEEKS
Yes | 2 | 7 |  | 274 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 33 | Cables inside distribution board is disorganized. | Organize all the power cables securely and neatly inside distribution board to prevent from electrical hazards. | 6 WEEKS
Yes | 2 | 7 |  | 275 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 34 | Three phase MCCB connected to control two phases or less. | Check and redesign the requirements to control the circuits. If three phase control is not required, then replace with suitable control devices. | 4 WEEKS
Yes | 2 | 7 |  | 276 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 35 | No identification and signs for electrical room including high voltage danger signs. | Provide identification and warning notice in front every electrical panel. Include voltage level on the notice and any precautions if required for special case. Put tags of identification of the circuits or machines on the respective circuit breaker. | 4 WEEKS
Yes | 2 | 7 |  | 277 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 36 | Protective device mounted on wall without enclosures. | Protective devices should be encased in metal casing made of 20 SWG thickness metal sheets. | 4 WEEKS
Yes | 2 | 7 |  | 278 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 37 | Distribution Board's top/bottom/rear is left open (typical issue). | Seal each distribution board's top/bottom/rear; and use cable glands holding/supporting cables. | 6 WEEKS
Yes | 2 | 7 |  | 279 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 38 | Distribution board/panel is filled with lint/dust. | Ensure inside distribution boards/panels are always kept clean. Seal them properly and ensure adequate ventilation. | 4 WEEKS
Yes | 2 | 7 |  | 280 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 39 | Wooden plank inside the panel. | Remove the wooden plank. | IMMEDIATE
Yes | 2 | 7 |  | 281 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 40 | Burn sign visible at terminal(s) inside panel. | Check the connected load and tighten connections. If required, replace the burnt cable/device. | IMMEDIATE
Yes | 2 | 7 |  | 282 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 41 | Cable insulation has deteriorated at the termination point. | Check the connected load and temperature. Insulate the cable properly. | IMMEDIATE
Yes | 2 | 7 |  | 283 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 42 | Changeover switch contacts smeared with bearing grease. | Clean excess grease from the contacts. Use thin layer of contact grease for lubricating. | 4 WEEKS
Yes | 2 | 7 |  | 284 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 43 | Distribution panel is too rusty. | Replace the rusty panel. | 6 WEEKS
Yes | 2 | 7 |  | 285 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 44 | Cables terminated at electrical busbar/MCCB without cable lugs. | Terminate all the power/earth/neutral cable with proper sized cable lug. | 4 WEEKS
Yes | 2 | 7 |  | 286 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 45 | Electrical panel placed under stair/beside entry/exit or walkway. | Electrical panel located below stairs/ beside entry/exit or walkway must be relocated to safe location. Every item of installation shall be arranged so as to facilitate its operation, maintenance & access. Keep the entry/exit/walkway free from panel. | 10 WEEKS
Yes | 2 | 7 |  | 287 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 46 | Protective device has not been fixed inside the panel. | All protective devices must be fixed inside the panel. | 4 WEEKS
Yes | 2 | 7 |  | 288 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 47 | Panel doors are not connected with earth. | All metal panel doors must have an earth connection of at least 4 rm earth cable. | 4 WEEKS
Yes | 2 | 7 |  | 289 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 48 | Distribution panel installed under the stair. | Panels located below stair must be relocated to safe place for ease of access to the panel during emergency. | 10 WEEKS
Yes | 2 | 7 |  | 290 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 49 | Loop connection is used to power multiple MCBs/MCCBs. | Eliminate loop cables; use a single cable for each MCBs/MCCBs. You may use busbar to avoid multiple termination. | 6 WEEKS
Yes | 2 | 7 |  | 291 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 50 | Multiple cables terminated at MCCB terminals/ busbar. | Terminate each power cable at single terminal and use proper sized cable lug. Multiple cables termination can be used if all are all soldered properly and powering a single circuit. | 6 WEEKS
Yes | 2 | 7 |  | 292 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 51 | Hot spots detected at termination point of protective devices. | Arrange periodic inspection & thermal scan to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. | IMMEDIATE
No | 2 | 7 |  | 293 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 52
No | 2 | 7 |  | 294 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 53
No | 2 | 7 |  | 295 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 54
No | 2 | 7 |  | 296 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 55
No | 2 | 7 |  | 297 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 56
No | 2 | 7 |  | 298 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 57
No | 2 | 7 |  | 299 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 58
No | 2 | 7 |  | 300 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 59
No | 2 | 7 |  | 301 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 60
No | 2 | 7 |  | 302 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 61
No | 2 | 7 |  | 303 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 62
No | 2 | 7 |  | 304 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 63
No | 2 | 7 |  | 305 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 64
No | 2 | 7 |  | 306 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 65
No | 2 | 7 |  | 307 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 66
No | 2 | 7 |  | 308 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 67
No | 2 | 7 |  | 309 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 68
No | 2 | 7 |  | 310 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 69
No | 2 | 7 |  | 311 | 421 | 6 | 5 |  | Accord Electrical Safety Inspection | Electrical | No |  |  | Essay response | Essay, bottomless text box |  |  |  |  | 70