## Structural
Date
30-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A J Super Garments Ltd., Aj Garden, Goshbag, Post- Zirabo, Thana - Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-03-23
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Live load has not been calculated for storage area (Bonded Warehouse) on Ground floor used for storage of fabric and other raw material. | Factory should engage an expert structural engineer to calculate actual live load for each critical section of the floor, particularly storage area and sewing section. Measured live load should be verified with the designed live load considering factor of safety. If it is overloaded, immediately excess live load from that part should be removed. | Corrected | Oct 5 2015 | On 09/11/2015: No load plan is required for bonded warehouse as it is situated in ground floor. On 08/03/2016: Corrected in previous follow up inspection. On 09/03/2017: Corrected in previous inspection. On 27/10/2017 : Corrected from previous inspection. No load plan is required for bonded warehouse as it is situated in ground floor. On 12/04/2018: Corrected from previous inspection. On 22/05/2019: This issue was corrected from previous inspection. Calculation of load plan does not required for ground floor. On 27-Sep-2021: Issue remains corrected. During inspection storage area found only at ground floor. Calculation of load plan does not require for ground floor. On 04-Oct-2022: This issue was corrected from previous inspection. On 16-Jan-2025: Corrected previously. | Jun 10 2014 | Corrected
Initial Inspection |  | 2 | Racks for accessories in accessories store on Ground floor are not anchored as per Alliance Standards Part 8 Section 8.18 Seismic Bracing of Key Non-Structural Elements and 2006 BNBC Part 6. | Adequately anchor and brace accessories rack systems to resist earthquake forces to comply with the BNBC and Alliance Standard. | Corrected | Oct 5 2015 | On 09/11/2015: The racks are anchored at the ground floor. On 08/03/2016: Racks in the ground floor is found well anchored during physical inspection. On 09/03/2017: Racks have been anchored at Ground floor level. On 27/09/2017 : Corrected from previous inspection. Racks has been found anchored at ground floor. On 12/04/2018: Corrected from previous inspection. On 22/05/2019: This issue was corrected from previous inspection. During inspection, racks were found anchored. On 27-Sep-2021: Racks were found adequately anchored. Issue remains corrected. On 04-Oct-2022: This issue was corrected from previous inspection. Racks were found adequately anchored. On 16-Jan-2025: Corrected previously. Storage racks were found adequately anchored. | Jun 10 2014 | Corrected
Initial Inspection |  | 3 | Fabrics in ground floor area should be kept as per load plan as per 2006 BNBC Part 6 Chapter 1 Section 1.4.6 and Alliance Standard Part 13 Section 13.7 and Part 8 Section 8.9. | Develop a program to ensure that all live loads for which a floor or roof has been designed for will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Corrected | Oct 5 2015 | On 09/11/2015: There is no requirement of load plan at ground floor. Furthermore loading was in acceptable limit in ground floor of building. On 08/03/2016: Corrected in 1st follow up inspection. On 09/03/2017: Corrected in 1st follow up inspection. On 27/09/2017 : Corrected in 1st follow up inspection. There is no requirement of load plan at ground floor. Furthermore loading was in accepted limit in ground floor of building. On 12/04/2018: Corrected from previous inspection. During inspection live load was observed below allowable limit. Load manager was also present during inspection. On 22/05/2019: This issue was corrected from previous inspection. Calculation of load plan does not required for ground floor. On 27-Sep-2021: Dedicated load manager has been appointed to maintain floor loading. Issue remains corrected. On 04-Oct-2022: This issue was corrected from previous inspection. On 16-Jan-2025: Corrected previously. During inspection, loading was found within the limit (63 psf). The load plan was posted on each floor. | Jun 10 2014 | Corrected
Initial Inspection |  | 4 | A concentrated load of materials (fabrics) are piled up in the storage area in ground floor and no live load has been calculated or posted. | Engage a qualified structural engineer to confirm and document that appropriate provisions have been made to accommodate concentrated loads in the storage area (although on ground floor, there may be question regarding quality of castings). If appropriate provisions have not been made, have a qualified structural engineer develop a remediation plan. | Corrected | Oct 5 2015 | On 09/11/2015: No load plan is required for piled fabrics as it is situated in ground floor. On 08/03/2016: Corrected in 1st follow up inspection. On 09/03/2017: Corrected in 1st follow up inspection. On 27/09/2017 : Corrected in 1st follow up inspection. No load plan is required for piled fabrics as it is situated in ground floor. On 12/04/2018: Corrected from previous inspection. On 22/05/2019: This issue was corrected from previous inspection. Calculation of load plan does not required for ground floor. On 27-Sep-2021: Issue remains corrected On 04-Oct-2022: This issue was corrected from previous inspection. On 16-Jan-2025: Corrected previously. | Jun 10 2014 | Corrected
Initial Inspection |  | 5 | Water ponding in roof top of north side stair case therefor not in compliance with Alliance Standard Part 8 Section 8.26 Durability and Maintenance. Additionally, exposed rebar was observed in 11 columns on roof top & in two beam in west exterior. | Remove ponded water from rooftop. As noted elsewhere, install roof drainage system and proper roof slope to prevent water from ponding on roof. | Corrected | Oct 5 2015 | On 09/11/2015: No water ponding has been observed at the time of inspection on north side staircase. Furthermore no exposed rebar was observed on columns and beams at west corner of building. On 08/03/2016: No water ponding observed during inspection. Corrected in 1st follow up inspection. On 09/03/2017: Corrected in 1st follow up inspection. No water ponding observed during inspection. On 27/09/2017 : Corrected from previous inspection. During inspection, proper drainage was observed and no water ponding was found. On 12/04/2018: Corrected from previous inspection. On 22/05/2019: This issue was corrected from previous inspection. During inspection, water ponding at roof and exposed re-bar was not found. On 27-Sep-2021: No exposed rebar was found. Also no water ponding at roof has been observed. On 04-Oct-2022: This issue was corrected from previous inspection. During inspection no water ponding was found at roof, also no exposed rebar also found. On 16-Jan-2025: Corrected previously. During the inspection, no water ponding and exposed re-bar were found. | Jun 23 2014 | Corrected
Initial Inspection |  | 6 | Load Manager is not present. Load Manager should be required for load planning properly in every floor as per Alliance Standards Part 8 Section 8.9 Factory Load Manager. | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to factory and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | Corrected | Oct 5 2015 | On 09/11/2015: Load manager has been appointed to take care the sustainable load on floors. On 08/03/2016: Load manager has been appointed and maintain operational load. Corrected in 1st follow up inspection. On 09/03/2017: Load manager has been appointed. During inspection load manager was present at Factory. On 27/10/2017 : Corrected from previous inspection. Load manager has been appointed. During inspection load manager was present at Factory. On 12/04/2018: Corrected from previous inspection. Load manager has been appointed and he was present during inspection. On 22/05/2019: This issue was corrected from previous inspection. A designated load manager has been appointed. On 27-Sep-2021: Dedicated load manager has been appointed to maintain floor loading. Issue remains corrected. On 04-Oct-2022: This issue was corrected from previous inspection. Dedicated load manager has been appointed to maintain floor loading. On 16-Jan-2025: Corrected previously. | May 27 2014 | Corrected
Initial Inspection |  | 7 | Load Plans have not been prepared for each floor documenting the actual maximum operational loading that is intended and/or allowable on each floor as per Reference Alliance Standards Part 8 Structural Design Section 8.10 Floor Loading Plans (Load Plans). | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3 | Corrected | Oct 5 2015 | On 09/11/2015: Load plan was prepared and it was posted on each floors of building .But the load plan has not got approval from Alliance. On 08/03/2016: During inspection load plan observed in every floor which was not approved by Alliance. Structural design review comment was sent from Alliance on 08 March 2016 but revised report is not submitted to Alliance yet. On 09/03/2017: Load plan was produced and got acceptance along with Design report from Alliance. During inspection load plan was found posted on floor. Posted load plan shows 63 psf for cutting section whereas provided load plan shows 42 psf. It couldn't be verified due to unavailability of original documents. On 27/09/2017 : Load plan has been prepared as a part of design report which was accepted by Alliance on 8th March 2016. During inspection, some discrepancy has been observed in as built drawing. Factory is required to revise design report as per verification report. On 12/04/2018: This issue is required to be covered in DEA. Factory was required to submit revised DEA to Alliance as per DEA verification but till the inspection date factory has not submitted the revised DEA to Alliance yet. Factory is required to submit revised DEA to Alliance as soon as possible. On 22/05/2019: Load plan was produced as part of DEA which was accepted by Alliance on 8th March 2016. During verification inspection by ACCORD on 27th September 2017, some mismatch was found in between as built drawing and actual site condition. Later, DEA of the factory building was re-accepted by Alliance on 12th June 2018 as per discrepancy of 4th RVV done by Alliance. But the re-accepted documents did not cover the discrepancy report issued from ACCORD. Still mismatch was found in between revised documents and actual site condition as per ACCORD discrepancy report. Now factory is required to submit revised DEA to ACCORD within 10 days from receiving the report. During inspection, load plan was found posted in each of the floor and loading was found within allowable limit of posted load plan (42 psf). On 27-Sep-2021: A set of load plans was prepared along with DEA which was accepted from ALLIANCE on 8th March 2016. Factory submitted revised DEA documents to RSC as per DEA verification report and a review comments mail was sent on 9th June 2021. Factory is required to submit the revised documents to RSC as per review mail within 26th July 2021 which has not been submitted yet. During inspection, floor loading was found below 42psf and load plans were found posted. Factory is required to maintain the final load plan after DEA acceptance with required remediation (if necessary). On 04-Oct-2022: Load plan was produced as part of DEA which was accepted by Alliance on 8th March 2016. During verification inspection by ACCORD on 27th September 2017, some mismatch was found in between as built drawing and actual site condition. After that factory has revised the drawing and DEA report as per site condition and submitted to RSC, which was again reviewed and accepted from RSC on 6th July 2022. As per Accepted DEA some retrofitting is required. During inspection retrofitting was found ongoing where remediation timeline is January 31, 2023. Load was found below 42 psf at all floor. Factory is required to maintain the final load plan after completion of remediation work. On 16-Jan-2025: During the inspection, it was found that the factory completed all remediation works as per accepted DEA, except two columns (grid A/8, A/9 on the first floor). Later factory completed the remediation works for the mentioned two columns and sent pictorial evidence, which was found satisfactory. Also, the remediation work completion certificate and material test reports were found onsite. However, loading was found within the limit (63 psf). The load plan was posted on each floor. | Jun 10 2014 | Corrected
Initial Inspection |  | 8 | Assessment team did not see any load plan anywhere in the building as per Alliance Standard Part 8 Section 8.20.5.3. | As noted elsewhere, have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. For each section of a floor, live load should be posted in the adjacent column, particularly for the critical sections. | Corrected | Oct 5 2015 | On 09/11/2015: Load plan was prepared and it was posted on each floors of building but the load plan has not got any approval from Alliance. Loading condition was in acceptable limit except at 1st floor where there was stack of fabrics touching celling height On 08/03/2016: During inspection load plan observed in every floor which was not approved by Alliance. Factory engineer must prepared a safe load plan as per Alliance standard. Floor load on 5th floor is observed more than 42 psf. On 09/03/2017: Load plan was produced and got acceptance along with Design report from Alliance. During inspection load plan was found posted on floor. Posted load plan shows 63 psf for cutting section whereas provided load plan shows 42 psf. It couldn't be verified due to unavailability of original documents. However, floor live loads were found less than 42 psf at suspended floors in the time of inspection. On 27/09/2017 : Load plan has been prepared as a part of design report which was accepted by Alliance on 8th March 2016. During inspection, some discrepancy has been observed in as built drawing. Factory is required to revise design report as per verification report. On 12/04/2018: During inspection load plan was found posted at every floor and load was observed within allowable limit. However, final load plan will be followed after getting re-acceptance of DEA from Alliance. On 22/05/2019: Load plan was produced as part of DEA which was accepted by Alliance on 8th March 2016. During verification inspection by ACCORD on 27th September 2017, some mismatch was found in between as built drawing and actual site condition. Later, DEA of the factory building was re-accepted by Alliance on 12th June 2018 as per discrepancy of 4th RVV done by Alliance. But the re-accepted documents did not cover the discrepancy report issued from ACCORD. Still mismatch was found in between revised documents and actual site condition as per ACCORD discrepancy report. Now factory is required to submit revised DEA to ACCORD within 10 days from receiving the report. During inspection, load plan was found posted in each of the floor and loading was found within allowable limit of posted load plan (42 psf). On 27-Sep-2021: DEA was accepted from ALLIANCE on 8th March 2016. However, Factory submitted revised DEA documents to RSC as per DEA verification report and a review comments mail was sent on 9th June 2021. Factory is required to submit the revised documents to RSC as per review mail within 26th July 2021 which has not been submitted yet. On 04-Oct-2022: Load plan was produced as part of DEA which was accepted by Alliance on 8th March 2016. During verification inspection by ACCORD on 27th September 2017, some mismatch was found in between as built drawing and actual site condition. After that factory has revised the drawing and DEA report as per site condition and submitted to RSC, which was again reviewed and accepted from RSC on 6th July 2022. As per Accepted DEA some retrofitting is required. During inspection retrofitting was found ongoing where remediation timeline is January 31, 2023. Load was found below 42 psf at all floor. Factory is required to maintain the final load plan after completion of remediation work. On 16-Jan-2025: During the inspection, it was found that the factory completed all remediation works as per accepted DEA, except two columns (grid A/8, A/9 on the first floor). Later factory completed the remediation works for the mentioned two columns and sent pictorial evidence, which was found satisfactory. Also, the remediation work completion certificate and material test reports were found onsite. However, loading was found within the limit (63 psf). The load plan was posted on each floor. | Jun 10 2014 | Corrected
Initial Inspection |  | 9 | Assessment team did not observe any load plans posted as per Reference Alliance Standards Part 8 Structural Design Section 8.11 Floor Load Markings. | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Corrected | Oct 5 2015 | On 09/11/2015: Load plan was prepared and it was posted on each floors of building but the load plan has not got any approval from Alliance. Loading condition was in acceptable limit except at 1st floor where there was stack of fabrics touching celling height. On 08/03/2016: During inspection signage has been observed on column and wall for every floor but that was not appropriate. Double marking was found in some areas. On 09/03/2017: Load plan was produced and got acceptance along with Design report from Alliance. During inspection load plan was found posted on floor. Posted load plan shows 63 psf for cutting section whereas provided load plan shows 42 psf. It couldn't be verified due to unavailability of original documents. However, floor live loads were found less than 42 psf at suspended floors in the time of inspection. Height marking has been provided on storage areas. On 27/09/2017 : Load plan has been prepared as a part of design report which was accepted by Alliance on 8th March 2016. Factory provided signage for acceptable loading limit at storage area. During inspection, some discrepancy has been observed in as built drawing. Factory is required to revise design report as per verification report. On 12/04/2018: During inspection load marking was observed in the storage areas. However, final load marking will be followed after getting re-acceptance of DEA from Alliance. On 22/05/2019: Load marking was found at storage area and loading was found within allowable limit of accepted load plan(42psf). Final load marking is required to be provided as per final load plan. On 27-Sep-2021: Floor loading was found below 42psf and load plans were found posted in each floor. However, load height markings were provided in the storage area. After DEA acceptance, factory is required to maintain final load plan after completing remediation (if required). On 04-Oct-2022: Load plan was produced as part of DEA which was accepted by Alliance on 8th March 2016. During verification inspection by ACCORD on 27th September 2017, some mismatch was found in between as built drawing and actual site condition. After that factory has revised the drawing and DEA report as per site condition and submitted to RSC, which was again reviewed and accepted from RSC on 6th July 2022. As per Accepted DEA some retrofitting is required. During inspection retrofitting was found ongoing where remediation timeline is January 31, 2023. Load was found below 42 psf at all floor. Factory is required to maintain the final load plan after completion of remediation work. On 16-Jan-2025: During the inspection, it was found that the factory completed all remediation work as per the accepted DEA, except for two columns (grid A/8, A/9 on the first floor). Later the factory completed the remediation work for the mentioned two columns and sent pictorial evidence, which was found satisfactory. Also, the remediation work completion certificate and material test reports were found onsite. However, loading limit marking was found in the storage areas. | Jun 10 2014 | Corrected
Follow Up Inspection |  | 10 | New finding 01: Newly constructed Jhut building found at factory premises. | Factory engineer is required to produce as built drawing and design report for Jhut building | Corrected (EA Report Accepted from RSC on 30.04.2025 ) | Nov 28 2022 | On 04-Oct-2022: During inspection, newly constructed 6 storied Jhut building found adjacent to the main building. Factory is required produce design report and as built drawing and submit to RSC for review. On 16-Jan-2025: This issue is required to be covered in the EA report. As per the last review comments, the factory is required to submit the revised EA to RSC. RPO Comments: On 01-May-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 11 | New finding 02: Newly constructed Jhut building found at factory premises. | Have a qualified structural engineer develop Floor Loading Plans as per the requirements | Corrected (EA Report Accepted from RSC on 30.04.2025 ) | Nov 28 2022 | On 04-Oct-2022: Factory engineer is required to produce load plan as part of design report and submit to RSC for review. During inspection, load was found below 42 psf. On 16-Jan-2025: Factory prepared a load plan as part of EA. As per the last review comments, the factory is required to submit the revised EA to RSC. However during inspection loading was found within 63 psf. RPO Comments: On 01-May-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 12 | New finding 03: Newly constructed boiler room found at factory premises. | Factory engineer is required to produce as built drawing | Corrected | Nov 28 2022 | On 04-Oct-2022: Factory engineer is required to produce as built drawing for boiler room and submit to RSC for review. On 16-Jan-2025: Factory prepared a set of as-built drawings for the boiler room which found matched with the site condition. | (within 6 weeks) | Corrected

## Fire
Date
30-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A J Super Garments Ltd., Aj Garden, Goshbag, Post- Zirabo, Thana - Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-03-23
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Exterior exit stairs are not compliant with Alliance Standard Part 6 Section 6.3.1.2. Exterior stair (North) discharges next to Fusing room. The Fusing room is not fire rated and it is less than 3 ft from stair discharge. | Provide a fire-resistive rated assembly between the exterior exit stairs and the building to achieve the required separation. The rating of the exterior wall shall extend 3.05 m (10 ft) beyond the ends of the stair structure. A fire rated door assembly (1.5-hr fire-resistance rating) will be required for fusing room door exit. The rated assembly should be approved and/or designed by a qualified fire protection engineer. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected as per previous follow up inspection. On 08/06/2017: Corrected as per previous follow up inspection. On 31/07/2017: Corrected as per previous follow-up. On 28/01/2018: Corrected as per previous follow-up. On 12/07/2018: Corrected as per previous follow up. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 2 | All doors in a means of egress are in violation of Alliance Standards Part 6 Section 6.8 Doors and Gates. All exit doors are sliding type doors. | Remove all collapsible gates at the exit stairs and along all portions of the means of egress. Replace with side-hinged swinging type doors in compliance with Standard (see other actions regarding fire rated door assemblies). | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected. Factory has removed non-compliant doors/gates from egress routes. On 12/07/2018: Corrected On 15/04/2019: Corrected. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 3 | Doors have locks which are not in compliance with Alliance Standards Part 6 Section 6.8 Doors and Gates | Remove all locking devices form all doors to exits / means of egress. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | corrected | Mar 15 2016 | On 08/03/2016: Partially corrected. Still locking features are available on north exit stair discharge path. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected. During follow up inspection non-compliant locking features were not found in egress routes exit doors/gates. On 12/07/2018: Corrected. On 15/04/2019: Corrected. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 4 | Exit enclosures are not provided with fire-resistive rated construction barriers Alliance Standards Part 4 Section 4.5 Separation. Exits are not protected by fire doors. Factory has a horizontal exit with open air bridge between Main and Annex building. No fire rated doors are provided as per BNBC Part 4 3.12. In east stairwell adjacent east window of factory floor is not fire protected. | Factory will need to install fire rated door assemblies at all exits (1.5 hour rating). Fire doors assemblies shall conform to NFPA 252, BS 476 Part 22, EN 1364-1, GB 12955-2008, or IS 3614. Part II. Doors must remain in closed position or be of self-closing type. Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. For the horizontal exit, door should be self closing and have two leaves opening in opposite directions. In east stairwell, the building exterior walls within 3050 mm (10 ft) horizontally of the unprotected openings (windows) should be constructed to have a fire-resistance rating of not less than 1 hr and openings within such exterior walls (such as windows) shall be protected by opening protectives having a fire protection rating of not less than ¾ hr. Factory can install fire rated windows or seal openings in exterior wall. Unprotected openings in stairwells may be sealed to assure continuous fire rating of exit enclosure. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. Factory has installed fire rated door at exit stair. On 09/03/2017: Corrected. Fire door installation is completed for all stair exit but interfacing is not completed yet. On 08/06/2017: Corrected. Fire door installation is completed for all stair exit but interfacing is not completed yet. On 12/07/2018: Corrected. Note: Installation of fire door is completed but interfacing work is still going on. Door accessories (magnetic holder, door coordinator etc) were found missing or non functional in almost every door. On 15/04/2019: Corrected as per previous follow up. Note: Horizontal exit bridge between main building & annex building not protected from non rated windows. Factory shall install fire rated windows or seal the windows or provide a rated horizontal exit way. On 04/10/2022: Corrected as per previous FUI. Refer to the issue no-35. On 28-Jan-25: Refer to Cap-40. On 21-Aug-25: Refer to Cap 40. | Jun 3 2014 | Corrected
Initial Inspection |  | 5 | Other than manual submersible pump to lift water from deep tubewell to overhead tank, there is no fire pump for the standpipe system. | Revise existing standpipe system to include a rated fire pump evaluated against requirements of NFPA 20 by a qualified fire engineer. All valves controlling fire pumps systems shall be electrically supervised by fire alarm system control unit. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected as per previous follow up inspection. On 08/06/2017: Corrected as per previous follow up inspection. On 12/07/2018: Corrected. On 15/04/2019: Corrected. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | May 23 2014 | Corrected
Initial Inspection |  | 6 | The factory has only a manual alarm system with single point smoke detectors installed. An automatic fire alarm and detection system shall be provided throughout all existing moderate hazard industrial occupancies per Alliance Standard 5.7.3.6 (An automatic fire alarm and detection system shall be provided throughout all new and existing moderate hazard industrial occupancies). | Replace the single-station smoke alarms with automatic smoke detectors tied into an automatic fire alarm system located in accordance with NFPA 72. Configure the fire alarm system to initiate occupant notification upon activation of any smoke detectors in addition to the manual fire alarm stations. Detectors should be placed in accordance with requirements of NFPA. | Corrected | Mar 15 2016 | On 08/06/2017: Partially corrected. Reviewed drawing was available during 3rd follow-up inspection. Installation was almost completed. Fire doors, HVAC system, fire pump controls should be interfaced with FACP if applicable. Factory have to prove whether the installed fire alarm cable has been certified by any third party or not. On 31/07/2017: Interfacing works are still pending. The factory shall provide proper certificate for the fire alarm cable. On 28/01/2018: Fire alarm system drawing has been reviewed by Alliance. Still interfacing works is pending. On 12/07/2018: Reviewed drawings by Alliance were present on site. Installation of panel is completed. Interfacing work is still going on. On 15/04/2019: Reportedly, installation is complete. It was advised to submit T&C documents to Accord prior to T&C VI if T&C done by contractor. Moreover, fire door interfaced with FACP not completed. As built drawing not match with FACP. On 04/10/2022: Fire alarm and detection system installation has been completed (reportedly). Factory shall apply for T&CVI immediately. On 28-Jan-25: Factory submitted design and documents of FADS to RSC for Pre T&CVI on 20-Jan-2025, which is currently under "Desk based Documentation review". Panel was found active and normal during inspection. On 21-Aug-25: Pre T&CVI found that the system is not corrected. For details see the Pre T&CVI report. | Jun 3 2014 | In Progress
Initial Inspection |  | 7 | East exit stair discharges into unprotected interior area in violation of Alliance Standard Part 6 Section 6.14 Exit Enclosures | Provide a rated exit passageway between stairs and final exit discharge. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected as per previous follow-up. On 28/01/2018: Corrected as per previous follow up. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 8 | The fire alarm and detection system is not monitored by a central station monitoring service or directly connected to the Fire Service and Civil Defense as per Alliance Standard Part 5 Section 5.7.5 Monitoring. System is manual alarm system that is not actively monitored. | As noted elsewhere, factory should install automatic fire detection system. Arrange for direct connection of the fire alarm and detection system to a central station monitoring service or the Fire Service and Civil Defense as per Alliance Standard Part 5 Section 5.7.5 Monitoring. Until that time that a central station monitoring service or direct connection to the Fire Service and Civil Defence can be set up, a person shall be assigned to contact the fire department in the event of fire alarm activation. An annunciator shall be located in a constantly attended location to alert this person. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. (not applicable) On 09/03/2017: Corrected. (not applicable) On 08/06/2017: Corrected. (not applicable) On 31/07/2017: Not applicable. On 28/01/2018: Corrected as per previous follow up. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected. On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 9 | Handrails are provided on only one side of stairwell in violation of Alliance Standard Part 6 Section 6.9 Stairs and 6.12 Handrails and Guards | Handrails shall be provided on both sides of each exit stairway. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 10 | No loads are posted as per Alliance Standards Part 6 Section 6.4.4 Posting of Occupant Load | Post maximum occupant load for all areas (near exit) | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. Occupant load shall be posted in all required places. On 28/01/2018: Corrected as per previous follow up. On 12/07/2018: Corrected. On 15/04/2019: Issue refer to SL no 36. On 04/10/2022: Corrected. On 28-Jan-25: Refer to Cap-36. On 21-Aug-25: Refer to Cap-36. | May 6 2014 | Corrected
Initial Inspection |  | 11 | No fire department connection was available for fire hose system (only Class II connections were available). | Fire department (Siamese) inlet connections shall be provided to allow fire department pumper equipment to supplement the fire protection systems. Connections shall match the Fire Service and Civil Defence hose thread standard. Install identifications for fire department connections as per NFPA 14 (e.g. sign on Fire Department connection indicating STANDPIPE in 1 in lettering, etc and noted as fire department connection.) | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected as per previous follow-ups. On 28/01/2018: Corrected as per previous follow up. Note: It is an integrated part of standpipe system. On 12/07/2018: Corrected. It is an integrated part of standpipe system. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected. On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 12 | Boiler room does not meet requirement for 1-hour rated construction. No fire rated door assembly is present and other unprotected penetrations (windows) are present per Alliance Standards Part 4 Section 4.5. Transformer is located in same room with generator. | A room housing boilers shall be separated from other occupancies by minimum 1 hour construction. Install appropriate 1-hour fire rated door assembly. Seal and/or protect all openings including windows to maintain the required fire separations. Consult a qualified fire protection engineer to design the required rated construction barrier. Oil filled transformers for non high-rise buildings shall be separated by a minimum 2 hour fire resistive rated construction. Consult a qualified fire protection engineer to design the required rated construction barrier. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected. On 12/07/2018: Corrected. On 15/04/2019: Corrected. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 13 | Illuminated exit signs are not placed at exit stairs per Alliance Standard Part 6 Section 6.11 Exit Signs. However, continuation of egress is not obvious in certain exits, e.g. east side ground floor. Occupants may be confused. | Install Illuminated exit signs at entrances to exits and along the path of egress anywhere the continuation of egress is not obvious (e.g. east side ground floor) or there is a change in the direction of the path of travel. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected. On 12/07/2018: Corrected. On 15/04/2019: Corrected. On 04/10/2022: Refer to the issue no-28. On 21-Aug-25: Refer to the issue no-28. | May 23 2014 | Corrected
Initial Inspection |  | 14 | Storage was observed under cutting table in Annex building 4th floor. | Storage underneath the cutting tables shall be kept clear of combustibles at all time as per Alliance Standard Part 17 Section 13.7.2 Cutting tables. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected. On 12/07/2018: Corrected. On 15/04/2019: Corrected. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | May 6 2014 | Corrected
Initial Inspection |  | 15 | Emergency lighting was provided for all paths of egress, however, no testing or certifying means for conformance to lighting standard (10 lux). | Confirm through testing (light meter) or other certification that means of egress will have illumination of 10 lux for all corridors, exit doors, and stairways and 2.5 lux for all aisles. Illumination should last no less than 30 min in the event of failure of normal lighting. | Corrected | Mar 15 2016 | On 08/03/2016: Partially corrected. Still requires more emergency lights at each floor. Final CAP Timeline: Expired. Committed Timeline: 10-April-16. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 12/07/2018: Corrected. On 15/04/2019: Corrected. Note: Factory shall provide emergency light at store area. On 04/10/2022: Refer to the issue no-28. On 21-Aug-25: Refer to the issue no-28. | Apr 23 2014 | Corrected
Initial Inspection |  | 16 | In 3rd floor, horizontal exit (connecting steel passage between main building and Annex building) has higher slope than permitted by Alliance Standard Part 6 Section 6.3.4 Walking Surfaces. | Adjust horizontal exit configuration to meet requirement of Alliance Standard Part 6 Section 6.3.4 Walking Surfaces (beveled slope of 1 in 2 that does not exceed 12.7 mm) and BNBC Part 4 3.12.4 (no steps in horizontal exit and slope should not exceed 1 vertical in 10 horizontal). | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. Fire door has been installed at those areas. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected as per previous follow up. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 23 2014 | Corrected
Initial Inspection |  | 17 | Re-entry requirements have not been met per Alliance Standards Part 6 Section 6.8.3.1 as fire rated door assemblies with proper latching systems have not been installed. As noted in other areas, fire rated door assemblies are required for the exit enclosure. | During installation of fire rated door assemblies assure that every door in a stair enclosure serving more than 4 stories is provided with re-entry unless it meets the requirements of Alliance Standards Part 6 Section 6.8.3.1. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected as per previous follow up. Note: Factory shall post re-entry sign at all required locations. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 18 | Signs indicating floor level are posted adjacent to the door, however, stairs have not been designated. | Each stair should be designated with a unique identification (e.g. Stairwell 1). Signs indicate the name of the stair and the floor level in English and Bangla. Additionally, stair signs should indicate if there is or is not roof access from the named stair. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected as per previous follow up. Note: Factory shall update stair designation sign. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | May 6 2014 | Corrected
Initial Inspection |  | 19 | Valves and valve cabinets do not have labeling or signage. No Hydraulic design information sign is available. | Assure signage and labeling for all standpipe system components is per NFPA 14 Chapter 6. Including: identification of all valves with indication of what service they control, valve cabinets should be marked to include their contents, signs indicating the hydraulic design (e.g. location of most remote hose connections, design flow rate, inlet and outlet pressure, and design static pressure) | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected as per previous follow-up. On 28/01/2018: Corrected as per previous follow up. Note: It is an integrated part of standpipe system. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Initial Inspection |  | 20 | The standpipe system has not been evaluated for compliance with the design pressure and flow demands of NFPA 14 or BNBC as per Alliance Standard 5.4.3. | The standpipe system needs to be evaluated for compliance with the design pressure and flow demands of NFPA 14 or BNBC as cited in 5.4.3. Standalone standpipe systems shall be confirmed to meet the local BNBC requirements with a minimum 450 kPa (65 psi) pressure at the hydraulically most remote hose connection or NFPA 14. This testing should be documented and available for review. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected as per previous follow up inspection. On 08/06/2017: Corrected. On 31/07/2017: Corrected as per previous follow-up. On 28/01/2018: Please see issue no. 31. On 12/07/2018: Refer to issue #31. On 04/10/2022: Refer to the issue no-31. On 21-Aug-25: Refer to the issue no-31. | Jun 3 2014 | Corrected
Initial Inspection |  | 21 | Factory has a verbal system (approval must be sought for hot work) however, no written permitting program as per Alliance Standards Part 13 Section 13.4 Hot Work Permit and NFPA 51B | Develop a written hot work permit program. The program must comply with the requirements of NFPA 51B | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected as previous follow up. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Jun 3 2014 | Corrected
Follow Up Inspection |  | 22 | New finding (1st Follow-up):Transformer is not properly separated by fire rated construction with other Occupancies/Areas. | Transformer shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Switch gears and transformer bays shall be separately housed with a 2-hr rated wll in between. Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. | Corrected | Dec 31 2016 | On 20 June 2016 the factory is asking for the date 15/7/16.the time extension is not accepted. On 08/03/2016: In progress. Separation work is incomplete. On 09/03/2017: Fire door installation is completed for transformer room but interfacing with FACP has not been done yet. On 08/06/2017: Fire door installation is completed for transformer room but interfacing with FACP has not been done yet. On 31/07/2017: Corrected as per previous follow-up. On 28/01/2018: Corrected as per last follow up. On 12/07/2018: Corrected. Note: Separation has been provided but door of transformer room has been found opened with external objects. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Dec 9 2015 | Corrected
Follow Up Inspection |  | 23 | New finding (1st Follow-up): Compressor room is not properly separated by fire rated construction . | 1. Compressor shall be separated from other occupancies by a minimum 1-hr (2-hr for highrise building) fire rated construction (wall, floor, slab etc). Seal all penetrations and openings (door, window etc.) should be protected by 1 hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Corrected | Mar 15 2016 | On 08/03/2016: In progress. Separation work is incomplete. Final CAP Timeline: Expired. Committed Timeline: 10-April-16. On 09/03/2017: Shifted to Another place but not separated by fire rated construction. On 08/06/2017: Shifted to Another place but not separated by fire rated construction. On 31/07/2017: In progress. On 28/01/2018: Corrected. Sealed penetrations & installed fire door on west side mezzanine floor at exit. On 12/07/2018: Corrected. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected . | Dec 10 2015 | Corrected
Follow Up Inspection |  | 24 | New finding (1st Follow-up): Dining floor is not properly separated by fire rated construction. | Seal all penetrations and openings in floor (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating in dining floor. | Corrected | Dec 31 2016 | On 09/03/2017: No action has been taken yet. Fire rated separation is not completed with the Accessories Store Room. On 08/06/2017: Removed. Not found. On 31/07/2017: Issue is reopened. Dining area has been found in ground floor without fire rated separation. On 28/01/2018: It was found same as it was last follow-up (5th). On 12/07/2018: Corrected. Dining floor has been shifted to another building. On 15/04/2019: Corrected as per previous follow up. Note: Dinning floor not found during inspection. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Dec 11 2015 | Corrected
Follow Up Inspection |  | 25 | New finding (1st Follow-up): Penetrations through floor assemblies are found unsealed . | Seal all penetrations and openings in floor (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating . | Corrected | Mar 15 2016 | On 08/03/2016: No action has been taken yet. Final CAP Timeline: Expired. Committed Timeline: 10-April-16. On 09/03/2017: No action has been taken yet. On 08/06/2017: No action has been taken yet. On 31/07/2017: Few unsealed penetrations have been found unsealed. On 28/01/2018: Still penetration was found on several floors. On 12/07/2018: Corrected. All penetrations have been found sealed. On 15/04/2019: Floor to floor penetration were observed due to steam pipe. On 04/10/2022: During inspection floor to floor penetration were observed in electric riser and steam pipe line portion. On 28-Jan-25: Factory sealed penetration of metal steam pipeline by mortar and electrical cable riser by fire rated sealant material. Proper design and documents for sealant material was not found onsite to verify. Additionally, expansion joint at floor/ceiling assemblies was not properly sealed. On 21-Aug-25: The factory submitted the remediation proposal design and documentation to the RSC for review regarding expansion joint. After receiving the review observation the factory shall start the remediation work. Remediation has not started regarding cable riser. | Dec 12 2015 | In Progress
Follow Up Inspection |  | 26 | New finding (1st Follow-up): Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Corrected | Dec 31 2016 | On 20 June 2016 the factory is asking for the date 15/7/16.the time extension is not accepted. On 08/03/2016: No action has been taken yet. Final CAP Timeline: Expired. Committed Timeline: 10-April-16. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected as per previous follow-ups. Note: Manual on-off switch shall be removed from all emergency lights/ exit signs. On 28/01/2018: Corrected. Removed. On 12/07/2018: Corrected as per previous follow up. Note: Factory shall remove all existing manual on off switches from several emergency lights. On 15/04/2019: Manual on off switch & switch socket connection were observed on several locations. On 04/10/2022: During inspection found same as it was before. On 28-Jan-25: Corrected. Manual on/off switch for emergency light was not found onsite during inspection. On 21-Aug-25: Corrected. | Dec 13 2015 | Corrected
Follow Up Inspection |  | 27 | New finding (1st Follow-up): child care room is not properly separated by fire rated construction. | Seal all penetrations and openings in floor (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating in Child care room. | Corrected | Mar 8 2016 | On 08/03/2016: Corrected. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected. On 12/07/2018: Corrected. On 15/04/2019: Corrected. On 04/10/2022: Corrected as per previous FUI. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Dec 14 2015 | Corrected
Follow Up Inspection |  | 28 | New finding (1st Follow-up): Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Corrected | Mar 15 2016 | On 08/03/2016: In progress. Proper documentation is required as per accord standard. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected. On 28/01/2018: Corrected as per previous follow up. Note: Factory shall update emergency & exit light maintenance checklist. On 12/07/2018: Corrected. Note: Factory shall update checklist regularly. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Issue reopened. Emergency light and exit signs were not working during inspection time. Moreover, ITM was not maintaining as per standard. On 28-Jan-25: Corrected. Factory was maintain Emergency lighting system as per standard. On 21-Aug-25: Corrected. | Dec 15 2015 | Corrected
Follow Up Inspection |  | 29 | New finding (1st Follow-up): Areas used for in-process storage of combustible materials are open to the surrounding occupancy. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Dec 31 2016 | On 20 June 2016 the factory is asking for the date 15/7/16.the time extension is not accepted On 08/03/2016: No action has been taken yet. On 09/03/2017: Corrected. On 08/06/2017: Corrected. On 31/07/2017: Corrected as per previous follow-up. The factory shall maintain the in-process storage area as per recommendation. On 28/01/2018: Corrected. During follow up inspection storage areas (running goods) found as per standard. On 12/07/2018: Corrected. In process storages were found as per standard. Doors of defined storage room (bonded warehouse) were found opened with external objects. On 15/04/2019: Pile dimension area is not maintaining on several floors in case of in process storage. On 04/10/2022: In-process storage was not organized as per standard. On 28-Jan-25: Corrected. In process storage was found within limit. On 21-Aug-25: Corrected. | Dec 16 2015 | Corrected
Follow Up Inspection |  | 30 | New finding (1st Follow-up): Penetrations through floor/ceiling assemblies are found unsealed. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. | Corrected | Mar 15 2016 | On 08/03/2016: No action has been taken yet. Final CAP Timeline: Expired. Committed Timeline: 10-April-16. On 09/03/2017: It has found same as it was before. On 08/06/2017: It has found same as it was before. On 31/07/2017: Not corrected yet. On 28/01/2018: Not corrected. On 12/07/2018: Corrected. On 15/04/2019: Corrected as per previous follow up. On 04/10/2022: Issue reopened. during inspection floor to floor penetration were observed in electric riser and steam pipe line portion. On 28-Jan-25: Factory sealed penetration of metal steam pipeline by mortar and electrical cable riser fire rated sealant material. Proper design and documents for sealant was not found onsite to verify. Additionally, expansion joint at floor/ceiling assemblies was not properly sealed. On 21-Aug-25: The issue has already been addressed in CAP-25 for the structure. As this is covered in CAP-25, this cap is corrected. | Dec 9 2015 | Corrected
Follow Up Inspection |  | 31 | New Finding (3rd Follow up): On behalf of Stand pipe system Required Certificates were not available for fire pump as per NFPA-20. | Fire Pump shall be listed or approved as per NFPA 20 | Corrected: New Electric pump(1250 GPM@11BAR), Diesel Pump(1250 GPM @11BAR), jockey pump(25GPM@11BAR) and all hydrant systems with all accessories installation with Testing & Commissioning work is complete. | Jun 9 2017 | On 09/03/2017: NEW FINDING. On 08/06/2017: In progress. On 31/07/2017: Work is in progress. On 28/01/2018: Partially corrected. Standpipe system drawing has been reviewed by Alliance. Installation was almost completed. Factory have to prove whether the installed pumps with all accessories has been certified by any recognized third party or not. (Commissioning of the system in-front of contractor/ 3rd party will be done by Accord). On 12/07/2018: Reviewed drawings by Alliance were present on site. Fire pump installation and standpipe installation has been completed. Factory shall ensure that all accessories related to pumps and standpipes are certified by third party agency. On 15/04/2019: Reportedly, installation is complete. After completion of testing & commissioning by contractor, factory shall submit T&C documents to Accord prior to T&C VI. Factory shall ensure that all accessories related to pumps and standpipes are certified by third party agency. On 04/10/2022: Reportedly factory is yet to complete the modification work based on the last T&C report (07.23.2019). [Note: fire pump was shut off during inspection time.] On 28-Jan-25: Factory submitted design and documents of SUPS to RSC for Pre T&CVI on 20-Jan-2025, which is currently under "Desk based Documentation review". SUP system was found active during inspection. On 21-Aug-25: Pre T&CVI found that the system is not ready for T&C VI. . For details see the Pre T&CVI report. | Within 3 month | In Progress
Follow Up Inspection |  | 32 | New Finding (3rd Follow up): Rooms used for combustible storage are not separated from Cutting Section by firerated construction. | Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. Seal all penetrations and openings in the wal by fire rated materials to maintain the fire resistance rating. | Corrected | Jun 9 2017 | On 09/03/2017: NEW FINDING: On 08/06/2017: No action has been taken. On 31/07/2017: No action has been taken yet. On 28/01/2018: Still store rooms are not separate from work area on ground floor. On 12/07/2018: Same observation as previous follow ups. On 15/04/2019: Door was found kept open by external source on ground floor. Annex building 1st floor store is not separated from maintenance room & needle section due to non rated door. On 04/10/2022: During inspection found same as it was before. On 28-Jan-25: Significant progress found. Factory separated the storage areas by fire rated door. Fire rated door and it's components was found functional and interfaced with FACP. However, the storage areas at Annex building were not separated from other occupancies due to unprotected window opening. On 21-Aug-25: Corrected. Storage at Annex building has been separated by fire rated construction. | Within 3 month | Corrected
Follow Up Inspection |  | 33 | New Finding (3rd Follow up): Electrical DB located in the exit stair of ground floor. | Electrical DB shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 1.5 -hr fire rated materials to maintain the fire separation if required. | Corrected | Jun 9 2017 | On 09/03/2017: NEW FINDING: On 08/06/2017: Not corrected. On 31/07/2017: Corrected. Removed. On 28/01/2018: Corrected as per last follow up. On 12/07/2018: Corrected as per previous follow up. Note: Electrical DB were found in west stair only. On 15/04/2019: Corrected. On 04/10/2022: Corrected. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Within 3 month | Corrected
Follow Up Inspection |  | 34 | New Finding (5th Follow Up): The exit stairs are not separated from [work areas, other spaces] on each floor by fire-rated construction. Unprotected open has been observed in exit stair enclosure (Location: Stair no.4 in Annex building at North side). Moreover, fire doors have been found open with external source (blockage). | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire rated doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire rated doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Corrected | Sep 30 2017 | On 31/07/2017: New Finding On 28/01/2018: During follow up inspection installed fire doors were found open by external objects & door coordinators (in double) were not working properly on several floors. On 12/07/2018: Installation of fire doors have been completed. Door accessories (magnetic holders, door coordinators etc) have been found missing or non functional in almost every door. Doors have been found opened with external objects. Interfacing of door with fire alarm system has not been completed yet. On 15/04/2019: Fire door interface with FACP not completed yet. Door were kept open by external source. Moreover, proper fire door certificate shall kept on site. On 04/10/2022: Fire door coordinators, door closer, Positive latching system, magnetic door holders in various location have been found non-functional & Few fire doors were observed kept opened by unauthorized manner. So fire separation is not being maintained. On 28-Jan-25: Corrected. Separated by fire rated construction and installed fire rated door and it's component was found functional and interfaced with FACP. On 21-Aug-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 35 | New Finding (5th Follow Up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Aug 31 2017 | On 31/07/2017: New Finding On 28/01/2018: Still inadequate. On 12/07/2018: Corrected. On 15/04/2019: Corrected. Note: Factory shall ensure adequate emergency light on store area. On 04/10/2022: Issue reopened. Emergency light were not working during inspection time. On 28-Jan-25: Corrected. Emergency light was found functional during inspection. On 21-Aug-25: Issue reopened. Some emergency lights on each floors were not working during inspection time. | Within 1 month | In Progress
Follow Up Inspection |  | 36 | New Finding (8th Follow Up): Occupant load sign and emergency evacuation map are not posted at the exit stair at all level of all building. | Occupant load sign and emergency evacuation map shall be posted at the entrance to exit stair at all level at required all locations. | Corrected | May 15 2019 | New Finding On 04/10/2022: During inspection observed signage was missing at several location. On 28-Jan-25: Corrected. Occupant load sign and emergency evacuation map was posted at the entrance exit stair at required all locations. On 21-Aug-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 37 | New Finding (8th Follow Up): Compressed gas cylinders were located within the factory Premises. | Provide 2 hour rated fire separation from other occupancy with proper ventilation. Or The storage of liquefied or compressed flammable gas cylinders shall remove from the factory building. | Corrected | Jun 15 2019 | New Finding On 31/08/2021 (Special Inspection): Corrected. CNG cylinders removed and now boiler facilitated by supply natural gas. On 04/10/2022: Issue reopened. Compressed gas cylinder was located inside the factory premises. Location: Kitchen. On 28-Jan-25: Corrected. Kitchen removed and Compressed gas cylinder was not found inside the factory premises during inspection. On 21-Aug-25: Corrected. Not found at site. | Within 2 months | Corrected
Follow Up Inspection |  | 38 | New Finding (8th Follow Up): The fire pump room is not provided with adequate fire separation from paint store area. | Provide fire pump room with 2 hr rated fire separation when not sprinklered and 1 hr rated fire separation when provided with automatic sprinklers in accordance with NFPA 20 from other occupancy. Or remove all kind of storage from fire pump room. | Corrected | Jun 15 2019 | New Finding On 04/10/2022: Corrected. Storage was removed. On 28-Jan-25: Corrected On 21-Aug-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 39 | New Finding (9th FUI): Storage was observed at exit stair enclosures and exit discharge paths on several floors. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. | Corrected | Oct 30 2022 | On 04/10/2022: New Finding On 28-Jan-25: Corrected. Exit stair enclosures and Exit discharge was found continuously free and clear of all obstructions/storage. On 21-Aug-25: Corrected. | immediately | Corrected
Follow Up Inspection |  | 40 | New Finding(On 10th FUI) : Horizontal exit access path (Connecting bridge) between Main building & Annex building was not protected from Building interior. Location: 1st, 2nd and 3rd floor of Annex Building. | Separate the corridor by a minimum 1-hr fire rated construction. | Corrected | Mar 28 2025 | On 28-Jan-25: New Finding. On 21-Aug-25: Not separated yet. | Within 2 months | In Progress

## Electrical
Date
30-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A J Super Garments Ltd., Aj Garden, Goshbag, Post- Zirabo, Thana - Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-03-23
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | No electrical drawing available for information as per Alliance Standard Part 10 Section 10.3.7. | Have a qualified electrical engineer develop an as-built single line diagram detailing key components and capacity of the electrical system. | Corrected | Feb 28 2017 | On 20 June 2016 : This issue is not corrected yet. New committed timeline is given till 15th-April-2016. On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Not Corrected. On 28/01/2018: Not Corrected. SLD is reviewed by Alliance but mismatch is found between field and SLD drawing. On 12/07/2018: Not corrected. On 15/04/2019: Corrected. | Jun 23 2014 | Corrected
Initial Inspection |  | 2 | Workers that operate and maintain the electrical system have not received electrical safety training in compliance with NFPA 70e or equivalent standard. | Develop and implement an electrical safety program. Include key topics such as lock out tag out procedures, personal protective equipment requirements, etc. Reference NFPA 70e for example program requirements. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 3 | Oil filled transformers (NOTE: not currently in use, factory uses generator power only) are not separated by a minimum 2 hour fire resistive rated construction. | As per Alliance standard oil filled transformers for non high-rise buildings shall be separated by a minimum 2 hour fire resistive rated construction. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 4 | No lightning protection system installed on the building as per Alliance Standards Part 10 Section 10.11 Lightning Protection. Calculated Risk index of 40-50. | Install a lighting protection system in accordance with BNBC Part 8. A qualified electrical engineer should design the lightning protection system and a licensed electrician/contractor should install the designed system. | Corrected | Apr 15 2016 | Installation of LPS system is going on. New committed timeline is given till 15/04/2016. On 09/03/2017: Not Corrected. 08.06.2017: Corrected. | Jun 23 2014 | Corrected
Initial Inspection |  | 5 | Fourth Floor(Cutting) SDB and 2nd floor North side DB, there are two cables from single circuit breakers. | There should be no multi looping of wiring/cables at circuit breakers within switchboards and/or distribution boards. Remove looping of wiring/cables in distribution boards (Fourth Floor SDB and 2nd Floor North Side DB). Affirm no other multi looping is present in other DBs. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 6 | Un-terminated wires are found in all of the distribution boxes. No cable lugs in Phase, Neutral and Earthing bar. | No un-terminated wires are permitted in the DB. All cables should be affixes to phase, neutral or Earthling bar with appropriate lugs/sockets. Cables shall be connected to terminals only by soldered or welded lugs, unless the terminal are of such form that it is possible to securely clamp them without cutting away the cable strands as per BNBC Part 8 2.5.5.4. | Corrected | Apr 15 2016 | This issue is not corrected yet. Cable termination without lug and un-terminated wires are observed at floor level. New committed timeline is given till 31st-March-2016 to close this issue. On 09/03/2017: Corrected. Not Found. | Jun 23 2014 | Corrected
Initial Inspection |  | 7 | Periodic safety inspections of the electrical system components are not completed and documented as per Alliance Standard Part 10 Building Services Section 10.13 Inspection and Testing. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Inspection should include general conditions and conformance to Bangladesh standards and specs, insulation resistance testing, earth resistance testing, and operational testing under load (clamp on ammeters can be used). All testing should be conducted by competent personnel. Maintain records concerning inspections and follow up actions. | Corrected | Dec 31 2015 | Verified at Accord 2nd follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 8 | The majority of metal distribution panels (ground floor DB is exception) are not properly grounded. | All Distribution Board covers in the building should connected to the building earthing/grounding system such as metal rebar in concrete, metal frame of building, or metal water pipe in accordance with BNBC 2006 Part 8. | Corrected | Dec 31 2015 | Verified at Accord 2nd follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 9 | Proper identification was not provided on any switchboards and/or distribution boards as per BNBC Part 8 Section 2.11.5.4. | Switchboards and/or distribution boards should have clear and permanent unique identification markings (e.g. MDB-01) as per BNBC Part 8 Section 2.11.5.4. All distribution boards shall be marked by use (e.g. "Lighting" or "Power"), as the case may be, and also be marked with the voltage and number of phases of the supply. Each shall be provided with a circuit list giving diagram of each circuit which it controls and the current rating for the circuit and size of fuse element. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | Apr 23 2014 | Corrected
Initial Inspection |  | 10 | No labeling found on cabling or wiring. | Indelibly and clearly label all incoming and outgoing circuits of HT and LT panels. Provide circuit diagram and labeling of switches and cables in all DB. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 11 | Periodic safety inspections of the electrical system components are not documented as per Alliance Standard Part 10 Building Services Section 10.13 Inspection and Testing. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Inspection should include general conditions and conformance to Bangladesh standards and specs, insulation resistance testing, earth resistance testing, and operational testing under load (clamp on ammeters can be used). All testing should be conducted by competent personnel. Maintain records concerning inspections and follow up actions. | Corrected | Feb 28 2016 | Verified at Accord 2nd follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 12 | No thermographic scans of electrical equipment are completed at least every three years as per Alliance Standards Part 10 Section 10.13.8 Electrical Inspections. | Complete thermographic scans at least on a three year cycle. Thermographic scans should be completed in accordance with the Standard for Infrared Inspection of Electrical Systems & Rotating Equipment and NFPA70B or a comparable standard. | Corrected | Feb 28 2017 | On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Not Corrected. On 28/01/2018: Not Corrected. On 12/07/2018: Not corrected. Report do not cover bus bar of all panels. On 15/04/2019: Corrected. | Jul 23 2014 | Corrected
Initial Inspection |  | 13 | No periodical Insulation Resistance Measurement Program established and recorded as per Alliance Standard Part 10 Section 10.13.4 Insulation Tests and 10.13.8 Electrical Inspections. | Develop an Insulation Resistance Measurement Program that ensures deterioration of insulation resistance will be identified quickly. Testing should be in compliance with International Electrical Testing Association (NETA). All transformers, switchgears etc. shall be subject to an insulation resistance measurement test to ground after installation but before any wiring is connected. Insulation tests shall be made between open contacts of circuit breakers, switches etc. and between each phase and earth. | Corrected | Feb 28 2016 | Verified at Accord 2nd follow-up Inspection. | Dec 30 2015 | Corrected
Initial Inspection |  | 14 | No inspection in annual basis as per Alliance Standards Part 10 Section 10.13.8 Electrical Inspections. | Inspect electrical switchgear and panel boards on an annual basis to ensure that the equipment is in good working condition. | Corrected | Feb 28 2016 | Verified at Accord 2nd follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 15 | Cabling in substation is laid on floor without protection. | Cables run on floors must be protected and supported on cable trays or in trenches as per Alliance Standard 10.13 and BNBC Part 8 2.7.4 | Corrected | Feb 28 2017 | On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Not Corrected On 28/01/2018: Not Corrected. Still cables aren't properly supported.. On 12/07/2018: Corrected. | Jun 23 2014 | Corrected
Initial Inspection |  | 16 | Third floor south side DB is not provided with a dedicated neutral as per Alliance Standards Part 10 Section 10.3 Electrical Wiring and Cabling. | Each circuit must be provided with a dedicated neutral. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 17 | Third Floor East side MDB was missing protection against contact with circuits. | Install proper protective guards to prevent contact with bus bars. Proper guards will be constructed of non-conductive material and sufficient to prevent inadvertent contact with live circuits. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | Jun 23 2014 | Corrected
Initial Inspection |  | 18 | There was no instruction board for first aid and artificial respiration in the generator and substation room. | Instruction board for first aid and artificial respiration should be installed in substation and generator room. | Corrected | Oct 15 2015 | Verified at Accord first follow-up Inspection. | May 23 2014 | Corrected
Initial Inspection |  | 19 | Signage indicating the prohibition of light fixtures without protective covers not installed in storage areas as per Alliance Standards Part 10 Section 10.15 Naked Lights. | Install signage in all storage areas or other areas of combustibles indicating no use of light fixtures without protective covers as per Alliance Standard 10.15.2. Signs should conform to ANSI Z535 or equivalent international standard regarding safety signs. | Corrected | Dec 31 2015 | Verified at Accord 2nd follow-up Inspection. | Jun 23 2014 | Corrected
Follow Up Inspection |  | 20 | On the south side of the third floor, the Distribution Board has no phase separators at MCCB. | Install phase separators between terminal connections at south side DB of 3rd Floor. Affirm phase separators are provided on all other factory DB's. | Corrected | Dec 31 2015 | Verified at Accord 2nd follow-up Inspection. | Jun 23 2014 | Corrected
Follow Up Inspection |  | 21 | New Finding: Earth Pit resistance record is unavailable. Again, Earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. Again, all earthing systems shall be tested for resistance on any dry day not less than once in every two years and records should be preserved. | Corrected | Dec 31 2015 | Verified at Accord 2nd follow-up Inspection. | 2 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Panel base plates removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. | Corrected | Feb 28 2017 | On 20 June 2016 : This issue is not corrected yet. New committed timeline is given till 15/04/2016. On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Circuit is drawn from bus bar without Circuit breaker or any protective means. | For distribution board, along with the main circuit breaker all outgoing circuits shall have individual outgoing circuit breaker. | Corrected | Jan 31 2017 | On 20 June 2016 : This issue is not corrected yet. New committed timeline is given till 15/04/2016 to close this issue. On 09/03/2017: Not Corrected. 08.06.2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Multiple cables terminated at MCCB terminals / Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. | Corrected | Jan 31 2017 | On 20 June 2016 : This issue is not corrected yet. New committed timeline is given till 15/04/2016 to close this issue. On 09/03/2017: Not Corrected. 08.06.2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Oil leakage has been observed from transformer. | Stop oil leakage from transformer and keep clean top of transformer. | Corrected | Jan 10 2016 | Verified at Accord 2nd follow-up Inspection. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Earth connections are not segregated. Transformer neutral and system earthing are connected in same bus. | Ensure separate earthing connection for all neutrals Generator body, transformer body, Electrical system and Lightning Protection System. Mark them all. | Corrected | Apr 15 2016 | On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Not Corrected. On 28/01/2018: Not Corrected. On 12/07/2018: Not corrected. LT & HT panel share earth pits. On 15/04/2019: Not corrected. On 04-Oct-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Transformer Arcing horn has not installed. | Install transformer arcing horn with proper alignment (maintain not less than 2 inch gap between two horns). | Corrected | Feb 28 2017 | On 20 June 2016 : The factory is asking for the date 10/08/2016. the time extension is not accepted. On 09/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Excessive wires crowding inside the panel. | Cables inside panel must be securely fastened. | Corrected | Apr 15 2016 | On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. | Corrected | Apr 15 2016 | On 09/03/2017: Not Corrected. 08.06.2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: MCCB/MCB/ electrical device is installed without any enclosure. | Need to provide electrical graded enclosure. | Corrected | Jan 31 2017 | On 20 June 2016 : The factory is asking for the date 10/08/2016. the time extension is not accepted. On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Not Corrected. On 28/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. | Corrected | Apr 15 2016 | On 09/03/2017: Not Corrected. 08.06.2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Cable duct/channels closed to steam line are not covered. | Cover all cable duct specially those duct closed to steam line immediately. Ensure there is enough insulation between steam line cable duct so that heat cannot be transferred to cables. Normally power cable should keep 0.9m apart from hot area. | Corrected | Feb 28 2017 | On 20 June 2016 : The factory is asking for the date 15/07/2016. the time extension is not accepted. On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. On 31/07/2017: Not Corrected. On 28/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Cables inside trench are disorganized. | Organize all the power cables securely inside trench then covered it by non-combustible material. | Corrected | Jan 31 2017 | On 09/03/2017: Not Corrected. 08.06.2017: Not Corrected. Moreover cable channel are not covered. On 31/07/2017: Not Corrected. On 28/01/2018: Not Corrected. On 12/07/2018: Not corrected. On 15/04/2019: Not corrected. On 04-Oct-2022: Not Corrected. Still work is pending. RPO Comments: On 26-11-2023 the factory management reported the remediation completion. This item will be verified in the next inspection. On 21/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Corrected | Apr 15 2016 | On 09/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Power sockets are hung without proper support. | Power socket has to be installed on rigid support/base securely and at minimum 200mm above floor level. | Corrected | Mar 7 2018 | On 12 June 2018 : the factory is asking for the date till 30/6/2018.The time extension is not accepted. On 28/01/2018: Not Corrected. New timeline: 07/03/2018. On 12/07/2018: Not corrected. On 15/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. | Corrected | Sep 15 2017 | On 28/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: List of circuit or SLD of existing circuits are not available on each electrical panel/board. | List of circuit or SLD of respective circuits shall be available for each electrical panel/board. | Corrected | Mar 7 2018 | On 28/01/2018: Not Corrected. New timeline: 07/03/2018. On 12/07/2018: Not corrected. On 15/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Transformer Body earthing (equipment earthing) cable size is inadequate. | Equipment earthing cable size must be increased. The earth cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. | Corrected | Mar 7 2018 | On 28/01/2018: Not Corrected. New timeline: 07/03/2018. On 12/07/2018: Not corrected. On 15/04/2019: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: i. Transformer Silica gel is discolored. ii. Transformer Breather oil cup is empty. | i. Silica gel shall be changed; or reuse can be done, if color regains after sundry. ii. Transformer breather oil cup must be filled not more than 70% of its capacity. | Corrected | Sep 15 2017 | On 28/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Oil leakage from transformer has been observed. | Oil leakage from transformer must be stopped and top of transformer must also be kept clean. | Corrected | Mar 7 2018 | On 28/01/2018: Not Corrected. New timeline: 07/03/2018. On 12/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Inadequate sized earth cable connected to generator frame. | Two separate earth connection & one separate and distinct Neutral connection must be provided over generator. Generator body must have earth connection with half of phase conductor/follow manufacturer/suppliers recommendation. | Corrected | Mar 7 2018 | On 28/01/2018: Not Corrected. New timeline: 07/03/2018. On 12/07/2018: Not corrected. On 15/04/2019: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Air terminals are missing at several points of Lightning Protection System. LPS not maintained regularly. Connectors are rusted. Air terminals are not installed at desired height. | Missing Air Terminals shall be reinstalled. Rusted/damaged joints, air terminals, conductor shall be cleaned/replaced. LPS shall be maintained regularly for loosened joints, damaged/broken air terminals & bonding. Increase the air terminals height | Corrected | Mar 7 2018 | On 28/01/2018: Not Corrected. Air terminals are at desire height and have all terminals but still rusted connectors are present. New timeline: 07/03/2018. On 12/07/2018: Not corrected. Most of the work is done. On 15/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Lead acid battery terminals must be covered/ capped and rust must be checked and cleaned. | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. | Corrected | Aug 17 2018 | On 15/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Oil level in transformer conservator oil tank is below/ above required level. | Oil level in transformer conservator oil tank must be maintained within given limit, and it shall be checked periodically. | Corrected | Aug 17 2018 | On 15/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Metal fixtures of QC table has no earthing. | All metal fixture within reach (may have chance to be touched by user/operator) must have earth connection. | Corrected | Aug 17 2018 | On 15/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Distribution panel/board is installed without proper grout. | Distribution panel/board must be installed with proper grout. | Corrected | Aug 17 2018 | On 15/04/2019: Not corrected. On 04-Oct-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Aug 12 2018 | On 15/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. |  | Nov 10 2022 | RPO Comments: On 26-11-2023 the factory management reported the remediation completion. This item will be verified in the next inspection. On 21/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/ duct/BBT). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. |  | Nov 10 2022 | RPO Comments: On 26-11-2023 the factory management reported the remediation completion. This item will be verified in the next inspection. On 21/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Sewing machine MCB / Fuse are not installed / adjusted as per load demand. | All the MCB/Fuse must be installed/adjusted as per connected load current; if adjustment is not possible, replacement will be the only way and update the SLD accordingly. | Corrected | Nov 10 2022 | RPO Comments: On 26-11-2023 the factory management reported the remediation completion. This item will be verified in the next inspection. On 21/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. | In Progress | Aug 2 2025 | RPO Comments on 01-May-2025: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 6 Months | In Progress