## Structural
Date
18-Feb-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A&A Trousers Ltd, Haribari Tak, Pubail Collage Gate, Pubail, Gazipur Sadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-07-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Building-1: The available documents indicate conformity to the requirements of BNBC 1993 in the General Notes, but no design report was available to confirm this information. Building-2: Credible structural documentation was not available. | Engage a qualified structural engineer to develop the required documents to confirm the structural integrity of the buildings. Documents must comply with Alliance Standard Part 8 Section 8.19 and 8.20. This should be completed for all buildings. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Yet not prepare any as build documents & design report for both building. On verification period we found some discrepancy in architectural & structural drawing of building #1 and also found horizontal extension in Building#2(Shed ). The factory should be discuss with ALLIANCE structural team. On 20-11-2017: Factory has carried out DEA report, which was accepted by ALLIANCE on 12 Feb 2017. DEA of main building-1 was done for 6 storied. During inspection building was found 4 storied and the retrofitting work up to 4 storied found completed as per accepted drawing. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. This issue was covered by DEA which was accepted by ALLIANCE on 12-Feb-2017. DEA of Main Building-1 was done for 6 storey. During inspection, the building was found 4-storied and retrofitting works were found completed as per accepted drawing. Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously. | Oct 15 2014 | Corrected
Initial Inspection |  | 2 | There are five 1.5-ton water tanks and two 2-ton water tanks located on the roof level of the main building. There was no evidence available to indicate that the impact of these concentrated loads was considered. | Engage a qualified structural engineer to confirm and document that provisions have been made to accommodate these water tanks. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Water tank have been braced except Boiler room roof top PVC tank. The factory should be include water tank load in design report. On 20-11-2017: Factory has carried out DEA report, which was accepted by ALLIANCE on 12 Feb 2017. DEA of main building-1 was done for 6 storied. During inspection building was found 4 storied and the retrofitting work up to 4 storied found completed as per accepted drawing. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. This issue was covered by DEA which was accepted by ALLIANCE on 12-Feb-2017. DEA of Main Building-1 was done for 6 storey. During inspection, the building was found 4-storied and retrofitting works were found completed as per accepted drawing. On 09-Mar-2025: Corrected previously. | Oct 15 2014 | Corrected
Initial Inspection |  | 3 | Building-1: The available documents indicate conformity to the wind and seismic design requirements of BNBC 1993, but no design report was available to confirm this information. Building-2: Credible structural documentation was not available. | Have a qualified structural engineer document compliance with the seismic and wind requirements stated in the 2006 BNBC. This should be completed for all buildings. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Cover in Assessment report On 20-11-2017: Factory has carried out DEA report, which was accepted by ALLIANCE on 12 Feb 2017. DEA of main building-1 was done for 6 storied. During inspection building was found 4 storied and the retrofitting work up to 4 storied found completed as per accepted drawing. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. This issue was covered by DEA which was accepted by ALLIANCE on 12-Feb-2017. DEA of Main Building-1 was done for 6 storey. During inspection, the building was found 4-storied and retrofitting works were found completed as per accepted drawing. Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously. | Oct 15 2014 | Corrected
Initial Inspection |  | 4 | Building-1: The available documents indicate conformity to the wind design requirements of BNBC 1993, but no design report was available to confirm this information. Building-2: Credible structural documentation was not available. | Engage a qualified structural engineer to confirm satisfactory structural performance of the buildings under wind loading. This should be completed for all buildings. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Cover in Assessment report On 20-11-2017: Factory has carried out DEA report, which was accepted by ALLIANCE on 12 Feb 2017. DEA of main building-1 was done for 6 storied. During inspection building was found 4 storied. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. This issue was covered by DEA which was accepted by ALLIANCE on 12-Feb-2017. DEA of Main Building-1 was done for 6 storey. During inspection, the building was found 4-storied and retrofitting works were found completed as per accepted drawing. Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously. | Oct 15 2014 | Corrected
Initial Inspection |  | 5 | Building 1: There are signs of corrosion in the steel members at Levels 1 and 2. Building-2 : Corrosion of steel members was not observed. | Complete further testing on areas of deterioration in order to understand the level of corrosion and potential weakening of the members and have a qualified structural engineer develop a remediation plan. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: It will cover in Assessment report but on ground we found corrosion in column main rod and factory person didn’t taken any action about corrosion issue. The factory should be take action immediately. On 20-11-2017: Corrosion of building-1 has been repaired by factory. During inspection corrosion effected area was found painted. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. During inspection, corrosion was found in a steel bracing, later, factory sent some pictures after repairing the corrosion and providing paints, which seems satisfactory. Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected from previous inspection. During inspection, corrosion was found in steel members at stair room on roof, later, factory sent some pictures after repairing the corrosion and providing paints, which seems satisfactory. | Oct 15 2014 | Corrected
Initial Inspection |  | 6 | No load management plan is currently in place. | Develop a program to ensure that all live loads for which a floor or roof has been designed for will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: The factory posted load plan but not reviewed by ALLIANCE On 20-11-2017: Load plan was produced and accepted along with DEA report. Load plan was found posted. Load was found below allowable loading limit. On 06-Feb-2024: Corrected from previous inspection. Load plan was prepared as part of DEA which got acceptance from ALLIANCE on 12-Feb-2017. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). On 09-Mar-2025: Corrected previously. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). | Oct 15 2014 | Corrected
Initial Inspection |  | 7 | Building-1: The structure is a special system (concrete columns and steel beams with deck slab) and hence the lateral load system is not apparent and the redundancy is not known. Building-2: It is a single story "shed" structure constructed with concrete columns and steel roof trusses. Therefore the lateral load system is not apparent and the redundancy is not known. | Have a qualified structural engineer complete further analysis of the structure and develop a remediation plan if required. This should be completed for all buildings. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Cover in Assessment report On 20-11-2017: Factory has carried out DEA report, which was accepted by ALLIANCE on 12 Feb 2017. DEA of main building-1 was done for 6 storied. During inspection building was found 4 storied and the retrofitting work up to 4 storied found completed as per accepted drawing. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. This issue was covered by DEA which was accepted by ALLIANCE on 12-Feb-2017. DEA of Main Building-1 was done for 6 storey. During inspection, the building was found 4-storied and retrofitting works were found completed as per accepted drawing. Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously. | Oct 15 2014 | Corrected
Initial Inspection |  | 8 | Building-1: A set of credible design document is not available on site for review (design live loads, section details of RCC column and steel beam connection points, etc. are not available). Additionally, a design report is not available which is required per BNBC 2006 clause 1.9.1.1, and the credentials of the Structural Engineer and Architect of record are not complete. Building-2: Credible structural documentation is not available. | Have a qualified structural engineer prepare credible as-built documents for unavailable parts of design documents based on the requirements of Part 8 Section 8.19 of the Alliance Standard including a design report. Note that in addition to other items, these documents should include a full set of as-built structural and architectural drawings with the signature and credentials of the structural engineer and architect (per 2006 BNBC requirements). | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Yet not prepare any as building documents & design report for both building. On verification period we found some discrepancy in architectural & structural drawing of building #1 and also found horizontal extension in Building#2(Shed ). The factory should be discuss with ALLIANCE structural team. On 20-11-2017: A set of as built drawing was produced and accepted along with DEA report. DEA of main building-1 was done for 6 storied. During inspection building was found 4 storied. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. As built drawings were prepared as part of DEA which got acceptance from ALLIANCE on 12-Feb-2017. DEA of Main Building-1 was done for 6 storey. During inspection, the building was found 4-storied and retrofitting works were found completed as per accepted drawing. Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously | Oct 15 2014 | Corrected
Initial Inspection |  | 9 | The following items requiring maintenance were identified: -Dampness at Ground Level and Level 1, Building 1 -Corrosion at Levels 1 and 2, Building 1 -Dampness at east portion of Building 2 | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Water proofing was not provided even drainage system was not improved. On 20-11-2017: Water proofing was found provided at building-1. Also note that, In the future, the factory will build two more floors as per accepted DEA. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. Factory has improved drainage system by providing water proofing layer on the current roof. During inspection, corrosion was found in a steel bracing, later, factory sent some pictures after repairing the corrosion and providing paints, which seems satisfactory. Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously. | Oct 15 2014 | Corrected
Initial Inspection |  | 10 | The following elements not noted to not have adequate bracing or anchorage: -Storage racks in store room at Ground Level and Level 1, Building 1. -Plastic rooftop water tanks, Building 1 | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: Water tank have been braced except Boiler room roof top PVC tank . The factory should be include water tank load in design report. On 20-11-2017: Water tank was found braced. Also storage racks were found anchored. On 06-Feb-2024: Corrected from previous inspection. Water tanks and storage racks were found braced and anchored respectively. On 09-Mar-2025: Corrected previously. Water tanks and storage racks were found braced and anchored respectively. | Oct 15 2014 | Corrected
Initial Inspection |  | 11 | There are sign of water intrusion through the floor slabs and walls of Building 1. | Have the exterior façade repaired to ensure prevention of dampness. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: South side roof slab & wall damped On 20-11-2017: During inspection no dampness was found. Factory was repaired dampness portion area of Building 1. On 06-Feb-2024: Corrected from previous inspection. During inspection, no dampness was found. On 09-Mar-2025: Corrected previously. During inspection, a few dampness were found. Later, the factory sent some pictures after removing dampness and providing paints, which seems satisfactory. | Oct 15 2014 | Corrected
Initial Inspection |  | 12 | There is a Civil engineer in the factory who is trained about loading. But the engineer is not appointed as Load Manager. | The factory should appoint a load manager who will be on-site full time and trained regarding the structural floor capacity. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: The factory engages an load manager On 20-11-2017: This issue was corrected from previous inspection. Load manager was assigned by factory. Load plan was produced and accepted along with DEA report. Load plan was found posted. Load was found below allowable loading limit. On 06-Feb-2024: Corrected from previous inspection. Load manager was appointed by the factory. On 09-Mar-2025: Corrected previously. Load manager was appointed by the factory. | Jan 1 2015 | Corrected
Initial Inspection |  | 13 | Building-1: Floor load plans have not been developed. Building-2: Floor load plans not required (single story building). | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: The factory posted load plan but not reviewed by ALLIANCE On 20-11-2017: Load plan was produced and accepted along with DEA report. Load plan was found posted. Load was found below allowable loading limit. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. Load plan was prepared as part of DEA which got acceptance from ALLIANCE on 12-Feb-2017. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). | Oct 15 2014 | Corrected
Initial Inspection |  | 14 | Building-1: Floor load plans have not been developed or posted. Building-2: Floor load plans not required (single story building). | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. Floor load plans should be visibly posted on all levels of the building. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: The factory posted load plan but not reviewed by ALLIANCE On 20-11-2017: Load plan was produced and accepted along with DEA report. Load plan was found posted. Load was found below allowable loading limit. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. Load plan was prepared as part of DEA which got acceptance from ALLIANCE on 12-Feb-2017. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). Fabric Shed and Dry Process Shed were found closed. On 09-Mar-2025: Corrected previously. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). | Oct 15 2014 | Corrected
Initial Inspection |  | 15 | Building-1: There are no acceptable loading limit markings. Building-2: Loading limits not required (single story building). | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: No marking level in building #1 On 20-11-2017: During inspection load marking was found. Load plan was produced and accepted along with DEA report. Load plan was found posted. Load was found below allowable loading limit. Fabric shed and Dry Process shed was found closed. Factory provide some documents that both shed will no longer part of them. On 06-Feb-2024: Corrected from previous inspection. Load plan was prepared as part of DEA which got acceptance from ALLIANCE on 12-Feb-2017. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). Fabric Shed and Dry Process Shed were found closed. Factory has provided height markings on the storage areas. On 09-Mar-2025: Corrected previously. During inspection, load plan was found posted on each floor and floor loading was found within the allowable limit (63 psf). Factory has provided height markings on the storage areas. | Oct 15 2014 | Corrected
Initial Inspection |  | 16 | The Certificate of Occupancy is not available. | Provide Certificates of Occupancy for review. | Already completed and verified by Alliance on the dated 17/09/2017. Done | Sep 17 2017 | On 11-Nov-2015: The factory didn’t shown any O/C. They should be concern with ALLIANCE team. On 20-11-2017: This issue was was not applicable. On 06-Feb-2024: Corrected from previous inspection. This issue is N/A. On 09-Mar-2025: Corrected previously. | Oct 15 2014 | Corrected
Follow Up Inspection |  | 17 | New Finding 1: Mismatch in as-built drawings (Doctor & Childcare Shed, Dining Shed, Generator & Substation) | Building engineer is required to survey the structures and update the as-built drawings | Work done (The factory management reported the remediation completion.) | Apr 6 2024 | On 06-Feb-2024: During inspection, mismatches were found in the as-built drawings of Doctor & Childcare Shed, Dining Shed, Generator & Substation. Building engineer is required to survey the structures and update the as-built drawings. On 09-Mar-2025: As-built drawings are prepared and submitted to RSC. During the verification inspection, discrepancies were found between the provided as-built drawings and the actual onsite conditions. These inconsistencies will be addressed in the review comments. Building engineer is required to survey the structures, update the as-built drawings and submit to RSC. RPO Comments: On 16-Feb-2026 the design documents EA have been reviewed and accepted by RSC. The factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 18 | New Finding 2: Apparent inadequate connection of steel truss due to uplift pressure of wind (Dining Shed) | Building engineer is required to check the adequacy of steel connections. | Work done (The factory management reported the remediation completion.) | Apr 6 2024 | On 06-Feb-2024: During inspection, steel truss to brickwall connection seems apparently inadequate. Building engineer is required to check the adequacy of connection due to uplift pressure of wind. On 09-Mar-2025: This issue is required to be covered in EA. Connection adequacy checks have been conducted, and the relevant calculations have been submitted to RSC, which is now under review. However, the factory has already completed the remediation work. RPO Comments: On 16-Feb-2026 the design documents EA have been reviewed and accepted by RSC. The factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification

## Fire
Date
18-Feb-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A&A Trousers Ltd, Haribari Tak, Pubail Collage Gate, Pubail, Gazipur Sadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-07-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | All doors along the path of egress are wider than 0.8 m in all buildings. 5 staircases are available in 3 story main composite building and 5 doors are connected with 5 stairs on each floor. Among them 4 are emergency exit doors and those are collapsible type gates with roll down shutters. The other exit door is a swing type glass door. No door has required fire rating. | Install outward opening, side-swinging, self-closing, non-lockable fire doors of required fire ratings. | We have already rectified those fire doors. Done | Feb 7 2016 | On 05/03/2018: Corrected. On 12.07.2018: Corrected. On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Refer to the issue no-30. On 01/08/2023: Corrected as per previous follow up. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Oct 31 2014 | Corrected
Initial Inspection |  | 2 | All of the doors in the means of egress are collapsible gates with roll down shutters and sliding type steel doors. | Replace all non-compliant doors and frames in the means of egress with doors that are listed, approved, automatic-closing, side-swinging, fire rated doors in compatible fire rated frames with latching panic hardware. | Corrected | Jul 20 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Oct 31 2014 | Corrected
Initial Inspection |  | 3 | There are collapsible gates with locking arrangements like hasps, locks, slide bolts at the exit doors but doors are not locked. | Provide 1 hr fire protective opening assemblies in 2 hr rated exit enclosures. Remove all hasps, locks, slide bolts, or other locking devices at the noted locations. Doors may be locked only where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. Turning a door handle and disengaging a lock are considered two motions. | Corrected | Jul 20 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Aug 22 2014 | Corrected
Initial Inspection |  | 4 | There is a Penetration in the separation wall of the compressor room and production floor in the dry process shed. 5 staircases are available in 3 story main building and 5 doors are connected with those stairs on each floor. The doors leading towards the staircase do not have required ratings. Door openings are available in accessories store and finished goods store with the cutting section, and same type of door opening is also in the pump house on the ground floor of 3 story main building. | Seal the Penetrations with proper fire-resistant sealants in all fire resistance rated walls. Seal openings that are not required with fire resistant construction barriers. | Corrected | Dec 30 2015 | On 05/03/2018: Corrected. On 12/07/2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Oct 31 2014 | Corrected
Initial Inspection |  | 5 | 3 story main composite building is a non-rated construction and area of per floor is 30,000 sft which is greater than 22,000 sft. So, in accordance with the requirements of Alliance Standard Section 3.5.3.1 automatic sprinkler system is required for this building. Automatic sprinkler system is not installed in this building. | Install an automatic sprinkler system throughout the building designed by a qualified fire protection engineer comply with NFPA 13. Suggested deadline for start design within 31-Oct-14, complete design within 23-Jan-14 and begin construction within 17-Apr-15. | Fire sprinkler systems designed and installed by a fully qualified engineer in accordance with NFPA 13 regulations | Jul 31 2016 | For previous comments, see the earlier reports. On 26/07/2022: The factory is required re Pre-T&CVI on site after modification of work, documents and drawings. See the Pre T&CVI report (26-July-2022) for details. On 29/03/2023: According to the Pre-T&C inspection report again on-site Pre-T&C inspection is required. See the Pre-T&CVI report for details. On 01/08/2023: Reportedly the modification work of Sprinkler System has been completed. Factory has submitted the documents of Pre T&C VI to RSC on dated 27 July 2023. On 21-Dec-2023: Pre-T&C found that the system is ready for full functional T&CVI. See details in Pre T&CVI report. On 06-Feb-2024: T&CVI found that the suppression system requires final verification inspection (FVI). See detail in the T&CVI report. On 16-Oct-24: FVI found that the Fire Pump system requires another final verification inspection (FVI). See detail in the FVI report. On 22-May-25: Final verification was conducted along with the follow-up inspection. Final Verification found that another Final Verification is required. For details, please see the FVI report. On 25-Sep-25: Final verification was conducted along with the follow-up inspection. FVI found that SUPS is approved. See details in the FVI report. | Apr 17 2015 | Corrected
Initial Inspection |  | 6 | 5 staircases are available in 3 story main composite building and all staircases are protected with brick wall of required rating. Here 5 doors are connected with 5 stairs on each floor. Among them 4 are emergency exit doors and those are collapsible type gates with roll down shutters. Other exit door is swing type glass door. No doors have required ratings, which fails to provide those exit enclosures with a fire-resistant rated construction barrier. Other buildings are single story and no stairs are available there. | Install outward opening, side-swinging, self-closing, non-lockable fire doors of 1 hr rating in all stairwell enclosures. | We have already rectified those fire doors. Done | Feb 7 2016 | On 10/10/2017: Corrected in 4th F-up inspection. In 5th F-up inspection its found that in some door the door coordinator is not working properly. On 05/03/2018: On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Refer to the issue no-30. On 01/08/2023: Corrected as per previous follow up. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Oct 31 2014 | Corrected
Initial Inspection |  | 7 | An automatic sprinkler system is required in the 3 story production building but no sprinkler system or fire pump was available. | Install dedicated fire pump following the requirements of NFPA 20. Fire pump installation is to be tested for final acceptance in presence of Alliance and a final inspection of the installation shall be conducted by the Alliance prior to final acceptance of the installation. Acceptance testing of the installation shall be in accordance with NFPA 20, 22, and 24 testing requirements. Documentation of all testing shall be submitted to the Alliance for review prior to final acceptance. | Fire pump system installed in accordance with NFPA 20 | Jul 31 2016 | For previous comments, see the earlier reports. On 26/07/2022: The factory is required re Pre-T&CVI on site after modification of work, documents and drawings. See the Pre T&CVI report (26-July-2022) for details. On 29/03/2023: According to the Pre-T&C inspection report again on-site Pre-T&C inspection is required. See the Pre-T&CVI report for details. On 01/08/2023: Reportedly the modification work of Sprinkler System has been completed. Factory has submitted the documents of Pre T&C VI to RSC on dated 27 July 2023. On 21-Dec-2023: Pre-T&C found that the system is ready for full functional T&CVI. See details in Pre T&CVI report. On 06-Feb-2024: T&CVI found that the suppression system requires final verification inspection (FVI). See detail in the T&CVI report. On 16-Oct-24: FVI found that the Fire Pump system requires another final verification inspection (FVI). See detail in the FVI report. On 22-May-25: Final verification was conducted along with the follow-up inspection. Final Verification found that another Final Verification is required. For details, please see the FVI report. On 25-Sep-25: Final verification was conducted along with the follow-up inspection. FVI found that SUPS is approved. See details in the FVI report. | Apr 15 2015 | Corrected
Initial Inspection |  | 8 | Document or certificate by appropriate authority for training on fire fighting, first aid and rescue is not available. | Train at least 25% of workers in fire fighting, first aid and rescue by the proper authority. | Corrected | Dec 31 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected. On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Jan 23 2015 | Corrected
Initial Inspection |  | 9 | In 3 story main building, 1st and 2nd floor is separated with steel composite structure, which is non-rated. Therefore, the floor separation cannot be considered as a fire resistant rated barrier. | Provide fire-resistant rated construction barriers between floors. Consult a qualified fire protection engineer to design the rated construction barriers. | Designed by a qualified engineer and provided with a fire resistant barrier | Feb 8 2016 | For previous comments, see the earlier reports. On 26/07/2022: The factory is required re Pre-T&CVI on site after modification of work, documents and drawings. See the Pre T&CVI report (26-July-2022) for details. On 29/03/2023: According to the Pre-T&C inspection report again on-site Pre-T&C inspection is required. See the Pre-T&CVI report for details. On 01/08/2023: Reportedly the modification work of Fire Protection System has been completed. Factory has submitted the documents of Pre T&C VI to RSC on dated 27 July 2023. On 21-Dec-2023: Pre-T&C found that the system is ready for full functional T&CVI. See details in Pre T&CVI report. On 06-Feb-2024: T&CVI found that the suppression system requires final verification inspection (FVI). See detail in the T&CVI report. On 16-Oct-24: FVI found that the Fire Pump system requires another final verification inspection (FVI). See detail in the FVI report. On 22-May-25: Final verification was conducted along with the follow-up inspection. Final Verification found that another Final Verification is required. For details, please see the FVI report. On 25-Sep-25: Final verification was conducted along with the follow-up inspection. FVI found that SUPS is approved. See details in the FVI report. | Oct 31 2014 | Corrected
Initial Inspection |  | 10 | On 1st floor of 3 story RCC building, there is a spot removing room with a glass barrier and a LP gas cylinder shed on the east side and adjacent to the 3 story main building where a maintenance room is found. Both rooms are without any construction barrier. | Provide fire-resistive rated construction barrier according to Table 4.1.1 from BNBC Part 4. Consult a qualified fire protection engineer to design the required rated construction barrier. | Corrected | Dec 30 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Refer to Issue-39. | Jan 23 2015 | Corrected
Initial Inspection |  | 11 | No fire department connection was found in any location. | Install fire department connections where required and in compliance with the Standard. Fire department outlet connections shall be provided to allow fire department pumper vehicles to draw water from ground-level or underground water storage tanks. Connections shall match the Fire Service and Civil Defense hose thread standard. | Corrected | Jul 20 2015 | On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Jan 23 2015 | Corrected
Initial Inspection |  | 12 | Fabrics are stored underneath the cutting tables in the cutting section on the ground floor of 3 story main production building. | Remove all combustibles stored underneath the cutting tables at the noted locations as soon as possible. | Corrected | Jul 20 2015 | On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: See Issue No. 34. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Jan 23 2015 | Corrected
Initial Inspection |  | 13 | No available plan or record is found of conducting periodic tests for the emergency battery backup for illumination of exit signs. | Develop a testing and maintenance program that ensures the emergency power for exit signs is tested at least once per year. If battery operated signs are used, these lights are tested on a monthly basis. Functional testing of battery powered signs is provided for a minimum 90 min once per year. | Corrected | Nov 30 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 5 2014 | Corrected
Initial Inspection |  | 14 | No documentation of any training program in accordance with the Alliance Safety Training Curriculum was found. The factory authority arranged for some training not following Alliance curriculum. | Impart training in accordance with Alliance Safety Training Curriculum and keep records with proper documentation. | Corrected | Jul 20 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 5 2014 | Corrected
Initial Inspection |  | 15 | 5 staircases are available in 3 story main building. All stairs except stair-5 on the north side are provided with only one side handrail. The maximum width of a stair is 2 m. Therefore, intermediate handrails are not required. The height of existing handrails is minimum 33 inch for all stairs. | Provide handrails on both side of each stairway. Provide handrails mounted between the range 865 mm (34 in.) and 965 mm (38 in). | Corrected | Feb 6 2016 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Jan 23 2015 | Corrected
Initial Inspection |  | 16 | Records of verifying emergency power for means of egress illumination were not found as required. | Develop a testing and maintenance program that ensures the operation of all exit lights is verified at least once per year. If battery-operated lights are used, these lights shall be tested on a monthly basis. Functional testing of battery powered lights shall be provided for a minimum 90 min once per year. | Corrected | Nov 30 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 5 2014 | Corrected
Initial Inspection |  | 17 | Extinguishers are inspected monthly by serving agent, but no documents are found in support of (i) annual maintenance of extinguishers by a servicing agent and (ii) annual testing of nozzle of CO2 extinguisher. These are required as per NFPA 10. | Fire extinguishers are to be inspected, tested, and maintained in accordance with NFPA 10 Chapter 7 as demanded in Alliance Standard Part 13 Section 13.10.3. | Corrected | Jul 20 2015 | On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Jan 23 2015 | Corrected
Initial Inspection |  | 18 | Occupant loads are not posted in any assembly or production floor. | Post the occupant load for every assembly and production floor in a conspicuous space near the main exit or exit access doorway for the space. | Corrected | Jul 20 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 5 2014 | Corrected
Initial Inspection |  | 19 | An automatic fire alarm and detection system is available in the factory, but currently there is no monitoring company in Bangladesh. Fire service and civil defense is not capable of monitoring fire alarm and detection systems of the factories. | Arrange for direct connection of the fire alarm system to a central monitoring station or Fire Service and Civil Defense. Until that time that monitoring can be set up, arrange a monitoring system using factory's central detection system and personnel. A person shall be assigned to contact the fire department in the event of fire alarm activation. | An automatic fire alarm and detection system is available in the factory. All the findings mentioned in the last pre T & CVI have been resolved/completed. | Feb 7 2016 | For previous comments, see the earlier reports. On 26/07/2022: The factory is required re Pre-T&CVI on site after modification of work, documents and drawings. See the Pre T&CVI report (26-July-2022) for details. On 29/03/2023: According to the Pre-T&C inspection report again on-site Pre-T&C inspection is required. See the Pre-T&CVI report for details. On 01/08/2023: Reportedly the modification work of Fire Alarm System has been completed. During the inspection the panel was found active with remarkable trouble; However, Factory has submitted the documents of Pre T&C VI to RSC on dated 27 July 2023. On 21-Dec-2023: Pre-T&C found that the system is ready for full functional T&CVI. See details in Pre T&CVI report. On 06-Feb-2024: T&CVI found that the fire alarm system is approved. See detail in the T&CVI report. On 22-May-25: Corrected. The fire alarm and detection system was active, and the FACP was free of any abnormal condition during the inspection. On 25-Sep-25: Corrected. The Fire Alarm and Detection System was found active and free of any abnormal conditions during the inspection. | Sep 5 2014 | Corrected
Initial Inspection |  | 20 | No occupancy certificates are available for any buildings on the factory premises. | Apply to PWD for issuance of occupancy certificates and pursue the matter's expedition. | Corrected | Feb 5 2016 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 19 2014 | Corrected
Initial Inspection |  | 21 | A written housekeeping policy was not found. | Establish written corporate and plant policies on housekeeping to ensure scheduled cleaning for floor, wall, ceiling, supply and return air ventilation systems. Promptly reschedule skipped cleanings. Provide a documented line of authority for authorizing a cleaning delay and rescheduling. As a general rule the maximum tolerable deposit thickness for loose fluffy lint is 13 mm (½ in.) over a maximum of 46.5 m2 (500 ft2). Limit dense deposits to 6 mm (¼ in.) and oil saturated deposits to 3.2 mm (⅛ in.). | Corrected | Jul 20 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected as last follow up On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Mar 17 2015 | Corrected
Initial Inspection |  | 22 | The trade license, BERC license, fire license and acid license are not up-to-date. | Obtain or renew all the licenses and permits required from the proper issuing authority. | Corrected | Dec 30 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected as per last follow up On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 5 2014 | Corrected
Initial Inspection |  | 23 | Fire Department pre-planning has not been completed yet. | Complete fire department pre-planning activities with the local Fire Service and Civil Defense. | Corrected | Feb 7 2016 | On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 5 2014 | Corrected
Initial Inspection |  | 24 | A hot-work permit program is not established yet. However, hot-work is not taking place in the factory right now. | Develop a hot-work permit program. The program must comply with the requirements of NFPA 51B | Corrected | Jul 20 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected as last follow up On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected as per previous FUI. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Jan 23 2015 | Corrected
Initial Inspection |  | 25 | Temporary signs with stair designations and floor level identification was found on printed white paper. | Install signage adjacent to each stair door indicating the stair name and the floor level at the noted locations in both English and Bengali. | Corrected | Jul 20 2015 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Sep 5 2014 | Corrected
Follow Up Inspection |  | 26 | New Finding (2nd Follow-up): Manual on-off switch is provided for emergency lighting units. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | We have already removed on/off switch's from emergency light ( 01 emergency Light)-. Done | Feb 6 2016 | On 05/03/2018: Corrected. On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding (2nd Follow-up): Boiler & compressor is located in a same room and is not properly separated by fire rated construction from each other. Location: Shed building (East side). | Boilers or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr (2-hr for high-rise building) fire rated construction (wall, floor, slab etc.). Seal all Penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. | Corrected | Feb 6 2016 | On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding (2nd Follow-up): Penetrations through floor/ceiling assemblies are found unsealed. Location: 1st floor & 2nd floor MDB panel adjacent to North-East exit stair. | Seal all Penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. | We have already relocated those MDB from 1st & 2nd floor and sealed the penetrations. Done | May 15 2016 | On 05/03/2018: Corrected. On 12.07.2018: Corrected as per previous follow up On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 29 | New Finding (2nd Follow-up): Penetrations through floor/ceiling assemblies are found unsealed. Location: 1st floor & 2nd floor MDB panel adjacent to North-East exit stair. | Seal all Penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. | We have already reorganized our storage area proper system. Done | May 15 2016 | On 12.07.2018: Corrected On 09/01/2019: Corrected. On 17/11/2019: Corrected. On 26/07/2022: Corrected. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 30 | New Finding(7th follow up):During inspection some fire rated doors were found physically damaged and some were found open using external materials where required accessories were nonfunctional. | Change the damaged fire rated doors with credible and required rating. Ensure proper functionality of all installed fire rated doors with required accessories, if any door requires to keep open ensure compliant interfacing with functional fire alarm system. | Most of the findings observed in the last pre T & CVI have been resolved and some new fire doors are being procured to be installed. We will complete all the jobs within the time line accepted by RSC. | Sep 17 2018 | For previous comments, see the earlier reports. On 26/07/2022: Fire door coordinators, door closer, Positive latching system, magnetic door holders in various location have been found non-functional & Few fire doors were observed kept opened by unauthorized manner. So fire separation is not being maintained. On 29/03/2023: Fire doors coordinator & Positive latching were not properly working. Several door were physical damaged. Additionally, Unprotected openings were found in between floor and stairs. On 01/08/2023: The Factory has replaced the damage doors by fire rated doors. During the inspection the doors were found functional. However, Factory shall provide the listed documents of existing rated doors. On 21-Dec-2023: Corrected. During Inspection fire door found functional. On 22-May-25: Corrected. On 25-Sep-25: Corrected. | Within 2 Month | Corrected
Follow Up Inspection |  | 31 | New Finding (10th FUI): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: Ground floor | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Already Emergency light has been completed & illumination level as per rules. | Aug 26 2022 | On 26/07/2022: New Finding. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Issue re-opened. The emergency light was found inadequate in the Laser Room, Ground Floor. On 25-Sep-25: Corrected. Emergency lighting was found adequate in the Laser Room, Ground floor. | Within 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding (10th FUI): Chemical storage area is not separated by fire-rated construction having non functional door and unsealed penetrations and openings. Location: Ground floor/ Washing Section | Separate the chemical storage room by minimum 4-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. Keep 16-points MSDS of all chemicals in the storage area. ** As per BNBC, chemical storage room shall be Type-1 construction. Follow section-2.13 and Table 3.2.1 of BNBC-2006 for the guideline. | We have already Installed New fire door in Chemical store | Sep 26 2022 | On 26/07/2022: New Finding. On 29/03/2023: Corrected. On 01/08/2023: Corrected. On 21-Dec-2023: Corrected. On 22-May-25: Corrected. On 25-Sep-25: Corrected. No Chemical storage was found on the Ground floor/ Washing Section. | Within 2 Months | Corrected
Follow Up Inspection |  | 33 | New Finding (13th FUI): Areas used for combustible storage are not separated by fire rated construction at Ground, 1st and 3rd floor | Provide dedicated storage rooms separated by minimum 1-hr fire rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.4m and maximum area of 23m2 If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Areas used for combustible storage has been removed from at Ground, 1st and 3rd floor. | Feb 21 2024 | On 21-Dec-2023: New Finding. On 22-May-25: In-process storage has been found exceeding the limits on 1st floor, Main Production building. On 25-Sep-25: Corrected. The in-process storage was found within the limits on the 1st floor, Main Production Building. | Within 2 months | Corrected
Follow Up Inspection |  | 34 | New Finding (13th FUI): Fabrics are stored underneath the cutting tables in the cutting section on the ground floor of 3 story main production building. | Remove all combustibles stored underneath the cutting tables at the noted locations as soon as possible. | All fabric has been removed from under the cutting table. | Jan 21 2024 | On 21-Dec-2023: New Finding. On 22-May-25: Still storage was observed underneath the cutting table on the 1st floor, Main Production Building. On 25-Sep-25: Corrected. The factory has sealed the cutting table cabinets with boards and storage was not found underneath the cutting table on the 1st floor, Main Production Building. | Within 1 month | Corrected
Follow Up Inspection |  | 35 | New Finding (14th FUI): Aisles have not been found in several locations of the building. Location: 2nd, 3rd Floor, Main Production Building. | Aisles shall be provided at all required places and the minimum unobstructed clear-width of aisles is 0.9 m (36 in.) | Aisles provided at all required places and the minimum unobstructed clear-width of aisles is 0.9 m (36 in.) | Jun 22 2025 | On 22-May-25: New Finding. On 25-Sep-25: Corrected. The required aisle marks have been provided on the 2nd & 3rd floors. | Within 1 month | Corrected
Follow Up Inspection |  | 36 | New Finding (14th FUI): Storage has been observed in the dining area. Location: Dining Shed. | Remove storage from the dining area. | Storage has been removed from the dining area. | May 25 2025 | On 22-May-25: New Finding. On 25-Sep-25: Corrected. Storage was not found inside the Dining Shed during the inspection. | Immediately | Corrected
Follow Up Inspection |  | 37 | New Finding (14th FUI): During the inspection fire rated door coordinators were not worked and doors were not latched properly. Location:2nd & 3rd floor of the building. | The maintenance work shall have to be done for the door accessories on a regular basis. Repair/ replace the unworkable accessories. | The maintenance work has been done & now the doors are latching properly. | Jun 22 2025 | On 22-May-25: New Finding. On 25-Sep-25: Corrected. The fire-rated doors were found functional, interfaced with the FACP and door accessories were working properly. | Within 1 month | Corrected
Follow Up Inspection |  | 38 | New Finding (15th FUI): Storage was located in the exit stair/stair enclosure. Location: Stair-1, Stair-2 & Stair-3 enclosures of Roof Top (above 3rd floor), Main Production Building. | Remove all storage from exit stairs and egress path in accordance with section 13.8 of RSC Technical Guidelines (Standard)¹ V1.0. Means of egress shall be maintained continuously free and clear of all obstructions or impediments to full instant use in the case of fire or other emergency. No furnishings, decorations, or other objects shall obstruct exits and access to exits. Nothing shall obstruct or impede visibility to exits. | work done . | Sep 28 2025 | On 25-Sep-25: New Finding. RPO Comments: On 10-Dec-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 03 days | Pending Verification
Follow Up Inspection |  | 39 | New Finding (15th FUI): Liquefied or compressed gas cylinders (02 no's)were located within the factory on ground floor east side without adequate fire separation. Location: Near Medical & Childcare Room. | Remove the liquefied or compressed flammable gas cylinders. The storage or use of liquefied or compressed flammable gas (LPG/CNG) cylinders within the factory building as per section 3.4.2.1.11 of RSC Technical Guidelines (Standard)¹ V1.0. Or, Factory shall follow the requirements RSC Published "SUPPLEMENTARY PAPER ON TECHNICAL GUIDANCE NOTE FOR USE OF LIQUIFIED OR COMPRESSED FLAMMABLE GAS IN FACTORY PREMISES" to use or store liquefied or compressed flammable gas cylinders in the factory premises. | Work done . (The factory had submitted a gate pass and picture where cylinder not found) | Dec 25 2025 | On 25-Sep-25: New Finding. RPO Comments: On 16-Feb-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification

## Electrical
Date
18-Feb-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A&A Trousers Ltd, Haribari Tak, Pubail Collage Gate, Pubail, Gazipur Sadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-07-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Workers that operate and maintain the electrical system have not received electrical safety training. | Develop and implement an electrical safety program. Include key topics such as lock out tag out procedures, personal protective equipment requirements, etc. Reference NFPA 70e for example program requirements. | we already provided training program about electrical safety training for all electrician & worker .also we provide electrical safety training by alliance training equipment and by show drama. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 2 | Electrical equipment is not efficiently earthed and properly connected to the required number of earth electrodes. All equipment earthing connections are provided from one earth bus bar, and earth and neutral connection from common bus bar. | Provide earthing of equipment at required locations and connect to required number of electrodes. Refer to the BNBG for required number of electrodes. | we have six (6) earthing electrode .2 for body earthing( LT/transfer/DB)2 for transformer neutral and one for generator body earth & lighting arrestor | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 3 | Distribution boards are metal enclosed without dead front construction. Location: All distribution boards. | Ensure distribution boards are metal enclosed with a dead front construction. | we already all metal enclosed replace from dead front construction | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 4 | Light fixtures without protective covers are installed in storage areas. | Ensure light fixtures without protective covers are not installed in storage areas or in any area where the Inspector of the Factories Rules disallows these fixtures. | Corrected | May 30 2016 | On 15th Feb 2016: Corrected. On 2nd May 2016: This issue rise again due to poor maintenance. New timeline is given till 30th-May-2016. On 07/03/2017: Not Corrected. On 05/06/2017: Not corrected. On 10/10/2017: Corrected. | 30/05/2016 | Corrected
Initial Inspection |  | 5 | Emergency power switchboards, distribution boards, and circuits are not properly identified. | All boxes and enclosures (including transfer switches, generators, and power panels) for emergency circuits shall be permanently marked so they will be readily identified as a component of an emergency circuit or system. The required marking can be by color code, the words “emergency system,” or any other method that identifies the box or enclosure as a component of the emergency system. | we already mark emergency switch on all DB . | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 6 | Electrical diagram of main distribution circuit and floor levels circuits connecting electrical loads (machines/lights/cooling system etc.) are available at site but it is not as built. | Have a qualified electrical engineer develop an as-built single line diagram detailing key components and capacity of the electrical system. | Corrected | Dec 31 2015 | On 15th Feb 2016: This issue is not corrected yet. New committed timeline is given till 31- December-2015. On 2nd May 2016: Not corrected. SLD needs modification. On 07/03/2017: Not Corrected. SLD is not as built. On 05/06/2017: Not corrected. On 10/10/2017: Corrected. | 31/12/2015 | Corrected
Initial Inspection |  | 7 | Distribution boards are not provided with adequate clearance. Location: SDB-02/Boiler Room. | Provide clearance of at least 1 m (39 in) in front of distribution boards. | we already replace water tank in front DB in the boiler room. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 8 | Panel boards are installed within 2.5 m of washing unit in washing area. | Ensure panel boards are not installed within 2.5m of any washing unit in washing rooms or laundries. | we already replace dryer machine in front MDB . | Sep 20 2015 | On 2nd May 2016: Corrected. On 15th February 2016: The panel has been relocated. | 20/09/2015 | Corrected
Initial Inspection |  | 9 | Electrical cables are not sized according to capacity of circuit breakers. | Consult with a qualified Electrical Engineer and ensure electrical cables are sized according to capacity of circuit breakers. | we already changed problem circuit Breaker. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 10 | Multi looping and bunch of cables observed at circuit breakers within distribution boards. Location: LT Panel/Substation Room. | Remove multi looping and bunch of cables at circuit breakers within distribution boards. | All multi looping connection already removed from LT panel Board. Change old LT panel Board. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 11 | Cable trenches are not covered properly. Location: Beside COS/Generator Room. | Provide adequate cover on cable trench. | Already all cables are rearrange by trenches in the cos/generator room. | Sep 20 2015 | On 15th February 2016: Ensure adequate cover for cable trench using checkered plate bearing floor height. On 2nd May 2016: Corrected. | 20/09/2015 | Corrected
Initial Inspection |  | 12 | Indications of overheating were observed at some locations during thermography. | Find out the cause of overheating and take proper action including replacing cable or equipment where necessary. | We already completed maintenance work those findings area and rectify all over heating area. | Dec 20 2015 | On 15th Feb 2016: It seems that previous issues were corrected, but hot spot found at other points. This is an urgent issue. Check the point immediately and take necessary steps. On 2nd May 2016: Not corrected. Thermographic scanning is not conducted yet. On 07/03/2017: Corrected. No overheating observed during inspection. | 20/12/2015 | Corrected
Initial Inspection |  | 13 | Wiring systems are not selected and erected considering the effect of damage caused by ingress of water. | Ensure wiring systems are selected and erected so that no damage is caused by the ingress of water. | we already replace MDB 2 safe position. | Sep 20 2015 | On 15th February 2016: The panel has been relocated. On 2nd May 2016: Corrected. | 20/09/2015 | Corrected
Initial Inspection |  | 14 | Each circuit is not provided with a dedicated neutral. | Provide dedicated neutral for each circuit. | We have already completed dedicated neutral installation for each circuit. | Mar 31 2016 | Factory Asking Timeline: 15/2/2017. On 15th Feb 2016: This issue is not corrected yet. New committed timeline is given till 31- December-2015. New extended timeline from 31/12/15 to 31/03/2016. On 2nd May 2016: Not corrected. On 07/03/2017: Not Corrected. On 05/06/2017: Corrected. | 31/03/2016 | Corrected
Initial Inspection |  | 15 | No design and document found to verify the required spacing of vertical and horizontal conductor. | Consult with an expert engineer to have design and drawing of lightening protection system and ensure your building is secured. | LPS installation work already stated and work completion date is 31/05/2017 (consultant BD Technology). | Mar 31 2016 | On 15th Feb 2016: This issue is not corrected yet. New committed timeline is given till 31- December-2015. New extended timeline from 31/12/15 to 31/03/2016. On 2nd May 2016: Not corrected. Design needs more information. Installation is not started yet. On 07/03/2017: Not Corrected. Installation is not started yet. On 05/06/2017: Not corrected. On 10/10/2017: Corrected. | 31/03/2016 | Corrected
Initial Inspection |  | 16 | 1 Nos down conductor is found. No such design and drawing found to identify down conductors are installed based on the building size. | Consult with an Expert electrical engineer to make sure your system have appropriate numbers of down conductors are installed based on the building size. | LPS installation work already started and work completion date is 31/05/2017 (consultant BD Technology). | Mar 31 2016 | On 15th Feb 2016: This issue is not corrected yet. New committed timeline is given till 31- December-2015. New extended timeline from 31/12/15 to 31/03/2016. On 2nd May 2016: Not corrected. Design needs more information. Installation is not started yet. On 07/03/2017: Not Corrected. Installation is not started yet. On 05/06/2017: Not corrected. On 10/10/2017: Corrected. | 31/03/2016 | Corrected
Initial Inspection |  | 17 | The lightning protection ground terminals are not bonded to the building or structure grounding. | Consult with a professional electrical engineer to verify the lightning protection ground terminals are bonded to the building or structure grounding. | we already prepared Lightning protection system diagram. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 18 | No document is found to check presence of harmful substances such as PCBs in transformer oil of main service transformer. | Consider replacing transformers with harmful substances to reduce health hazards. | We have PCBs test certificate | Aug 30 2015 | Verified at Accord first follow-up inspection. | 30/08/2015 | Corrected
Initial Inspection |  | 19 | All distribution boards are not provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Ensure distribution boards provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | We have already provided MCB stopper those findings Distribution Boards and finally corrected. Done | Dec 31 2015 | On 15th Feb 2016: This issue is not corrected yet. New committed timeline is given till 31- December-2015. On 2nd May 2016:Not corrected. On 07/03/2017: Not Corrected. On 05/06/2017: Corrected. | 31/12/2015 | Corrected
Initial Inspection |  | 20 | Electrical cables are not properly identified. | Ensure the means of identification is obtained by separate color coding, marking tape, tagging, or other approved means. | We have already completed cables identification work properly as per instruction - done. | Dec 31 2015 | On 15th Feb 2016: This issue is not corrected yet. New committed timeline is given till 31- December-2015. On 2nd May 2016:Not corrected. On 07/03/2017:Not Corrected. On 05/06/2017: Corrected. | 31/12/2015 | Corrected
Initial Inspection |  | 21 | Distribution boards have no permanent identification markings. | Ensure clear and permanent identification marks are painted in all distribution boards, switchboards, sub main boards and switches. | Now all MDB/SDB permanently marked by paint. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 22 | Distribution boards have no capacity information labels. Location: All distribution boards. | Provide capacity information labels (Maximum current rating, no of circuit breakers etc.) for distribution boards | Now all MDB/SDB has capacity labels. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 23 | Internal components of distribution boards are not properly concealed. Location: All distribution boards. | Provide covers or blanks to conceal all live internal components of switchboards and/or distribution boards. | we already covered and conceal all live internal components of switchboards and/or distribution boards. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 24 | Power and telecommunication or antenna cables are not led in separately. Location: Between MDB-05 & SDB-17/2nd Floor (Main building). | Lead Led telecommunication or antenna cables separately to the main point of service. Power and telecommunications cables must have separate entrance. | we already separate telecommunications cables from power cable. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 25 | Generator frame earthing (grounding) is not provided at two separate points. | Provide two separate points earthing (grounding) provided for generator. | Now generator is connected with two different body earthing (grounding). | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 26 | Electrical wiring and conduit is not properly supported. Location: Electrical wiring and conduit in Main Building (Opposite of Boiler Room). | Provide adequate supports for electrical wiring and conduit. | Electrical wiring and conduct is now properly supported. | Sep 20 2015 | On 15th February 2016: Ensure cable tray/ladder to support cables at any where to keep cable out of tension. On 2nd May 2016: Corrected. | 20/09/2015 | Corrected
Initial Inspection |  | 27 | Electrical connections at equipment, fixtures, etc. are not properly secured. Location: Sewing section/2nd Floor/Main building. | Ensure electrical connections at equipment, fixtures, etc. are properly secured. | Now Electrical connection at equipment , fixtures properly secured. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 28 | Cable sockets are not provided for stranded conductors. Location: MDB-03/ Finished Goods Area/ Main building. | Provide cable sockets for stranded conductors having a nominal cross-sectional area 6mm2 or greater. | Now cable socket provided stranded conductors. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 29 | Improper cable joints are found. | Ensure cable joints through porcelain/PVC connectors with PIB tape wound around joint. | Now cable joint is proper. | Sep 20 2015 | On 15th February 2016: Heat shrink has been used for cable joint. On 2nd May 2016: Corrected. | 20/09/2015 | Corrected
Initial Inspection |  | 30 | No mechanical guards are provided for electrical wiring where necessary. Location: Cable and conduit near COS-03/Substation Room. | Provide mechanical guards for electrical wiring where necessary. | we already provided mechanical guards for electrical wiring in the sub station room, | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 31 | Distribution boards are not clean. Location: SDB-03/ETP. | Disconnect the panel from the electrical service and clean interior components of all dust and debris. Seal all openings within the enclosure to prevent dust and debris from entering. | Now all distribution boards is clean . Also we check periodically. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 32 | Distribution boards are not properly grounded (earthed). Location: SDB-06/PP Section/Dry process Shed. | Provide grounding (earthing) for distribution boards. | Now distribution boards is properly grounded(Earthed). | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 33 | Electrical cable is not properly terminated. | Ensure all electrical cable properly terminated at its point of termination. | Now all electrical cable is properly terminated. | Sep 20 2015 | On 15th February 2016: Unterminated wire was not found. On 2nd May 2016: Corrected. | 20/09/2015 | Corrected
Initial Inspection |  | 34 | Transformer oil analysis is not routinely completed on main service transformer. | Complete an oil analysis on applicable transformers at appropriate intervals based on voltage and power. | now we are routinely check transformer oil and we have record also. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 35 | Non graded electrical insulation mats are provided in front of substation, and distribution boards. | Provide electrical insulation mats in front of distribution boards. | we already provided electrical graded rubber mat under all distribution board. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 36 | No signage indicating the prohibition of light fixtures without protective covers is installed at required locations. | Light fixtures without protective covers (otherwise known as naked lights) shall not be allowed in storage areas or in any area where the Inspector of the Factories Rules disallows these fixtures. Install signs posted in Bengali and English, indicating this prohibition at all entrances to these areas. | we already covered our light all storages areas. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 37 | Inspection, maintenance, and testing procedures of the emergency generator are not completed. Improper document is provided. | Establish a routine maintenance and testing program for the emergency generator. The program shall be based on all of the following: (1) Manufacturer's recommendations. (2) Manufacturer's Instruction manuals. | Now we have check list & maintenance plan and record. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 38 | Inspection, maintenance, and testing procedures of the UPS and IPS are not completed. | Establish an inspection testing, and maintenance program for the Uninterruptable Power Supply (UPS) and associated components. The program must based on the following: (1) Manufacturer's recommendations. (2) Manufacturer's instruction manuals. | Now we have check list & maintenance plan and record. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Initial Inspection |  | 39 | Phase separators are not provided between terminals on circuit breakers. | Install phase separators between terminal connections. Verify phase separators are installed at all remaining locations. | Now every MCCB has phase separator. | Sep 20 2015 | Verified at Accord first follow-up inspection. | 20/09/2015 | Corrected
Follow Up Inspection |  | 40 | New Finding: Transformer Breather oil cup is empty. | Fill the transformer breather oil cup by transformer oil. | Corrected | May 30 2016 | Factory Asking Timeline: 31/5/2017 On 2nd May 2016: This issue is not corrected yet. New timeline is given till 30th-May-2016. On 07/03/2017: Not Corrected. Can not verify this as access barred around transformer. On 05/06/2017: Not corrected. On 10/10/2017: Corrected. | 30/05/2016 | Corrected
Follow Up Inspection |  | 41 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. | We have already provided metal pipe around vertical boiler surface. Done | May 30 2016 | On 2nd May 2016: This issue is not corrected yet. New timeline is given till 30th-May-2016. On 07/03/2017:Not Corrected. On 05/06/2017: Corrected. | 30/05/2016 | Corrected
Follow Up Inspection |  | 42 | New Finding: Cables are laid on floor without any support. | Provide cable tray inside cable drain and cover it by checkered plate. | We have already provided cable try with cover as per instruction in the transformer room . Done | Jun 30 2016 | On 2nd May 2016: This issue is not corrected yet. New timeline is given till 30th-June-2016. On 07/03/2017: Not Corrected. Cable trench makes obstacle. On 10/10/2017: Not Corrected. They buried cable. On 05/03/2018: Not Corrected. Still cables are buried in generator room. On 12/07/2018: Corrected. | 30/06/2016 | Corrected
Follow Up Inspection |  | 43 | New Finding: MCB & Neutral busbar installed outside the panel without any enclosure. | Need to provide electrical graded enclosure | We have already relocated our faulty MDB & SDB at new location where MCB & Neutral busbar installed inside the panel with enclosure. Done | Jul 15 2016 | On 07/03/2017: Not Corrected. Enclosure is not electrical graded. On 05/06/2017: Corrected. The issue related panel board is removed. | 15/07/2016 | Corrected
Follow Up Inspection |  | 44 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust) and overloaded with excessive cables. | Clean all the cable channels/ducts/trench; remove flexible conduit then seal them for permanent (you may use checkered/perforated plate at the bottom). But ensure that 20-25% tray area are kept free. | We have already clean all dust and removed excessive cables form channels.- Done | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Not corrected. On 10/10/2017: Not Corrected. On 05/03/2018: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 45 | New Finding: Power cables entering to or exiting from Distribution board/panel through flexible conduit are not properly fixed. | Power cables entering to or exiting from distribution board/panel must be fixed through Panel base/top plate using cable glands (metal/PVC). You may use cable tray/ladder to support cables. Remove flexible if you face problem to grip cables. | We have already provided cable ladder for fixed power cable- Done | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Not corrected. On 10/10/2017: Not Corrected. On 05/03/2018: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 46 | New Finding: Panel/Distribution boards are inaccessible/do not have enough space in front or can not be opened to perform any maintenance work. | Take necessary initiative thus every panel/distribution board can be easily accessible. | We have already relocated those faulty located distribution boards in the washing section at new compliant location .Done | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Not corrected. On 10/10/2017: Not Corrected. On 05/03/2018: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 47 | New Finding: Separation between LT panels and HT units (Transformer, HT switchgear) is made by iron fencing. | Make a brick built separation between LT and HT units; ensure that after making separator you have adequate ventilation (cross ventilation) and working clearance around each electrical equipment. |  | Jul 15 2016 | On 10/10/2017: Not Corrected. On 05/03/2018: Not Corrected. On 12/07/2018: Not Corrected. On 09/01/2019: Not corrected. On 17-Nov-2019: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 48 | New Finding: Crowded inside panel (MCCB, MCB, Bus bars and Wires). | Additional panels may be installed by redesigning the electrical distribution systems to ease crowding inside panel. | We have already relocated these MDB & SDB with additional panels at new compliant location. Done | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 49 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | We have already removed oversized circuit breaker and provided required adjustable circuit breaker. Done . | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 50 | New Finding: Cables in service are joined (splicing) between terminations. | Joints of cable shall be avoided. For unavoidable cases, existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | We have already removed joint cable from SDB ( Pump Control Board) .Done | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Not corrected. On 10/10/2017: Not Corrected. On 05/03/2018: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 51 | New Finding: a)Panel base plates removed to allow cable entry. b) Cables passing through wall/floor slab are not protected at the entry/exit point(s). | a)Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. b) Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. |  | Jul 15 2016 | On 07/03/2017:Not Corrected. On 05/06/2017:Not corrected. On 10/10/2017: Not Corrected. On 05/03/2018:Not Corrected. On 12/07/2018:Not Corrected. On 09/01/2019: Not corrected. On 17-Nov-2019: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 52 | New Finding: a) Power cables are bent excessively. b) Light fixture are not properly support from the structure. c) Battery terminals are left open and are kept on brick without having any casing. d) Indicator light is mounted without control device. | a) Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. b) Ensure Lighting fixtures are supported from the structure properly; if flexible cords are used to support light fixture then make sure it has enough strength to carry the weight. c) Use insulated rubber cap to cover all the battery terminals and store battery flammable case/shelf. d) Indicator light should be connected with control device such as fuse or MCB. |  | Jul 15 2016 | On 07/03/2017:Not Corrected. On 05/06/2017:Not corrected. On 10/10/2017: Not Corrected. On 05/03/2018:Not Corrected. Still cables are bent excessively. On 12/07/2018:Not Corrected. On 09/01/2019: Not corrected. On 17-Nov-2019: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 53 | New Finding: a)Earth busbar is installed on insulator and Panel doors are not connected with earth. b) Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | a) Provide an additional connection to panel body if earth busbar is installed on insulator, then connect all metal panel doors by at least 4 rm earth cable. b) Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | We have already provided door earthing properly with required cable size. Done | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 54 | New Finding: a) Insulation resistance test of electrical cables is not performed. b) Earth Pit resistance record is unavailable. c) Electric safety training program is not initiated/conducted. d) There is no programmed schedule for periodical inspection & testing of electrical equipment. e) List of circuit or SLD of existing circuits are not available in each electrical panel board. | a) Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). b) All earthing systems shall be tested for resistance on any dry day not less than once in every two years. c) Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. d) Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance). List of circuit or SLD of existing circuits shall be available for each electrical panel board. | We have already rectified those findings issues and Insulation resistance test of electrical cables will be conducted within 31/05/2017. In- progress | Jul 15 2016 | On 07/03/2017: Not Corrected. On 05/06/2017: Not corrected. On 10/10/2017: Corrected. | 15/07/2016 | Corrected
Follow Up Inspection |  | 55 | New Finding: Panel board rusted and broken. | Rusted panel board shall be replaced by new one maintaining proper IP rating. | We have already changed problematic panel board. Done | May 15 2017 | On 05/06/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | Corrected | Oct 8 2017 | On 10/10/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 57 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Oct 7 2017 | On 10/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Generator exhaust system is kept exposed/not insulated. | Provide fabricated removable insulation blanket systems/mechanical guard (conditional) for engine and generator exhaust components to reduce thermal radiation and convection within the engine room. | We have already provided fabricated removable insulation blanket systems for engine and generator exhaust components. Done | Oct 7 2017 | On 10/10/2017: Not Corrected. They had planned to insulate it. On 05/03/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: The engine-mounted radiator/exhaust has positioned at the entrance of the generator room. | Rearrange the generator set; do not place radiator/exhaust to access route of the generator room. Place the generator exhaust to the exterior of the building in a safe location any other side except south. | We have already rearrange our generator room . Done | Oct 8 2017 | On 10/10/2017: Not Corrected. They had planned to rearrange it. On 05/03/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 60 | New Finding: Boiler is found bulging and corrosive. Combustion products are blown back from burner leakage area. Besides that leakage on the steam outlet make the floor wet. | Shutdown the boiler, and take action immediately. Boiler shall be operated again after all necessary test. | Corrected | Dec 6 2017 | On 10/10/2017: Corrected. They disconnected old Boiler. | 7 Days | Corrected
Follow Up Inspection |  | 61 | New Finding: Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Corrected | Dec 5 2018 | On 12/07/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 62 | New Finding: Lightning Protection System (LPS) and drawing is unavailable for dinning. Maintenance is pending for existing LPS. | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is more than 40). Once a LPS is designed properly, installation must be done accordingly asap. |  | Aug 28 2022 | On 29/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/ duct/BBT). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. |  | Aug 28 2022 | On 29/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Aug 28 2022 | On 29/03/2023: Not Corrected. Some progress has been observed. But still found in few panels. On 01-Aug-2023: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Electrical Single Line Diagram (SLD) is available in the factory but it needs some update. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD shall be updated properly when electrical system is modified. | We have updated all mismatch as per SLD | Aug 28 2022 | On 29/03/2023: Not Corrected. Factory submitted the as-built SLD to RSC for review on 17-Nov-2022. On 01-Aug-2023: Not corrected. Still mismatch found with field & SLD (Earth pit marking, CB current setting mismatch, Busbar size mismatch, load identification missing, Exhaust Fan marking). They need to work based on accepted SLD. On 25/04/2024: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Corrected | May 3 2023 | On 01-Aug-2023: Corrected | 1 Month | Corrected