## Structural
Date
25-Feb-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Ind.Ltd., Plot-28, Milk Vita Rd., Section-07, Mirpur, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2013-12-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Verify concrete strengths in internal columns from Ground floor to 4th floor | Maintain current use of the floors and don´t change use or increase occupation, either of which could increase loading. | Corrected DEA approved and retrofitting also have been completed | Jun 30 2017 | On 09/12/2014 The factory did not prepared any loading plan on basis of current use life load & storages. They engages a consulting firm to review structural design and to do DEA. Core sampling & testing work done. The factory will be submit DEA report on 20th January2015. On 23/03/2016 High loading was found in every floor of the building. Loading is required to be reduced in every floor. Factory has done DEA and submitted to ACCORD. Revised DEA is required to submit within the timeline On 10/11/2016 During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval of DEA on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: During inspection load plan was posted on each every floor and live load was found more than the accepted load plan at 1st floor. Factory is required to maintain load as per accepted load plan. On 14/01/2018: During inspection, load plan was observed posted on each and every floor and live load was found below accepted loading (42psf). Factory is required to maintain load as per accepted load plan. On 05/09/2018: Found corrected from previous inspection. During follow up inspection loading was found as per accepted load plan. On 21st November 2018: Corrected previously. Load plans were found posted on floors and loading was observed within load limit. On 14-July-2019: Corrected in previous follow up inspection. During inspection load plans were found posted in each floor and overall loading was observed within the allowable limit (<42 psf) except 1st floor fabric storage. On 11-Dec-2019: Corrected from previous inspection. During inspection, load plan was found posted in each of the floor and loading was found within accepted load limit (<42 psf). On 17-Nov-2020: Corrected from previous inspection. During inspection load plan was found posted & loading was found within allowable limit (42 psf). On 24-May-2022: This issue was corrected from previous inspection. During inspection, load plan was found posted in each of the floor and loading was found within accepted load limit (<42 psf). On 06-Oct-2022: Corrected from previous follow up inspection. During inspection, load plan was found posted to floor and overall loading was found within the allowable accepted loading limit (<42 psf). On 27-Feb-2023: Corrected in the previous follow-up inspection. During inspection loading was found within the load limit (42 psf). Load plan was found posted on each floor. On 15-Jul-2024: Corrected previously. During inspection loading was found within the load limit (42 psf & 63 psf). Load plan was found posted on each floor. | Immediately | Corrected
Initial Inspection |  | 2 | Verify concrete strengths in internal columns from Ground floor to 4th floor | Factory Engineer to review design, loads and columns stresses in area identified above. | Corrected DEA approved and retrofitting also have been completed | Jun 30 2017 | On 09/12/2014 The factory did not prepared any loading plan on basis of current use life load & storages. They engages a consulting firm to review structural design and to do DEA. Core sampling & testing work done. The factory will be submit DEA report on 20th January2015. On 23/03/2016 High loading was found in every floor of the building. Loading is required to be reduced in every floor. Factory has done DEA and submitted to ACCORD. Revised DEA is required to submit within the timeline On 10/11/2016 During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval of DEA on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: A DEA report has been produced and accepted by accord on 28/08/2016. during Retrofitting works are found ongoing. On 14/01/2018: This issue was required to be covered in DEA which was re-accepted by ACCORD on 18th January 2017. On 05/09/2018: Found corrected from previous inspection. With some corrections DEA of the factory was reaccepted from ACCORD on 18th January 2017. On 21st November 2018: Corrected previously. DEA has been reviewed and re-accepted. On 14-July-2019: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 11-Dec-2019: Corrected from previous inspection. DEA of the factory building was re-accepted by ACCORD on 18-Jan-2017. On 17-Nov-2020: Corrected from previous inspection. DEA of the factory was re-accepted by ACCORD on 18-jan-2017. On 24-May-2022: This issue was corrected from previous inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 06-Oct-2022: Corrected from previous follow up inspection. Factory management got DEA re-acceptance from ACCORD on 18-Jan-2017. As per DEA recommendation factory management had completed all remedial works. On 27-Feb-2023: Corrected in the previous follow-up inspection. On 15-Jul-2024: Corrected previously. | Immediately | Corrected
Initial Inspection |  | 3 | Verify concrete strengths in internal columns from Ground floor to 4th floor | Verify insitu concrete stresses either by cores or existing cylinder strength data for cores from 4 columns. | Corrected Column retrofitting work completed & managing loading plan | Jun 30 2017 | On 09/12/2014 The factory did not prepared any loading plan on basis of current use life load & storages. They engages a consulting firm to review structural design and to do DEA. Core sampling & testing work done. The factory will be submit DEA report on 20th January2015. On 23/03/2016 High loading was found in every floor of the building. Loading is required to be reduced in every floor. Factory has done DEA and submitted to ACCORD. Revised DEA is required to submit within the timeline On 10/11/2016: During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval of DEA on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: Cores were taken from columns for verifying insitu concrete strength. It was verified from previous DEA verification inspection. On 14/01/2018: Corrected from previous follow up inspection. On 05/09/2018: Found corrected from previous inspection. Original core test report was available during inspection and core location was matched. On 21st November 2018: Corrected previously. Original core test reports were available during inspection. On 14-July-2019: Corrected in previous follow up inspection. This issue had been covered in DEA report. Factory management got DEA re-acceptance on 18-January-2017. Core test had been done and during inspection original core test report was kept onsite. On 11-Dec-2019: Corrected from previous inspection. Core test was done as part of DEA which was re-accepted by ACCORD on 18-Jan-2017. During inspection original core test report was found. On 17-Nov-2020: Corrected from previous inspection. Core test was carried out as a part of DEA which was re-accepted by ACCORD on 18-Jan-2017. During inspection original core test report was found on-site. On 24-May-2022: This issue was corrected from previous inspection. On 06-Oct-2022: Corrected from previous follow up inspection. Core test had been done as a part of DEA. During inspection original core test report was found on-site. On 27-Feb-2023: Corrected in the previous follow-up inspection. On 15-Jul-2024: Corrected previously. | Immediately | Corrected
Initial Inspection |  | 4 | Verify concrete strengths in internal columns from Ground floor to 4th floor | A Detail Engineering Assessment of Factory to be commenced, see attached Scope. | Corrected Column retrofitting work completed & managing loading plan | Jun 30 2017 | On 09/12/2014 The factory did not prepared any loading plan on basis of current use life load & storages. They engages a consulting firm to review structural design and to do DEA. Core sampling & testing work done. The factory will be submit DEA report on 20th January2015. On 23/03/2016 High loading was found in every floor of the building. Loading is required to be reduced in every floor. Factory has done DEA and submitted to ACCORD. Revised DEA is required to submit within the timeline On 10/11/2016 During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval of DEA on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: Factory management got their DEA acceptance on 28/08/2016 from accord. On 14/01/2018: Corrected from previous follow up inspection. DEA was re-accepted by ACCORD on 18th January 2017. On 05/09/2018: Found corrected from previous inspection. With some corrections DEA of the factory was reaccepted from ACCORD on 18th January 2017. On 21st November 2018: Corrected previously. DEA has been reviewed and re-accepted. On 14-July-2019: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 11-Dec-2019: Corrected from previous inspection. DEA of the factory building was re-accepted by ACCORD on 18-Jan-2017. On 17-Nov-2020: Corrected from previous inspection. DEA of the factory was re-accepted by ACCORD on 18-jan-2017. On 24-May-2022: This issue was corrected from previous inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 06-Oct-2022: Corrected from previous follow up inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 27-Feb-2023: Corrected in the previous follow-up inspection. On 15-Jul-2024: Corrected previously. | Immediately | Corrected
Initial Inspection |  | 5 | Verify concrete strengths in internal columns from Ground floor to 4th floor | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Corrected DEA approved and retrofitting also have been completed | Jun 30 2017 | On 09/12/2014: The factory did not prepared any loading plan on basis of current use life load & storages. They engages a consulting firm to review structural design and to do DEA. Core sampling & testing work done. The factory will be submit DEA report on 20th January2015. On 23/03/2016: High loading was found in every floor of the building. Loading is required to be reduced in every floor. Factory has done DEA and submitted to ACCORD. Revised DEA is required to submit within the timeline On 10/11/2016: During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval of DEA on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: During inspection load plan was found posted on each every floor and live load was observed more than the acceptable limit at 1st floor. Factory is required to maintain load as per accepted load plan. Retrofitting work found ongoing. On 14/01/2018: During inspection, load plan was observed posted on each and every floor and live load was found below accepted loading (42psf). Factory management should maintain load as per accepted load plan. On 05/09/2018: Found corrected from previous inspection. Load plan was found posted in all floors of the building and load was maintained within accepted load plan. On 21st November 2018: Corrected previously. Load plans have been produced and loading was observed within accepted load plan limit (42psf). On 14-July-2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. During inspection load plans were found posted in each floor and overall loading was observed within the allowable limit (<42 psf) except 1st floor fabric storage. On 11-Dec-2019: Corrected from previous inspection. Load plan was produced as part of DEA which was accepted by ACCORD on 18-Jan-2017. During inspection, load plan was found posted in each of the floor and loading was found within accepted load limit (42 psf). On 17-Nov-2020: Corrected from previous inspection. During inspection load plan was found posted & loading was found within allowable limit (42 psf). On 24-May-2022: This issue was corrected from previous inspection. Load plan was produced as part of DEA which was accepted by ACCORD on 18-Jan-2017. During inspection, load plan was found posted in each of the floor and loading was found within accepted load limit (42 psf). On 06-Oct-2022: Corrected from previous follow up inspection. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. During inspection load plans were found posted in each floor and overall loading was found within the allowable limit (<42 psf). On 27-Feb-2023: Corrected in the previous follow-up inspection. During inspection loading was found within the load limit (42 psf). Load plan was found posted on each floor. On 15-Jul-2024: Corrected previously. During inspection loading was found within the load limit (42 psf & 63 psf). Load plan was found posted on each floor. | (within 6-weeks) | Corrected
Initial Inspection |  | 6 | Verify concrete strengths in internal columns from Ground floor to 4th floor | Detail Engineering Assessment to be completed. | Corrected DEA has been approved and retrofitting work and varification work has been completed. This issue still pending due to removal of toilet built-up which also completed. Load plan also being maintaing as per approved load plan | Jun 30 2017 | On 09/12/2014 The factory did not prepared any loading plan on basis of current use life load & storages. They engages a consulting firm to review structural design and to do DEA. Core sampling & testing work done. The factory will be submit DEA report on 20th January2015. On 23/03/2016 High loading was found in every floor of the building. Loading is required to be reduced in every floor. Factory has done DEA and submitted to ACCORD. Revised DEA is required to submit within the timeline On 10/11/2016 During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval of DEA on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: Factory management got their DEA acceptance on 28/08/2016 from accord and retrofitting work found on going. On 14/01/2018: This issue was required to be covered in DEA which was re-accepted by ACCORD on 18th January 2017 in which remediation works were required. Factory management has completed total retrofitting works but has not completed total demolition work of build up at toilet zone. Factory management is required to complete rest of the demolition works immediately. On 05/09/2018: Found corrected from previous inspection. With some corrections DEA of the factory was reaccepted from ACCORD on 18th January 2017. Factory has demolished the toilet floor build up as per recommendation from accepted DEA. On 21st November 2018: Corrected previously. Factory has completed retrofitting works. On 14-July-2019: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 11-Dec-2019: Corrected from previous inspection. DEA of the factory building was re-accepted by ACCORD on 18-Jan-2017. Factory completed all the retrofitting works. On 17-Nov-2020: Corrected from previous inspection. DEA of the factory was re-accepted by ACCORD on 18-jan-2017. On 24-May-2022: This issue was corrected from previous inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 06-Oct-2022: Corrected from previous follow up inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. During inspection factory management had provided all material test reports and QC certificate. On 27-Feb-2023: Corrected in the previous inspection. DEA was re-accepted from ACCORD on 18-January-2017. Required retrofitting works have been completed. On 15-Jul-2024: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 7 | Verify concrete strengths in internal columns from Ground floor to 4th floor | Continue to implement load plan | Corrected DEA approved and retrofitting also have been completed | Aug 30 2016 | On 09/12/2014 The factory did not prepared any loading plan on basis of current use life load & storages. They engages a consulting firm to review structural design and to do DEA. Core sampling & testing work done. The factory will be submit DEA report on 20th January2015. On 23/03/2016 High loading was found in every floor of the building. Loading is required to be reduced in every floor. Factory has done DEA and submitted to ACCORD. Revised DEA is required to submit within the timeline On 10/11/2016 During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval of DEA on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: During inspection load plan was found posted on each every floor and live load was observed more than the acceptable limit at 1st floor. Factory is required to maintain load as per accepted load plan. Retrofitting work found ongoing. On 14/01/2018: During inspection, load plan was observed posted on each and every floor and live load was found below accepted loading (42psf). Factory is required to maintain load as per accepted load plan. On 05/09/2018: Found corrected from previous inspection. Load plan was found posted in all floors of the building and load was maintained within accepted load plan. On 21st November 2018: Corrected previously. Corrected previously. Load plans have been produced and loading was observed within accepted load plan limit (42psf). On 14-July-2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. During inspection load plans were found posted in each floor and overall loading was observed within the allowable limit (<42 psf) except 1st floor fabric storage. On 11-Dec-2019: Corrected from previous inspection. Load plan was produced as part of DEA which was accepted by ACCORD on 18-Jan-2017. During inspection, load plan was found posted in each of the floor and loading was found within accepted load limit (42 psf). On 17-Nov-2020: Corrected from previous inspection. During inspection load plan was found posted & loading was found within allowable limit (42 psf). On 24-May-2022: This issue was corrected from previous inspection. Load plan was produced as part of DEA which was accepted by ACCORD on 18-Jan-2017. During inspection, load plan was found posted in each of the floor and loading was found within accepted load limit (42 psf). On 06-Oct-2022: Corrected from previous follow up inspection. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. During inspection load plans were found posted in each floor and overall loading was found within the allowable limit (<42 psf). On 27-Feb-2023: Corrected in the previous follow-up inspection. During inspection loading was found within the load limit (42 psf). Load plan was found posted on each floor. On 15-Jul-2024: Corrected previously. During inspection loading was found within the load limit (42 psf & 63 psf). Load plan was found posted on each floor. | (within 6-months) | Corrected
Initial Inspection |  | 8 | Cracking on beams at levels 3rd and 4th | Monitor cracks on beams. Conduct regular inspection of cracks. Investigate if cracks are only in the plastering. | Corrected We have repaired cracks as per approved DEA | Aug 30 2016 | On 09/12/2014: The factory engineer or consultant should be monitoring all crack ,erosion and rebar expose and finally including in DEA report how to solve it. On 23/03/2016: Cracks are found on the side beam near supports. Factory Engineer must investigate the reason of cracking and repair and strengthen beam accordingly. On 10/11/2016: This issue already covered with DEA but still monitoring needed. On 15/05/2017: Crack was not repaired properly. Some visible crack was observed during inspection on 4th floor. On 14/01/2018: Cracks have been investigated and some cracks are repaired, but some cracks in slabs soffit were observed during inspection. Factory engineer to investigate the reason & extent of cracks and prepare an investigation report with proper remedial measures. Remediation is required to be implemented as per investigation report for all of the cracks. On 05/09/2018: Factory management has prepared crack investigation report & during follow up inspection no major crack has been observed. Moreover factory has repaired the previous crack surface. Factory management is required to monitor the repaired crack location for any kind of future propagation of crack. On 21st November 2018: Corrected previously. Investigation report was available and cracks were found repaired. On 14-July-2019: Corrected in previous follow up inspection. Factory management had repaired those cracks which were found in beam and also provided an investigation report. During inspection any major cracks were not found. On 11-Dec-2019: Corrected from previous inspection. Factory has repaired the cracks as per investigation report. On 17-Nov-2020: Corrected from previous inspection. Factory has repaired all cracks as per investigation report. On 24-May-2022: This issue was corrected from previous inspection. Factory management had repaired those cracks which were found in beam and also provided an investigation report. During inspection, cracks were not found. On 06-Oct-2022: Corrected from previous follow up inspection. Factory management had repaired those cracks which were found in beam and also provided an investigation report. During inspection, cracks were not found. On 27-Feb-2023: Corrected in the previous follow-up inspection. During inspection, further cracks were not found. On 15-Jul-2024: Corrected previously. During inspection further crack was not found on beams. | (within 6-months) | Corrected
Initial Inspection |  | 9 | Cracking on beams at levels 3rd and 4th | If cracks grow larger, removing all items above the slab and close working areas below the affected areas . Engage an engineer to investigate, repair and strengthen the beams | Corrected We have repaired cracks as per approved DEA | Aug 30 2016 | On 09/12/2014: The factory engineer or consultant should be monitoring all crack ,erosion and rebar expose and finally including in DEA report how to solve it. On 23/03/2016: Cracks are found on the side beam near supports. Factory Engineer must investigate the reason of cracking and repair and strengthen beam accordingly. On 10/11/2016: This issue already covered with DEA but still monitoring needed. On 15/05/2017: Crack was not repaired properly. Some visible crack was seen during inspection. On 14/01/2018: Cracks have been investigated and some cracks are repaired, but some cracks in slabs soffit were observed during inspection. Factory engineer to investigate the reason & extent of cracks and prepare an investigation report with proper remedial measures. Remediation is required to be implemented as per investigation report for all of the cracks. On 05/09/2018: Factory management has prepared crack investigation report & during follow up inspection no major crack has been observed. Moreover factory has repaired the previous crack surface. Factory management is required to monitor the repaired crack location for any kind of future propagation of crack. On 21st November 2018: Corrected previously. On 14-July-2019: Corrected in previous follow up inspection. Factory management had repaired those cracks which were found in beam and also provided an investigation report. During inspection any major cracks were not found. On 11-Dec-2019: Corrected from previous inspection. Factory has repaired the cracks as per investigation report. On 17-Nov-2020: Corrected from previous inspection. Factory has repaired all cracks as per investigation report. On 24-May-2022: This issue was corrected from previous inspection. Factory management had repaired those cracks which were found in beam and also provided an investigation report. During inspection, cracks were not found. On 06-Oct-2022: Corrected from previous follow up inspection. Factory management had repaired those cracks which were found in beam and also provided an investigation report. During inspection, cracks were not found. On 27-Feb-2023: Corrected in the previous follow-up inspection. During inspection, further cracks were not found. On 15-Jul-2024: Corrected previously. During inspection further crack was not found on beams. | (within 6-months) | Corrected
Initial Inspection |  | 10 | Lightweight steel structure on additional mezzanine above G.F. | Addition structures should be designed and upgraded to support code loads by the building Engineer, or they should be vacated and removed. | We have repaired cracks as per approved DEA | Aug 30 2016 | On 09/12/2014: This part should be include in DEA report. On 23/03/2016: Non engineered steel mezzanine is required to be upgraded. During inspection, Significant loading was found above mezzanine. On 10/11/2016: Corrected; During inspection non engineered steel mezzanine found demolished. On 15/05/2017: Found corrected from previous inspection. On 14/01/2018: Corrected from previous follow up inspection. During inspection no steel structure was observed over ground floor mezzanine. On 05/09/2018: Found corrected from previous inspection. Factory has demolished the mezzanine above GF. On 21st November 2018: Corrected previously. Mezzanine floor has been demolished. On 14-July-2019: Corrected in previous follow up inspection. Mezzanine floor was found demolished On 11-Dec-2019: Corrected from previous inspection. No Mezzanine floor was found above G.F. On 17-Nov-2020: Corrected from previous inspection. No Mezzanine floor was found above G.F. On 24-May-2022: This issue was corrected from previous inspection. Mezzanine floor was found demolished. On 06-Oct-2022: Corrected in previous follow up inspection. During inspection mezzanine floor was found demolished. On 27-Feb-2023: Corrected in the previous follow-up inspection. On 15-Jul-2024: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 11 | Water causing damage and corrosion Concrete spalling caused by reinforcement corrosion | Building engineer to inspect slabs in room near washrooms. | Done We have completed repairing of toilet pipe & rainwater pipe | Aug 30 2016 | On 09/12/2014: Work in progress within short time finish all work On 23/03/2016: Factory has not taken any initiative regarding this. Leakage was found in the pipe line and concrete spalling and reinforcement corrosion also observed. On 10/11/2016: During inspection factory engineer told they have repaired some leakage from downpipes and also installing new pipes. Still dampness observed in toilet portion due to water leakage. On 15/05/2017: Factory management have repaired some leakage from downpipes but water leakage was observed in toilet area due to continue retrofitting work at toilet portion. On 14/01/2018: Factory management have repaired some leakage from downpipes but dampness of slab was observed in toilet area due to continuous leakage. So, further remedial measures is required to implement. On 05/09/2018: During follow up inspection dampness of slab was observed. Factory management is required to take proper remedial measures to mitigate the dampness of slab. On 21st November 2018: Dampness was observed below toilet portion beam and slab. Factory Engineer is required to Investigate the cause and take remedial measures to prevent re-occurrence. On 14-July-2019: During inspection dampness was observed in slab and beam in several location specially in toilet areas. Factory management is required to take proper remedial measures to mitigate the dampness. On 11-Dec-2019: Factory has repaired the water causing damage with improper methodology. So, appearance of corrosion & concrete spalling was found near washrooms. Factory engineer is required to investigate the damage and prepare report including proper methodology. Factory is required to follow the recommendation of the report for the repair works. On 17-Nov-2020: During inspection water causing damage was found near washrooms. Moreover, no investigation report was found on site. Factory is required to investigate the damage & prepare report with proper methodology. Factory is also required to repair all damages with suitable method. On 24-May-2022: Building engineer has inspect the slab and suggest a remedial method, which was incorporated in DEA recommendation. On 06-Oct-2022: Corrected from previous follow up inspection. During inspection spalling of concrete was not found. On 27-Feb-2023: Corrected in the previous follow-up inspection. During the inspection spalling of concrete was not found. On 15-Jul-2024: Corrected previously. During inspection dampness and concrete spalling was not found. | (within 6-weeks) | Corrected
Initial Inspection |  | 12 | Water causing damage and corrosion Concrete spalling caused by reinforcement corrosion | Manage drainage from above levels to downpipes to avoid structural corrosion due to continuous moisture. | Corrected we have repaired the downpipe from the roof to facilitate the roof top water soomth passage | May 30 2016 | On 09/12/2014: Work in progress within short time finish all work On 23/03/2016: Factory has not taken any initiative regarding this. Leakage was found in the pipe line and concrete spalling and reinforcement corrosion also observed. On 10/11/2016: During inspection factory engineer told they have repaired some leakage from downpipes and also installing new pipes. Still dampness observed in toilet portion due to water leakage. On 15/05/2017: Factory management have repaired some leakage from downpipes but water leakage was observed in toilet area due to continue retrofitting work at toilet portion. On 14/01/2018: Factory management have repaired some leakage from downpipes but dampness of slab was observed in toilet area due to continuous leakage. So, further remedial measures is required to implement. On 05/09/2018: During follow up inspection dampness & concrete spalling was observed. Factory management is required to take proper remedial measures to mitigate the dampness & concrete spalling surface area. On 21st November 2018: Factory has provided downpipes from the roof to ground floor. On 14-July-2019: Corrected in previous follow up inspection. Factory management had provided downpipes from the roof to ground floor. On 11-Dec-2019: Corrected from previous inspection. Factory management had installed downpipes from the roof to ground floor. On 17-Nov-2020: Corrected from previous inspection. Factory management has installed downpipes from the roof to ground floor. On 24-May-2022: This issue was corrected from previous inspection. Factory management has installed downpipes from the roof to ground floor. On 06-Oct-2022: Corrected from previous follow up inspection. Factory management had installed downpipes from the roof to ground floor. On 27-Feb-2023: Corrected in the previous follow-up inspection. Downpipes have been installed. On 15-Jul-2024: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 13 | Water causing damage and corrosion Concrete spalling caused by reinforcement corrosion | Mitigate water source from washrooms and roof. Manage drainage, waterproof system and isolating layer. | Corrected We have repaired all damages as per suggested in DEA report. | May 30 2016 | On 09/12/2014: Work in progress within short time finish all work On 23/03/2016: Factory has not taken any initiative regarding this. Leakage was found in the pipe line and concrete spalling and reinforcement corrosion also observed. On 10/11/2016: During inspection factory engineer told they have repaired some leakage from downpipes and also installing new pipes. Still dampness observed in toilet portion due to water leakage. On 15/05/2017: Factory management have repaired some leakage from downpipes but water leakage was observed in toilet area due to continue retrofitting work at toilet portion. On 14/01/2018: Factory management have repaired some leakage from downpipes of upper floors but water leakage was observed in toilet area due to continue retrofitting work at toilet portion. On 05/09/2018: During follow up inspection dampness & concrete spalling was observed. Factory management is required to take proper remedial measures to mitigate the dampness & concrete spalling surface area. On 21st November 2018: During inspection, concrete spalling, dampness and rebar corrosion was observed. Factory engineer is required to prepare a investigation report and repair spalling and corrosion according to report recommendation. On 14-July-2019: During inspection some repairmen work was found but still concrete spalling, dampness was observed in several locations. Factory management is required to take proper remedial measures to solve this issue. On 11-Dec-2019: Factory has repaired the water causing damage with improper methodology. So, appearance of corrosion & concrete spalling was found near washrooms. Factory engineer is required to investigate the damage and prepare report including proper methodology. Factory is required to follow the recommendation of the report for the repair works. On 17-Nov-2020: During inspection water causing damage was found near washrooms. Moreover, no investigation report was found on site. Factory is required to investigate the damage & prepare report with proper methodology. Factory is also required to repair all damages with suitable method. On 24-May-2022: During inspection water causing damage was found near washrooms. Factory is also required to repair all damages with suitable method as per suggested in DEA report. On 06-Oct-2022: During inspection dampness was found near washrooms. Factory is required to repair all damages with suitable method as per suggested in DEA report. On 27-Feb-2023: Dampness has been repaired near the washrooms. During the inspection, no dampness was found. On 15-Jul-2024: Corrected previously. During inspection roof drainage system was found improved. | (within 6-months) | Corrected
Initial Inspection |  | 14 | Water causing damage and corrosion Concrete spalling caused by reinforcement corrosion | If required, specify a treatment system for corrosion and concrete repair | Corrected We have repaired all damages as per suggested in DEA report. | May 30 2016 | On 09/12/2014: Work in progress within short time finish all work On 23/03/2016: Factory has not taken any initiative regarding this. Leakage was found in the pipe line and concrete spalling and reinforcement corrosion also observed. On 10/11/2016: During inspection factory engineer told they have repaired some leakage from downpipes and also installing new pipes. Still dampness observed in toilet portion due to water leakage. On 15/05/2017: Factory have repaired the damages at columns due to water leakage from drainage pipe. But the drainage pipe has not been repaired properly which may causes continuous water intrusion in repaired column. So factory must repair all drainage pipes immediately. On 14/01/2018: Factory management have repaired dampness at some columns and slabs due to water leakage from drainage pipe. But the drainage pipe has not been repaired properly which may causes continuous water intrusion in repaired columns. So factory must repair all drainage pipes immediately. On 05/09/2018: During follow up inspection reinforcement corrosion & spalling of concrete was observed. Factory management is required to take proper remedial measures to mitigate the dampness & concrete spalling. On 21st November 2018: During inspection, concrete spalling and rebar corrosion was observed. Factory engineer is required to prepare a investigation report and repair spalling and corrosion according to report recommendation. On 14-July-2019: During inspection some repairmen work was found but still concrete spalling, dampness was observed in several locations. Factory management is required to take proper remedial measures to solve this issue. On 11-Dec-2019: Factory has repaired the water causing damage with improper methodology. So, appearance of corrosion & concrete spalling was found near washrooms. Factory engineer is required to investigate the damage and prepare report including proper methodology. Factory is required to follow the recommendation of the report for the repair works. On 17-Nov-2020: During inspection water causing damage was found near washrooms. Moreover, no investigation report was found on site. Factory is required to investigate the damage & prepare report with proper methodology. Factory is also required to repair all damages with suitable method. On 24-May-2022: During inspection water causing damage was found near washrooms. Factory is also required to repair all damages with suitable method as per suggested in DEA report. On 06-Oct-2022: During inspection dampness was found near washrooms. Factory is required to repair all damages with suitable method as per suggested in DEA report. On 27-Feb-2023: Dampness has been repaired near the washrooms. During the inspection, no dampness was found. On 15-Jul-2024: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 15 | Limit density of loading in storage areas | Building´s Engineer to ensure the structure is not loaded beyond capacity. We recommend limit stack height to 1.80m (1.50x1.50m area) and keep 0.60-0.70 m cleared strip around. Limit height to 1.80 m for loose clothing | Corrected In our floor are activly maintainging load plan which have been approved during DEA by ACCORD | Aug 30 2016 | On 09/12/2014: Covered in final DEA report . On 23/03/2016: Heavy loading was found in every floor which is required to be reduce immediately. On 10/11/2016: During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: During inspection load plan was found posted on each every floor and live load was found more than the acceptable limit at 1st floor. Factory is required to maintain loads as per accepted load plan. On 14/01/2018: During inspection, load plan was observed posted on each and every floor and live load was found below accepted loading (42psf). Factory is required to maintain load as per accepted load plan. Stack height is below 1.80m. No load restriction height marking was found. On 05/09/2018: Found corrected from previous inspection. During follow up inspection loading was found as per accepted load plan. On 21st November 2018: Corrected previously. Loading was observed within accepted load plan limit (42psf). On 14-July-2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. During inspection load plans were found posted in each floor and overall loading was observed within the allowable limit (<42 psf) except 1st floor fabric storage. On 11-Dec-2019: Corrected from previous inspection. During inspection, stack height was found within allowable limit (<1.8m). On 17-Nov-2020: Corrected from previous inspection. During inspection stack height was found within allowable limit (1.8m). On 24-May-2022: This issue was corrected from previous inspection. During inspection load restriction height marking was found provided. On 06-Oct-2022: Corrected from previous follow up inspection. During inspection load restriction height marking was found provided. On 27-Feb-2023: Corrected in the previous follow-up inspection. Load restriction height marking has been provided on storage areas. On 15-Jul-2024: Corrected previously. During inspection loading was found within the load limit (42 psf & 63 psf). Load plan was found posted on each floor. | (within 6-months) | Corrected
Initial Inspection |  | 16 | Limit density of loading in storage areas | Building Engineer to create controlled loading plans for all floors | Corrected In our floor are activly maintainging load plan which have been approved during DEA by ACCORD | Aug 30 2016 | On 09/12/2014: Covered in final DEA report . On 23/03/2016: Heavy loading was found in every floor which is required to be reduce immediately. On 10/11/2016: During DEA verification inspection load plan found posted but high loading observed in 5th & 3rd floor finished good storage and 1st floor fabric roll storage (>63 psf). Factory management got their approval on 28/08/2016 and retrofitting work found ongoing. On 15/05/2017: During inspection load plan was posted on each every floor and live load was found more than the accepted load plan at 1st floor. On 14/01/2018: During inspection, load plan was observed posted on each and every floor and live load was found below accepted loading (42psf). Stack height is below 1.80m.Factory is required to maintain load as per accepted load plan. On 05/09/2018: Found corrected from previous inspection. On 21st November 2018: Corrected previously. Loading plans have been produced. On 14-July-2019: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. During inspection load plans were found posted in each floor and overall loading was observed within the allowable limit (<42 psf) except 1st floor fabric storage. On 11-Dec-2019:Corrected from previous inspection. Load plan was produced as part of DEA which was accepted by ACCORD on 18-Jan-2017. During inspection, load plan was found posted in each of the floor and loading was found within accepted load limit (42 psf). On 17-Nov-2020: Corrected from previous inspection. During inspection load plan was found posted & loading was found within allowable limit (42 psf). On 24-May-2022: This issue was corrected from previous inspection. During inspection load plan was found posted & loading was found within allowable limit (42 psf). On 06-Oct-2022: Corrected from previous follow up inspection. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. During inspection load plans were found posted in each floor and overall loading was found within the allowable limit (<42 psf). On 27-Feb-2023: Corrected in the previous follow-up inspection. During inspection loading was found within the load limit (42 psf). Load plan was found posted on each floor. On 15-Jul-2024: Corrected previously. During inspection loading was found within the load limit (42 psf & 63 psf). Load plan was found posted on each floor. | (within 6-months) | Corrected
Initial Inspection |  | 17 | Non engineered steel structure on roof | Building engineer to check the structure and its supports and propose additional reinforcements and stability system. | Dea has been approved We will Remove the no-engineering steel structure and reconstruct the Shade on Roof according to the approved DEA | Aug 30 2016 | On 09/12/2014: Covered in final DEA report . On 23/03/2016: Additional reinforcement and stability system if required will be proposed after DEA review. On 10/11/2016: During DEA verification inspection observed that factory management demolished the non engineered steel shed & proposed a new steel shed which has been approved along with DEA. On 15/05/2017: Found corrected from previous inspection. Non-engineered steel shed was removed and a new steel shed was being constructed which was accepted along with DEA. On 14/01/2018: Corrected form previous follow up inspection. The new shed construction has been completed with proper support and connections. On 05/09/2018: Found corrected from previous inspection. On engineered steel structure has been removed & new shed has been constructed as per accepted drawings. On 21st November 2018: Corrected previously. DEA has been reviewed and re-accepted. On 14-July-2019: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 11-Dec-2019: Corrected from previous inspection. This issue has been covered in DEA which was re-accepted by ACCORD on 18-Jan-2017. On 17-Nov-2020: Corrected from previous inspection. This issue had been covered under DEA which was re-accepted by ACCORD on 18-Jan-2017. On 24-May-2022: This issue was corrected from previous inspection. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. As per DEA recommendation factory management had completed all remedial works. On 06-Oct-2022: Corrected from previous follow up inspection. This issue had been covered in DEA report. Factory management got DEA re-acceptance from ACCORD on 18-Jan-2017. As per DEA recommendation factory management had completed all remedial works. On 27-Feb-2023: Corrected in the previous follow-up inspection. On 15-Jul-2024: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 18 | Structural drawings are not completed, only geometry drawings and layout were shown for the concrete structure. No information about the metal roof structure. | Building engineer to check, collect information and produce accurate and complete as-built documentation soonest. | Corrected: As built architectural and structura drawing have been completed. | Apr 14 2016 | On 09/12/2014: Covered in final DEA report . On 23/03/2016: Structural Drawing has been completed and submitted with DEA. On 10/11/2016: During DEA verification inspection toilet build up observed but which is not incorporated in architectural drawing & FEM model. So factory management is required to resubmit their DEA to ACCORD. On 15/05/2015: A set as-built drawings was produced and it was accepted along with DEA but toilet build up was not incorporated with as built drawing. During inspection ,factory management were removing toilet build up also they told us they will remove all toilet build up as soon as possible. On 14/01/2018: This issue was required to be covered in DEA which was re-accepted by ACCORD on 18th January 2017. On 05/09/2018: Found corrected from previous inspection. On 21st November 2018: Corrected previously. DEA has been reviewed and re-accepted. On 14-July-2019: Corrected in previous follow up inspection. As built drawings were prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. On 11-Dec-2019: Corrected from previous inspection. As built drawing was produced as part of DEA which was re-accepted by ACCORD on 18-Jan-2017. On 17-Nov-2020: Corrected from previous inspection. As-built drawing was produced as a part of DEA which was re-accepted by ACCORD on 18-Jan-2017. On 24-May-2022: This issue was corrected from previous inspection. As built drawings were prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. On 06-Oct-2022: Corrected from previous follow up inspection. As built drawings were prepared as a part of DEA. Factory management got DEA re-acceptance from ACCORD on 18-January-2017. On 27-Feb-2023: Corrected in the previous follow-up inspection. On 15-Jul-2024: Corrected previously. | (within 6-months) | Corrected
Follow Up Inspection |  | 19 | New Findings 1: Cracks found on the column at movement joint of 3rd floor | Building Engineer to investigate cracks and repair accordingly | Correected we have investigate throughly and found that crack is just in plaster crack not in cloumn and we have repaired the plaster in that position | Jun 15 2016 | On 23/03/2016: It is required to investigate cracks and repair accordingly immediately. On 10/11/2016: During DEA verification inspection column at movement joint of 3rd floor found plastered. Factory engineer told it was a plaster crack. On 15/05/2017: Found corrected from previous inspection. Found same as before. On 14/01/2018: Corrected from previous follow up inspection. No deterioration in column is observed. On 05/09/2018: Found corrected from previous inspection. On 21st November 2018: Corrected previously. Cracks were found repaired. No alteration was observed. On 14-July-2019: Corrected in previous follow up inspection. On 11-Dec-2019: Corrected from previous inspection. Cracks were found repaired. No alteration was observed. On 17-Nov-2020: Corrected from previous inspection. Cracks were found repaired. No significant cracks were found during inspection. On 24-May-2022: This issue was corrected from previous inspection. Cracks were found repaired. No significant cracks were found during inspection. On 06-Oct-2022: Corrected from previous follow up inspection. Cracks were found repaired. No cracks were found during inspection. On 27-Feb-2023: Corrected in the previous follow-up inspection. No cracks were found during the inspection. On 15-Jul-2024: Corrected previously. During inspection no further crack was found on columns and movement joints. | Jul 4 2016 | Corrected
Follow Up Inspection |  | 20 | New Findings 2: Undocumented shed found at ground floor(North side) | Factory engineer is required to produce as built drawing and check the connection adequacy as part of EA | We are working on it | Jul 14 2022 | On 24-May-2022: During inspection, a undocumented shed found at ground floor(North side). Factory engineer is required to produce as built drawing also check the connection adequacy as part of EA and submit to RSC for review. On 06-Oct-2022: Factory management had provided a consent letter that they are not going to use the shed anymore and they already closed the entrance of the shed by brick wall. On 27-Feb-2023: Corrected in previous inspection. On 15-Jul-2024: Corrected previously. | (within 6 weeks) | Corrected
Special | Escalation | 21 | New findings 3: New ancillary structures found in the factory premises 1. Single Storied Childcare Shed 2. Single Storied Boiler Shed (Extension) 3. Single Storied Generator & Sub-station Shed | The factory is required to prepare full set of as-built drawing for all structures and submit the documents to RSC. | As-built drawings of the Single Storied Childcare Shed, Single Storied Boiler Shed (Extension) and Single Storied Generator & Sub-station Shed have been reviewed and accepted by the RMG Sustainability Council (RSC) on 31-03-2024. | Apr 20 2023 | On 27-Feb-2023: During the inspection 3 new ancillary structures were found in the factory premises. The factory is required to prepare a full set of as-built drawings for all structures. On 15-Jul-2024: Factory prepared the as-built drawings for the ancillary structures and received acceptance from RSC on 31 March 2024. During inspection prepared as-built drawings found matched with the site condition. | (within 6 weeks) | Corrected
Special | Escalation | 22 | New findings 4: Racks on the different floor level are not adequately anchored or braced to resist earthquake forces. | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC. | Done | Apr 20 2023 | On 27-Feb-2023: Some racks on the different floor level are not adequately anchored or braced to resist earthquake forces. The factory is required to anchor and brace all nonstructural elements to resist earthquake forces. On 15-Jul-2024: During the inspection, all non-structural elements were found adequately anchored. | (within 6 weeks) | Corrected

## Fire
Date
25-Feb-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Ind.Ltd., Plot-28, Milk Vita Rd., Section-07, Mirpur, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2014-03-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Hazardous materials storage area is not separated by fire-rated construction openings non-rated doors and penetrations all present | Separate the hazardous materials / flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings separations. | Done | Jun 20 2016 | On 17/07/2019: Corrected as per previous follow up. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected as per previous FUiN. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | with in three months | Corrected
Initial Inspection |  | 2 | The boiler room is not separated by fire-rated construction (openings, non-rated doors, penetrations all present | Separate the boiler room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Done | Jun 10 2016 | On 18/11/18: Separated On 17/07/2019: Corrected. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | with in three months | Corrected
Initial Inspection |  | 3 | The exit stairs are not separated from work areas on each floor by fire-rated construction | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Done | Jun 30 2016 | On 18/11/18: Fire doors have found open by external objects in maximum floors. In 2nd floor (Peoples Fashions Ltd.) door has installed improperly, also at 5th floor there is a kitchen/galley/tea process room has observed without separation. On 17/07/2019: Issue re-open. Refer issue no. 34. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Refer to issue no: 34. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. Refer to the issue no 34. On 24-May-2022: Refer to the issue no 34. On 06-Oct-2022: Refer to the issue no 34. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | with in three months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Done | Apr 15 2016 | On 14/12/2017: Sealed On 15/05/2018: Corrected. On 18/11/18: Found sealed in maximum cases On 17/07/2019: Corrected. Sealed. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected. On 06-Oct-2022: Refer to the issue no 34. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | with in three months | Corrected
Initial Inspection |  | 5 | Each floor had extensive amounts of fabric and stored goods piled above storage guidelines,Combustible storage is not separated by fire-rated construction throughout factory. Provide | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Done | Aug 30 2016 | On 18/11/18: Still not defined in 3rd & 5th floors On 17/07/2019: Issue re-open. Refer issue no. 35. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Refer to issue no: 35. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | with in three months | Corrected
Initial Inspection |  | 6 | The generator and transformer room is not separated by fireconstruction openings, non-rated doors, penetrations all present. Located at outbuildings | Separate the generator and transformer room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Done | Apr 30 2016 | On 17/07/2019: Corrected. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Refer issue number 39. On 06-Oct-2022: Refer issue number 39. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | with in six Months | Corrected
Initial Inspection |  | 7 | Storage was located in the egress paths throughout all of the factory floors, this needs to be kept clear at all times, in cases storage over spilling or above 9ft in height stacked in close proximity with main egress routes most notably basement, ground,fourth and fifth. | Keep egress paths and stairs clear of storage. | Done | Mar 30 2016 | On 15/05/2017: Corrected. On 22/08/2017: Corrected On 14/12/2017: Found block, specially aisles located beside walls. On 15/05/2018: Refer to Issue #31. On 18/11/18: Again see issue # 31 On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Refer to issue no: 31. On 21/11/2021: Refer to issue no. 31 On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Immediately | Corrected
Initial Inspection |  | 8 | Collapsible steel sliding gated doors are provided at building exits, exit stairs, along egress routes on the first floor and main exit discharge at ground level. All egress doors were open with locks in sealed position. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Oct 31 2014 | On 18/11/18: Replaced On 17/07/2019: Corrected. Factory has removed non-compliant doors/gates from egress routes. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | With in one month | Corrected
Initial Inspection |  | 9 | The width of egress aisles is less than 36-in at certain locations throughout the factory floors were internal columns meet work station desks | Provide minimum aisle widths of 36-in. | Done | Apr 10 2016 | On 18/11/18: Provided but without considering the working area of occupants On 17/07/2019: Corrected as per previous follow up. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. Note: Aisles mark shall be provided at sample section on 4th floor. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. Note: Factory shall ensure that, minimum width of aisle has been maintained through out all floor. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | With in three month | Corrected
Initial Inspection |  | 10 | The day-care room does not have direct access to an exit stair on the ground floor | Specify appropriate upgrade based on conditions: - Provide a minimum 2-hr firerated exit corridor between the day-care room and exit stair | Done | Dec 30 2015 | On 14/12/2017: Not found during inspection. On 15/05/2018: Corrected. Day care room has been shifted to another building. On 18/11/18: Relocated to ground floor On 17/07/2019: Corrected. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | Common path of egress travel exceeds 30 m. The Basement/Ground level, the 2 exits to the main egress exit is within 15ft of each other with a common path of travel more than 30m | Reconfigure the egress arrangement to reduce the maximum common path of travel to not more than 30 m. | Done | Apr 10 2016 | On 17/07/2019: Corrected. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | Exit capacity is not adequate for the occupant load.Having calculated the exit capacity for each floor, the occupant load is excessively more than allowed due to there being only two main exit stairs and the door widths being narrow on the South most facing stair 5th floor and North most stair 3rd floor. | Specify appropriate upgrade based on conditions: - Provide additional exits. | Done | Sep 15 2016 | On 18/11/18: Completed On 17/07/2019: Corrected as per previous follow up. Please see issue no. 36. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected as per previous FUI. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | Handrails are not provided in either of the exit stairs | Provide handrails on at least one side of exit stair. | Done | Oct 31 2014 | On 14/12/2017: Provided On 15/05/2018: Corrected. On 18/11/18: Provided On 17/07/2019: Corrected. Provided. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. Note: Factory shall ensure that, full handrail has been provided on Stair-2 and 3 on roof area. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 14 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | We have submitted documents to RSC ON 16-11-2025. | Aug 30 2016 | On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Modification of the system is going on. Factory has informed that modification will be completed within March and after modification they will apply for T&C. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Modification work is ongoing process. On 11/01/2022: Pre-T&C review found that the FADS is not ready for full T&CVI and the factory required a new on-site Pre-T&C Review. See detailed Pre-T&C Report. On 24-May-2022: Progress has been observed. Reportedly modification work based on the pre T&CVI report has been found on going. Factory shall apply immediately to RSC for another T&CVI after completion of modification work. On 06-Oct-2022: During the day of inspection, Pre T&CVI also has been conducted and found FADS requires another On-Site Pre T&CVI. On 27/02/2023 (Special Inspection): Not Checked. On 15/07/2024: Pre-T&CVI found that the FADS is not ready for full T&CVI and the factory required a new on-site Pre-T&CVI. See detailed Pre-T&CVI Report. On 25-Nov-24: Modification work based on the Pre T&CVI report has been found on going. Reportedly, factory will submit the design & documents to RSC within 31st Dec 2024. RPO Comments: On 23-Feb-2026, the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Design within 4 months, install within 9 months | In Progress
Initial Inspection |  | 15 | Inspection, testing, and maintenance records for the fire alarm system were not available. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | We have submitted documents to RSC ON 16-11-2025. | Aug 30 2016 | On 18/11/18: Integrated part of fire alarm system though they are maintaining for existing system On 17/07/2019: It is an integrated part of fire alarm system. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: It is an integrated part of fire alarm system. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Integrated part of fire alarm system. On 11/01/2022: It is an integrated part of fire alarm system. On 24-May-2022: It is an integrated part of fire alarm system. On 06-Oct-2022: It is an integrated part of fire alarm system. On 27/02/2023 (Special Inspection): Not Checked. On 15/07/2024: Integrated part of fire alarm system. On 25-Nov-24: Integrated part of fire alarm system. RPO Comments: On 23-Feb-2026, the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Within 3 months | In Progress
Initial Inspection |  | 16 | The fire alarm system does not appear to provide adequate audible notification coverage. | The fire alarm system does not appear to provide adequate audible notification coverage. | We have submitted documents to RSC ON 16-11-2025. | Aug 30 2016 | On 17/07/2019: It is an integrated part of fire alarm system. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: It is an integrated part of fire alarm system. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: It is an integrated part of fire alarm system. On 11/01/2022: Pre-T&C review found that the FADS is not ready for full T&CVI and the factory required a new on-site Pre-T&C Review. See detailed Pre-T&C Report. On 24-May-2022: It is an integrated part of fire alarm system. On 06-Oct-2022: It is an integrated part of fire alarm system. On 27/02/2023 (Special Inspection): Not Checked. On 15/07/2024: Pre-T&CVI found that the FADS is not ready for full T&CVI and the factory required a new on-site Pre-T&CVI. See detailed Pre-T&CVI Report. On 25-Nov-24: It is an integrated part of fire alarm system. RPO Comments: On 23-Feb-2026, the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Within 6 months | In Progress
Initial Inspection |  | 17 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single-station smoke alarms with automatic smoke detectors tied into the fire alarm system. Configure the fire alarm system to initiate occupant notification upon activation of any two smoke detectors in addition to the manual fire alarm stations. | We have submitted documents to RSC ON 16-11-2025. | Aug 30 2016 | On 17/07/2019: It is an integrated part of fire alarm system. On 07-10-2019 (Special Inspection): Not Checked. RPO Comments: On 24-Oct-2024 the factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 15/03/2020: It is an integrated part of fire alarm system. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021:It is an integrated part of fire alarm system. On 11/01/2022: Pre-T&C review found that the FADS is not ready for full T&CVI and the factory required a new on-site Pre-T&C Review. See detailed Pre-T&C Report. On 24-May-2022: It is an integrated part of fire alarm system. On 06-Oct-2022: It is an integrated part of fire alarm system. On 27/02/2023 (Special Inspection): Not Checked. On 15/07/2024: Pre-T&CVI found that the FADS is not ready for full T&CVI and the factory required a new on-site Pre-T&CVI. See detailed Pre-T&CVI Report. On 25-Nov-24: It is an integrated part of fire alarm system. RPO Comments: On 23-Feb-2026, the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Within 6 months | In Progress
Initial Inspection |  | 18 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes throughout factory floors, the lighting on exit routes was sufficient however on floor plates the lighting was not adequate for safe egress. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles | Done | Jun 15 2016 | On 17/07/2019: Corrected as per previous follow up. Note: Factory shall ensure that emergency light illumination level on aisles are adequate. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. Note: Adequate illumination for emergency lighting system shall be provided at all required places. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 19 | Exit signage was not adequate in line with Bangladesh building regulations throughout factory stairwells and floor plates | Provide exit signs above all exits to the exterior and all doors to the exit stairs | Done | Oct 31 2014 | On 17/07/2019: Directional arrow sign shall be illuminated and accordance with standard. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 20 | A number of Emergency lights did not function in test mode bulbs possibly burned out, no maintenance schedules provided. | Reguarly test the emergency lighting system on each floor and replace/repair lights as needed. | Done | Oct 31 2014 | On 18/11/18: Completed On 17/07/2019: Corrected as per previous follow up. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 21 | New Finding (2nd Follow up): The required standpipe system is not installed in accordance with the ACCORD standard. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupiable floor 10m (33ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. | Done | Sep 30 2016 | On 18/11/18: Waiting for T&C On 17/07/2019: The installation has been completed, but a T&CVI is needed to verify that the installation is installed in line with the standards and working effectively. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Modification of the system is going on. Factory shall apply for T&C after modification of the system. Installation of the system shall be as per NFPA 14, 20 & 22. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Modification of the system is going on. Factory shall apply for T&C after modification of the system. Installation of the system shall be as per NFPA 14, 20 & 22. On 11/01/2022: Pre-T&C review found that the SUPS is not ready for full T&CVI and the factory required a new on-site Pre-T&C Review. See detailed Pre-T&C Report. On 24-May-2022: Progress has been observed. Reportedly modification work of fire pump based on the pre T&CVI report has been found on going. Factory shall apply immediately to RSC for another Pre T&CVI after completion of modification work. On 06-Oct-2022: During the day of inspection, Pre T&CVI also has been conducted and found SUPS requires another On-Site Pre T&CVI. On 27/02/2023 (Special Inspection): Not Checked. On 15/07/2024: Pre-T&CVI found that the SUPS is not ready for full T&CVI and the factory required an on-site Pre-T&C closure verification. See detailed Pre-T&CVI Report. On 25-Nov-24: Modification work based on the Pre T&CVI report has been found on going. Reportedly, factory will submit the design & documents to RSC within 31st Dec 2024. | Design within 1 months, install within 3 months | Pending Verification
Follow Up Inspection |  | 22 | New Finding (3rd follow up): The northeast exit door in the fifth floor serving 50 or more occupants does not swing in the direction of egress travel. | Modify the egress door to swing in the direction of egress travel. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Jun 23 2016 | On 17/07/2019: Corrected. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 23 | New Finding (3rd Follow up): Unsealed penetration and openings (expansion joints) located in the fire rated floor (third, fourth and fifth floor) or ceiling assemblies is not separated by fire rated construction. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation. | Done | Jun 23 2016 | On 14/12/2017: Comments same as before On 15/05/2018: Corrected. On 18/11/18: Completed On 17/07/2019: Corrected. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected as per previous FUI. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 24 | New Finding (4th Follow up): Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Done | Aug 30 2016 | On 15/05/2018: Corrected. Comments same as before. On 18/11/18: Maintaining On 17/07/2019: Corrected as per previous follow up. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding (4th follow-up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10 | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Done | Aug 30 2016 | On 18/11/18: Comments same as before On 17/07/2019: Corrected as per previous follow up. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 26 | New Finding (4th follow-up): Headroom observed at ground floor does not comply with Accord standard. | Provide minimum clear height of 2.02m/6.8ft | Done | Sep 30 2016 | On 18/11/18: Completed On 17/07/2019: Corrected as per previous follow up. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected as per previous FUI. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New Finding (4th follow-up): Stair designations and occupant load signs were not posted at the entrance of all exit stair. | Fire evacuation maps shall be posted at the entrance to each exit stair. | Done | Jul 21 2016 | On 18/11/18: Posted On 17/07/2019: Corrected. Posted. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding (5th Follow Up): Storage located in the dining area. | Remove storage from the dining area. | Done | Sep 28 2016 | On 17/07/2019: Corrected. Removed. On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 29 | New Finding (5th Follow up): Dining area is not separated from other occupancies with fire rated assemblies | Re-locate the dining area or separate the dining area from other occupancies with fire rated construction | Done | Nov 25 2016 | On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. Note: Unsealed opening was found in dining area with other occupancies. Direct discharge to outside or exit stair shall be provided from dining room. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. Refer to the issue no 34. On 24-May-2022: Corrected as per previous FUI. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 30 | New Finding (10th FUI): Doors along means of egress are provided with non compliant locking system. | 1. Remove all non compliant locking features from egress doors. 2. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. 3. Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. 4. Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. | Done | Dec 20 2017 | On 07-10-2019 (Special Inspection): Not corrected. Factory has installed panic bars on egress doors at the ground level. Despite that, provisions for non-compliant locking features are still available on egress door (Pictorial evidence provided). Factory shall immediately remove all such locking arrangements from egress doors that does not comply with NFPA 101. On 15/03/2020: Corrected. Door holes were closed with sheets. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 31 | New Finding (10th FUI): The egress path along means of egress has interrupted by obstruction/storage. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Done | Dec 20 2017 | On 07-10-2019 (Special Inspection): Refer to Issue# 38 On 15/03/2020: Refer to issue no: 38. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 32 | New Finding (10th FUI): Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Corrected, We have provided dedicated storage room with proper fire separation by installing fire rated door. | Jan 14 2018 | On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Issue reopened. Unsealed openings were observed with storage rooms located in Ground floor. Interfacing of fire doors was not found proper during inspection. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Yet the same scene is evidant on 4th floor. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 33 | New Finding (10th FUI): Evacuation maps are not matched with existing floor conditions, also in many places they have not been provided the evaguation maps | Fire evacuation maps shall be posted at the entrance to each exit stair. | Done | Jan 14 2018 | On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected as per previous follow-up. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 34 | New Finding (On 17/07/2019): The exit stairs are not separated from work areas on each floor by fire-rated construction. Installed fire door was found open by external object on all floors. Installed doors were not interfaced properly with FACP by electro-magnetic door holder device. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Done | Aug 17 2019 | On 17/07/2019: New Finding On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Unsealed opening and penetration was observed with exit stair enclosure in ground floor and top floor. Moreover, interfacing of fire door was not found proper. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Yet the same scenes are evident on various floor. On 11/01/2022: During follow-up inspection some fire doors were not functioning properly. The north-east staircase was not separated from the QC room on the 5th floor and the south side stair was not separated from pantry room on 5th floor. Also unsealed penetration was found from dining area to south stair on 5th floor. On 24-May-2022: Not corrected yet. Exit stairs are not properly separated due to non functional fire door accessories of stair- 1 & 3 on several floors. On 06-Oct-2022: Not corrected yet. Due to opening and penetration Stair-2 is not separated on 4th Floor, Stair-3 on Ground Floor with warehouse and Stair-1 is not separated due to non interfaced magnetic door holder with addressable FADS. Moreover, gap between fire rated door and finished floor has been found more than 19 mm on several location of stair- 1. On 27/02/2023 (Special Inspection): Corrected. Fire doors with necessary accessories (doors leafs, doors coordinators, doors closures etc.) were functional properly during inspection. Unsealed openings & penetrations were found sealed. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 35 | New Finding (On 17/07/2019): Areas used for combustible storage (process goods) open to the factory are not separated by fire rated construction on several floors. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) – If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (1,000 ft2). Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | Done | Aug 17 2019 | On 17/07/2019: New Finding On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: In-process storage area was not found within limit in 5th floor. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: storage area was not found within limit in several locations. On 11/01/2022: During inspection in process storage areas were observed on 3rd on 5th floor. On 24-May-2022: Not corrected yet. Non-compliant open storage areas have been found on 3rd and 5th floor. On 06-Oct-2022 :Not corrected yet. Non-compliant Open storage areas have been found on Ground,3rd and 5th floor. On 27/02/2023 (Special Inspection): Corrected. Storage area was found within limit during inspection. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 36 | New Finding (On 17/07/2019): Egress capacity (535) is not adequate for the occupant loads (580 & 590) on 3rd and 4th floors respectively. | Reduce occupant load immediately to not more than available exit capacity (535) on 3rd and 4th foors. Provide additional exits in the future to increase exit capacity. | Done | Jul 24 2019 | On 17/07/2019: New Finding On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Corrected. Reduced occupant load less than 535 in factory floors. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per previous FUI. On 11/01/2022: Corrected as per previous FUI. On 24-May-2022: Corrected as per previous follow ups. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 37 | New Finding (On 17/07/2019): Manual on-off switch is provided for emergency lighting / exit sign units on all floors. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Corrected, We already removed manual on/off switches from emergency exit.. | Aug 17 2019 | On 17/07/2019: New Finding On 07-10-2019 (Special Inspection): Not Checked. On 15/03/2020: Not corrected. Manual on/off system was observed in exit lighting units. On 17/11/2020 (Special Inspection): Not Checked. On 21/11/2021: Corrected as per site condition. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Special | Escalation | 38 | New Finding (On 07-10-2019) Special Inspection: Egress aisles are interrupted by obstruction. Several aisles were found to be blocked with storage and work tables. | Aisles/ means of egress shall be maintained such that they are clear of all obstructions/ storage/ work tables at all times. | Corrected, We already removed obstruction from egress aisles. | Oct 10 2019 | On 07-10-2019 (Special Inspection): NEW FINDING On 15/03/2020: Few aisles were observed obstructed during inspection. On 17/11/2020 (Special Inspection): Corrected. During inspection storages were not observed on aisles and egress path. On 21/11/2021: Few aisles were observed obstructed during inspection. On 11/01/2022: Corrected. On 24-May-2022: Corrected. On 06-Oct-2022: Corrected. On 27/02/2023 (Special Inspection): Not Checked. On 25-Nov-24: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 39 | New Finding (17th FUiN ) The generator room is not separated from jhute godown by fire rated construction, openings, non-rated doors. Location : Ground Floor | Separate the generator and transformer room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Done We have sealed all opening between generator & jute room. | Jun 24 2022 | On 24-May-2022: New Finding. On 06-Oct-2022: Not corrected yet. Factory already install Fire Rated door and brick wall between Generator room and Jhute Room but some opening has been found also. On 27/02/2023 (Special Inspection): Corrected. Fire Rated door has been installed between Generator room and Jhute Room. Unsealed openings & penetrations at fire rated wall have been sealed properly. On 25-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 40 | New Finding (18th FUiN): Liquefied or compressed gas cylinder storage has been identified. Location: Infront of generator and substation, Ground Floor. | Factory Shall follow TECHNICAL GUIDANCE NOTE FOR USE OF LIQUIFIED OR COMPRESSED FLAMMABLE GAS IN FACTORY PREMISES: 1. The storage building must be at least 3 meters away from any other buildings and boundaries. 2. The exterior walls of the building must have a fire resistance rating of 3 hours using noncombustible construction. 3. Doors and other openings in the exterior walls must be protected with suitable closing devices having a fire protection rating of 3 hours. 4. The building is to be used for no other purpose than the storage of LPG/CNG cylinders. 5. The building must be mechanically ventilated to control the accumulation of flammable vapors. 6. The installations must be approved and accepted by the requirements of the AHJ, Gas supply company regulations, manufacturers/supplier’s instructions/guidance, Chief Inspector of Boiler (CIOB) and Chief Inspector of Explosives Bangladesh (CIEB). All general safety guidence shall be also meet. | Done We have removed compressed gas cylinder from factory premises. | Dec 6 2022 | On 06-Oct-2022: New Finding. On 27/02/2023 (Special Inspection): Corrected. Factory management removed CNG cylinders from the premises. Now they are using natural gas. On 25-Nov-24: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 41 | New Finding (19th FU): The compressor room was not separated from production area by fire rated construction due to unprotected openings, penetrations and non-rated doors on 4th floor. | Separate the compressor room by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain fire separations. | We have removed compressor from production area. | Feb 25 2025 | On 25-Nov-24: New Finding RPO Comments: On 23-Feb-2026, the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Within 3 months | In Progress
Follow Up Inspection |  | 42 | New Finding (19th FU): Unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies due to pvc toilet pipe. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's guideline. (Type-1 Construction). or, Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. (Type-1 Construction). | We are working on it. | Feb 25 2025 | On 25-Nov-24: New Finding RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress

## Electrical
Date
25-Feb-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Ind.Ltd., Plot-28, Milk Vita Rd., Section-07, Mirpur, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2014-03-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Cables terminating from wall are wrapped with combustible material | Remove all wrapped combustible material from cable. Cables/ wirings passing through permanent wall must be protected installing pipes and remaining gaps must be sealed with fire resistant materials. Cable tray/raceway shall be installed for the support of the cable throughout its length. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not corrected. On 13/02/2017: Corrected. | Within One Month | Corrected
Initial Inspection |  | 2 | High earth loop impedance measured. | Check for loose earthing-connection and take necessary action accordingly. |  | Dec 31 2014 | On 23/03/2016: Corrected at 1st follow-up | Within One Month | Corrected
Initial Inspection |  | 3 | Cables terminating at panel are not firmly fixed. | Install cable tray or riser to support the cables entering and leaving the electrical panel to reduce cable strain on cable termination point. Provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected On 13/02/2017: Corrected. | Within One Month | Corrected
Initial Inspection |  | 4 | Service cable directly laid on floor without any protection. | Install the cables tray or duct with cover (metallic) for the protection of the cable laid on floor. Ensure the cables are tightly latched inside the ladder/tray and provide covers made of non-combustible material preferably metallic sheet to protect the cables’ insulation from any physical damage as well as prevent the ingress of debris, dust and lint. |  | Sep 15 2016 | On 23/03/2016:This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016:Not corrected. On 25/09/2016:Not corrected. On 30/11/2016:Not corrected. On 13/02/2017:Not corrected. On 15/05/2017:Not Corrected. Service cables are not protected at the outside of the building. On 22/08/2017:Not Corrected. However, supports/ protections were provided to many cables. There are still cables to be protected from damage. Work is ongoing. On 14/12/2017: Corrected. | Within One Month | Corrected
Initial Inspection |  | 5 | Service cables terminating from wall is not supported | Cables must be protected and supported and installed through safe and prescribed routes. Cables laid on external walls of the building must be supported on covered ladders and cable trays in complete length of cables. Seal all the penetrations using appropriate fire rated material and ensure the cable insulation does not get damaged during sealing work. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not corrected. On 13/02/2017: Corrected. | Within One Month | Corrected
Initial Inspection |  | 6 | Transformer room not maintained regularly. | Transformer room must be regularly cleaned and maintained as part of the routine maintenance. Disconnect the transformer from the electrical system before maintenance work and cleaning. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Corrected. | Within One Month | Corrected
Initial Inspection |  | 7 | Excess service cable coiled on pole not supported. | Excess length of service cables must be trimmed and install a vertical cable tray or ladder with protective cover to support and protect the HT cable. Route the HT cable removing acute bend throughout it’s whole length. |  | Feb 28 2015 | On 23/03/2016: Corrected at 1st follow-up | Within six Month | Corrected
Initial Inspection |  | 8 | Silica gel in transformer breather, discolored. | Shut down the transformer and replace the silica gel or perform maintenance to remove moisture from it. Consult with transformer servicing company before performing the task. Establish a routine maintenance & inspection program for transformer as well as all other electrical equipment to ensure any future repetition of the occurrence. |  | Aug 31 2014 | On 23/03/2016: Corrected at 1st follow-up | Within One Month | Corrected
Initial Inspection |  | 9 | Oil cup below transformer breather is empty | Fill the Breather oil cup with transformer oil up to the required level as instructed by the manufacturer. Consult with transformer servicing company before performing the task. Establish a routine maintenance & inspection program for transformer as well as all other electrical equipment to ensure any future repetition of the occurrence. |  | Apr 30 2016 | On 23/03/2016: Though the issue was corrected at 2nd follow-up inspection but factory has failed to maintain it properly. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within One Month | Corrected
Initial Inspection |  | 10 | Gland holes in cable base plates left open. | Provide cable gland at the base plate of panels according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected On 13/02/2017: Corrected. | Within six Month | Corrected
Initial Inspection |  | 11 | Excessive heating of cables inside panel | Arrange periodic inspection to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected. On 13/02/2017: Not corrected. On 15/05/2017: Not Corrected. On 22/08/2017: Corrected. No thermal hotspot was found. | Within One Month | Corrected
Initial Inspection |  | 12 | Panel doors not connected with earth bond | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within One Month | Corrected
Initial Inspection |  | 13 | Generator battery placed on the concrete floor. | Remove all the combustible materials, kept near electrical equipment. Generator Battery must be place done the battery stand made of non-combustible material (steel fabricated, acid proof). |  | Dec 31 2014 | On 23/03/2016: Corrected at 1st follow-up | Within One Month | Corrected
Initial Inspection |  | 14 | PVC conduit broken/ damaged. | Broken conduit must be replaced with new standard PVC conduit. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected. On 13/02/2017: Not corrected. On 15/05/2017: Not Corrected. On 22/08/2017: Not Corrected. Cable is not supported at many places. On 14/12/2017: Corrected. | Within One Month | Corrected
Initial Inspection |  | 15 | Barrier/separators between different phases are not installed. | Provide phase separators between poles of MCCB made of non combustible materials preferably use rubber having enough dielectric strength to insulate phases from each other. |  | Jun 20 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/16: Not corrected. On 25/09/2016: Corrected. | Within One Month | Corrected
Initial Inspection |  | 16 | Excessive dust and/or lint deposit on the transformer. | Establish a routine cleaning program to keep neat and clean the transformer room. Shut down the power of the transformer and clean the exterior of the transformer at scheduled period. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within One Month | Corrected
Initial Inspection |  | 17 | Multiple cables terminating to MCCB in panel. | Multiple cables connecting at a MCCB terminal must be removed. Individual circuit breaker must used for each load according to the respective cable-size |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within three months | Corrected
Initial Inspection |  | 18 | Multiple cables connected at a terminal of the bus bar | Remove all the multiple connections made at a single point of bus bar and connect individual branch cables to individual points on bus bar using individual lug according to the respective cable size. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within three months | Corrected
Initial Inspection |  | 19 | Wooden board used with PVC conduit | Wooden board/combustible material should not be used in any electrical wiring system. Use any combustible material to mount any electrical device. |  | Jun 20 2016 | On 23/03/2016: Corrected at 1st follow-up | Within three months | Corrected
Follow Up Inspection |  | 20 | New Finding: Arcing horns are not aligned | Align all the arcing horns |  | Sep 30 2015 | On 23/03/2016: Corrected at 1st follow-up. | Within two months | Corrected
Follow Up Inspection |  | 21 | New Finding: Panel/Distribution boxes are inaccessible or can not be opened to perform any maintenance work. | Take necessary initiative thus every panel/ distribution board can be easily accessible |  | Jun 20 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 15th May, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Corrected | Within three months | Corrected
Follow Up Inspection |  | 22 | New Finding: No rubber (insulation) mat on the working area of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries). |  | Sep 30 2015 | On 23/03/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 23 | New Finding: Distribution board/panel is filled with fluffs (lint/dust) | Keep always clean inside all the distribution boards/panels. Seal them properly and ensure adequate ventilation. |  | Jun 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/16: Not corrected. On 25/09/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 24 | New Finding: Burnt sign observe inside panel. | Check the reason and replace the CT by a good one. |  | Apr 30 2016 | On 25/09/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 25 | New Finding: Cables terminated at electrical bus bar/MCCB without cable lugs | Terminate all the power/earth/neutral cable with proper sized cable lug |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 26 | New Finding: Change over switch has no earthing connection. | Ensure proper earthing connection for all change over switches, panel boards and electrical equipment. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected On 13/02/2017: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 27 | New Finding: MCB installed on wooden base and without enclosure. | Install circuit breaker on non-flammable base and enclosure. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 28 | New Finding: Loop connection has used powering multiple MCBs. | Eliminate loop cables; use single cable for each MCB. You may use bus bar to avoid multiple termination. |  | Sep 30 2015 | On 23/03/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 29 | New Finding: MCCBs are not adjusted accordingly | Adjust all the MCCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Done We have adjusted all the MCCBs and removed different size cable from the terminal. | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected. On 13/02/2017: Not corrected. On 15/05/2017: Not Corrected. On 22/08/2017: Not Corrected. Some breakers were changed to the required rated CB. Work is ongoing. On 14/12/2017: Not Corrected. On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Not corrected. On 15-03-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not Corrected. They are working on this issue. Most of the their work was done. On 21/11/2021: Not Corrected. No progress observed. On 11/01/2022: Not corrected. Factory has solved the issue at most panels except few places. On 24/05/2022: Not Corrected. Found this issue at very few places and factory is working on it. On 06/10/2022: Corrected | Within two months | Corrected
Follow Up Inspection |  | 30 | New Finding: Panel boards have openings. | Seal all of the openings with non-flammable material |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Corrected. | Within three months | Corrected
Follow Up Inspection |  | 31 | New Finding: No marking on panel board. | Identify and mark all panel boards with permanent marking. |  | Jun 20 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 32 | New Finding: Loose lighting fixture. | Fix all light fixtures properly. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected. On 13/02/2017: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 33 | New Finding: Uncovered light over stored goods. | Ensure fire rated lighting cover for lighting inside store. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 34 | New Finding: Generator output cables (laid on floor) are not protected and supported. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected On 13/02/2017: Corrected. | Within three months | Corrected
Follow Up Inspection |  | 35 | New Finding: Bottom plate of Generator terminal box left open. | Seal the bottom plate by metal sheet and use cable gland for cable entry. |  | Dec 30 2015 | On 23/03/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 36 | New Finding: Inadequate working clearance around the generator. | Working clearance around each generator should be 1.07m. If multiple generators are installed then the gap between two generators must be equal to the width of bigger generator. |  | May 31 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 31th May, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Corrected | Within three months | Corrected
Follow Up Inspection |  | 37 | New Finding: Wooden cable channel used for power distribution. | Replace wooden cable channel by non-combustible material (iron, aluminum etc.). Ensure that the metal structure has connection with earth. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Corrected. | Within three months | Corrected
Follow Up Inspection |  | 38 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 39 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | We have submitted the revised proposed SLD on 06-07-2022 & waiting for Approval. | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not Corrected. On 13/02/2017: Not corrected. On 15/05/2017: Not Corrected. On 22/08/2017: Not Corrected. Work was going on. On 14/12/2017: Not Corrected. On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. SLD is not as-built. On 17/07/2019: Not corrected. On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not Corrected. They are working on this issue. Most of the their work was done. On 21/11/2021: Not Corrected. Factory prepared new SLD which needs modification. Need to rectify as suggested during inspection and submit to RSC for review. On 11/01/2022: Not corrected. Factory has submitted the SLD at RSC. On 24/05/2022: Not Corrected. SLD under review process of RSC. On 06/10/2022: Corrected | Within three months | Corrected
Follow Up Inspection |  | 40 | New Finding: Absence of Lightning Protection System(LPS) | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. |  | May 31 2016 | On 23/03/2016: This issue is still open. New time line is given till 31st May, 16 On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not corrected. On 13/02/2017: Not corrected. On 15/05/2017: Not Corrected. Ensure regular maintenance of the LPS. On 22/08/2017: Not Corrected. No progress was found. On 14/12/2017: Not Corrected. Metal bonding is missing and earth pit was in accessible to verify. Some portion of shed is not shown in drawing and is not protected/protection area is not calculated in drawing. On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Not corrected. On 15-Mar-2020: Corrected. | Within three months | Corrected
Follow Up Inspection |  | 41 | New Finding: Thermography scanning report is absent | Keep a thermography scanning record of your electrical system at lease twice a year |  | Nov 30 2015 | On 23/03/2016: Corrected at 1st follow-up | Within three months | Corrected
Follow Up Inspection |  | 42 | New Finding: Earth pits are not identifiable. Earth Pit resistance record is unavailable. | Identify each earth pit and mark it for periodic maintenance purpose and record earth pit resistance for all the earth pit and do once in a year. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within three months | Corrected
Follow Up Inspection |  | 43 | New Finding: Transformer Oil Test report is unavailable | Check the transformer oil condition by performing oil test. Do it twice in a year and keep the record. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | Within two months | Corrected
Follow Up Inspection |  | 44 | New Finding: Insulation resistance test of electrical equipment is not performed | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off) |  | Dec 30 2015 | On 23/03/2016: Corrected at 1st follow-up | Within two months | Corrected
Follow Up Inspection |  | 45 | New Finding: Electric safety training program is not initiated/ conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded |  | Jun 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 46 | New Finding: Panel/Distribution boxes are not readily accessible | Take necessary initiative thus every panel/ distribution board can be easily accessible |  | Mar 1 2016 | On 23/03/2016: Corrected. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 47 | New Finding: Earth connections are not segregated. Transformer, Generator neutral and system earthing are connected in same bus. | Two separate earth connection & one separate and distinct Neutral connection must be provided for Transformer & generator. These body must have earth connection with half of phase conductor/follow manufacturer/suppliers recommendation. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 48 | New Finding: Power cable is covered by sand in the cable trench & cable trench are filled with fluffs (Lint/dust) | If it is designed keeping Power cable under sand, its OK; otherwise remove sand from cable trench avoiding physical damage of cable. Clean all the cable channels/ducts; then cover them (you may use checkered/perforated plate ). But ensure that you have options for further maintenance work. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not corrected. On 13/02/2017: Not corrected. On 15/05/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 49 | New Finding: Rewireable fuse (cut out fuse) used for circuit protection. | Replace rewire fuses (cut-out fuse) with MCB/MCCB. |  | Aug 30 2018 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 50 | New Finding: Phases are imbalanced. | In three phase outgoing circuits all the phases shall be balanced. Calculate each phase's load and redistribute loads to make phases balanced. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Not corrected. On 13/02/2017: Not corrected. On 15/05/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 51 | New Finding: Unterminated wire is kept inside the electrical panel/cable tray. | All unterminated wires shall be removed |  | Mar 1 2016 | On 23/03/2016: Corrected. No such cable was found during inspection | 2 Months | Corrected
Follow Up Inspection |  | 52 | New Finding: Insufficient illumination provided for generator room. | Install general lighting and emergency lighting in generator room. Generator room should be provided with battery-powered emergency lighting. The emergency lighting charging system and the normal service room lighting shall be supplied from the load side of the transfer switch. General lighting for room should be 32 lux. |  | Mar 1 2016 | On 23/03/2016: Corrected. Tube light is provided at the generator room | 2 Months | Corrected
Follow Up Inspection |  | 53 | New Finding: Storage found inside boiler room | Remove the storage & keep the room neat & clean. |  | Apr 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Cables in service are joined (splicing) between terminations. | Joints of cable shall be avoided. For unavoidable cases, existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. |  | Aug 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 55 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. |  | Aug 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: Exposed and heated steam line is close to cable channel. | Wires close/attached to steam line/heat source must be protected from external heat. In unavoidable case provide proper insulation for the heat source/steam line. Normally power cable should keep 0.9m apart from hot area. |  | Sep 15 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 31th May, 16 to close this issue. On 21/06/2016: Not corrected. On 25/09/2016: Not corrected. On 30/11/2016: Corrected | 3 Months | Corrected
Follow Up Inspection |  | 57 | New Finding: Three phase MCCB connected to control two phases or less. | Check and redesign the requirements to control the circuits. If three phase control is not required, then replace with suitable control devices. |  | Jun 30 2016 | On 23/03/2016: This issue is still open. New committed time line is given till 30th April, 16 to close this issue. On 21/06/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 58 | New Finding: Earthing connection is not provided to the electrical motors. | Ensure proper earthing connection for electrical equipment.. |  | Jun 30 2016 | On 25/09/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 59 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. |  | Mar 15 2017 | On 13/02/2017: Not corrected. New committed timeline given till 15/03/2017. On 15/05/2017: Not Corrected. Factory is working on it, not completed for the whole factory. On 22/08/2017: Not Corrected. In some panels this issue is done. Still it is to be completed in many panels. On 14/12/2017: Not Corrected. On 15/05/2018: Not Corrected. On 18/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Hazardous lights in store room / storage areas are uncovered. | hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. |  | Jan 15 2017 | On 13/02/2017: Corrected. No such issue was found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Power cable is buried in the concrete floor | Power cables must not be buried in the concrete. A cable trench shall be constructed or routing power cables. |  | Mar 15 2017 | On 13/02/2017: Not corrected. New committed timeline given till 15/03/2017 On 15/05/2017: Corrected. Cable trench should be kept dry. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Power cables are bent excessively | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. |  | Mar 15 2017 | On 15/05/2017: Corrected. Bended cable replaced by bus bar. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. |  | Mar 15 2017 | On 15/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Transformer Arcing horn/s are not aligned. | Transformer arcing horn must be installed with proper alignment. |  | Mar 15 2017 | On 15/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. |  | Mar 15 2017 | On 15/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Circuit is drawn from bus bar without any protective means | Each electrical circuit must be drawn from distribution board bus bar using a proper type protection arrangement (MCCB/MCB). |  | Jun 20 2017 | On 22/08/2017: Not Corrected. No steps were taken. On 14/12/2017: Not Corrected. On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Not corrected. On 15-Mar-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. |  | Sep 30 2017 | On 14/12/2017: Not Corrected. On 15/05/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Periodicity of Thermography survey is not continued. | Thermography survey must be done and recorded at least twice in a year. |  | Sep 30 2017 | On 14/12/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Electrical power cables are not identified properly | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | We have submitted the revised proposed SLD on 06-07-2022 & waiting for Approval. | Sep 30 2017 | On 14/12/2017: Not Corrected. On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Not corrected. On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not in scope. On 21/11/2021: Not Corrected. Few cables are not identified. On 11/01/2022: Not corrected. Factory has resolved the issue at most place except few panels. On 24/05/2022: Not Corrected. This issue related to SLD and SLD under review process of RSC. On 06/10/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment.(includes preventive and proactive) | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive) |  | Jan 20 2018 | On 15/05/2018: Not Corrected. On 18/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Insulation resistance record (cable information) doesn't match with field | Field information must be reflected in the record and significantly lower sized cables' record shall be avoided. |  | Jan 20 2018 | On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Not corrected. On 15-Mar-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Safety program is initiated but has no influence in the factory Uninsulated electrical tools are used by maintenance personnel in the factory | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. |  | Jan 20 2018 | On 15/05/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 73 | New Finding: Transformer Silica gel is discolored Lint and dust deposited on and around the transformer. | Silica gel shall be changed; or reuse can be done, if color regains after sundry. Transformer top and around it shall be kept neat and clean. |  | Jan 20 2018 | On 15/05/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 74 | New Finding: Motor has no ECC connection and no mechanical guards are provided for electrical equipment where necessary. | Each motor shall have earth connection, grouted properly ensuring all the safety. Mechanical guard (for rotary devices) shall be provided to avoid accident. |  | Jan 20 2018 | On 15/05/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Power sockets are hung without proper support. | Power socket has to be installed on rigid support/base securely and at minimum 200mm above floor level. |  | Jan 20 2018 | On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 76 | New Finding: Cables in service are joined (splicing) between terminations. Unterminated live wire is kept inside the electrical panel/cable tray. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. All the unterminated live power cables must be removed as soon as possible. |  | Jan 20 2018 | On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Not corrected. On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not in Scope. On 21/11/2021: Not Corrected. Factory used uncovered PVC connector used to join cables which need to be insulated properly. Unterminated live cable observed in boiler room. On 11/01/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Done We resolved the hotspots problem from LT panel & entire electrical system. | Dec 20 2017 | On 15/05/2018: Not Corrected. On 18/11/2018: Not Corrected. On 17/07/2019: Not corrected. On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not in Scope. On 21/11/2021: Not Corrected. Few hot spots observed during inspection. On 11/01/2022: Not corrected. Factory has worked at most of the hotspots and resolved those. Still the issue needs troubleshooting at LT panel. Report is updated. On 24/05/2022: Corrected. | 1 week | Corrected
Follow Up Inspection |  | 78 | New Finding: Transformer Oil Test report is outdated. | Check the transformer oil condition by performing oil test. Do it twice in a year and keep the record. |  | Dec 28 2018 | On 17/07/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: Thermography scanning report is outdated | Keep a thermography scanning record of your electrical system at lease twice a year |  | Dec 28 2018 | On 17/07/2019: Not corrected. Hot spot have to be removed. On 15-Mar-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Corrected We already resolved it | Dec 28 2018 | On 17/07/2019: Not corrected. On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not in Scope. On 21/11/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Circuit breaker has no capacity information. | Each Circuit breaker must have its own capacity information. |  | Dec 28 2018 | On 17/07/2019: Not corrected. On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not in Scope. On 21/11/2021: Not Corrected. No progress observed. On 11/01/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 82 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. |  | Aug 30 2019 | On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not in Scope. On 21/11/2021: Not Corrected. Proper PPE, tools & LOTO are not available. On 11/01/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 83 | New Finding: Cable duct/ channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. |  | Aug 30 2019 | On 15-Mar-2020: Not Corrected. On 17/11/2020 (Special Inspection): Not in Scope. On 21/11/2021: Not Corrected. Dust found in cable channel and cover missing at few areas. On 11/01/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 84 | New Finding: Haphazard wiring inside distribution board found & had no sufficient support. | Cables inside DB Panels have to be guided and dressed properly. Cable trays shall be installed in the Panels to ensure proper support. |  | Aug 30 2019 | On 15-Mar-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 85 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Done We have removed hazardous light from storage area and installed covered light. | Dec 25 2021 | On 11/01/2022: Not corrected. Factory has installed covered-LED lights at most of storage places except few places. On 24/05/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 86 | New Finding: Circuit is drawn from bus bar without any protective means. | Each electrical circuit must be drawn from distribution board busbar using a proper type of protection arrangement (MCCB/MCB). |  | Dec 25 2021 | On 11/01/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 87 | New Finding: Burnt sign visible at MCB terminal. | Check the connections and circuit breaker. Find out the exact reason of burning. If required, replace the burned breaker/cable. Assign an engineer to take necessary action depending on the problem. |  | Dec 25 2021 | On 11/01/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 88 | New Finding: MCB is installed without any enclosure. | Each MCCB/MCB must be enclosed by proper type material. the material must not be more than 18 SWG graded. |  | Dec 25 2021 | On 11/01/2022: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 89 | New Finding: Transformer Oil Test (dielectric strength test) report is generated without conducting any physical survey. | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year. If the operation of transformer is 24/7 in the facility twice in a year is a better practice. |  | Dec 25 2021 | On 11/01/2022: Corrected | 1 Month | Corrected

## Boiler
Date
25-Feb-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Ind.Ltd., Plot-28, Milk Vita Rd., Section-07, Mirpur, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2022-02-27
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 7101 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Done We have provided emergency stop push switch near the entrance outside of the boiler room. | Apr 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 12402 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Done We have provided emergency stop push switch near the entrance outside of the boiler room. | Apr 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 7101 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Done We have marked Low Low Water Level (LLWL) properly on water level gauge glass system. | Apr 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 7101 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. RPO Comments: On 21-Dec-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | Done | Apr 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 21-Dec-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 12402 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Done | Apr 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 21-Dec-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 7101 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Done We have provided emergency stop push switch near the entrance outside of the boiler room. | Mar 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 12402 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Done We have directed boiler Safety Valve outlet line outside of the boiler room. | Mar 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 12402 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | Done We have installed boiler manufacturer's nameplate on the boiler. | Mar 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 7101 | Boiler exhaust pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Done We have installed proper insulation boiler exhaust pipeline inside the boiler room . | Mar 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 12402 | Boiler exhaust pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Done We have installed proper insulation boiler exhaust pipeline inside the boiler room . | Mar 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 7101 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | Done We have boiler's initial registration certificate available on-site . | Apr 23 2025 | Comments on 16-Mar-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 12402 | Inconsistency was observed between the construction drawing and the actual construction of the boiler | Construction drawing should be consistent with the actual construction of the boiler. | We are working on it | Apr 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 13 | BB 7101 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | We are working on it | Apr 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 14 | BB 12402 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | We are working on it | Apr 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 15 | BB 7107 | Drainage arrangement was not installed for safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | Done | Apr 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 21-Dec-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 12402 | Drainage arrangement was not installed for safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | Done | Apr 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 17 | BB 7101 | The boiler air vent line was not directed to the outside of the boiler room. | The boiler vent line should be directed outside of the boiler room with proper support. | We are working on it | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 18 | BB 7101 | Salt and scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | We are working on it | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, the factory management reported the remediation completion. Relevant pictorial evidence is yet to submit, upon submission the issues will be marked as Pending Verification. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 19 | BB 7101 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | Done | Mar 2 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The remediation work shall be done following provided guideline and applicable standard. Pictorial evidence not credible | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 20 | BB 12402 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | Done | Mar 2 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 21-Dec-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 21 | BB 7101 | The Steam Pressure Limiter was missing | Steam Pressure Limiter should be installed and kept functional. | We are working on it | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, the factory management reported the remediation completion. Relevant pictorial evidence is yet to submit, upon submission the issues will be marked as Pending Verification. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 22 | BB 12402 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We are working on it | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 23 | BB 7101 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | Done | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 24 | BB 12402 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | We are working on it | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 25 | BB 7101 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | Done | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 21-Dec-2025, the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 26 | BB 12402 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | We are working on it | Mar 23 2025 | Comments on 16-Mar-25: The remediation work shall be done following provided guideline and applicable standard within the given timeline RPO Comments: On 23-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 MONTH | In Progress