## Structural
Date
05-Jan-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.G. Dresses Ltd., Plot-9, Block C, Tongi Industrial Area, Himardighi, Tongi, Gazipur,Dhaka, Gazipur, Dhaka
Date of Inspection |  | 2014-03-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Flat Slab Design | •Engineer to carry out punching shear calculation check on the building floor slabs. | DEA approved. | Apr 26 2015 | On 26/04/2015: DEA approved. On 8/11/2015: DEA approved. On 11/12/2016: This issue has been covered in DEA. DEA was accepted on 27 Jan 2015. As per accepted DEA the flat slab is adequate for punching shear. On 5/9/2018: Corrected in previous inspection. This issue has been covered in accepted DEA. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. DEA of the factory was accepted on 27-Jan-2015. On 31-Jan-2024: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 2 | Flat Slab Design | •Floor Loading plans to be created to indicate safe storage and building live load based on calculations (See item 4 below) | DEA approved. | Apr 26 2015 | On 26/04/2015: DEA approved. On 8/11/2015: DEA approved. On 11/12/2016: Load plan was produce according to floor capacity. This issue has been covered in DEA. DEA was accepted on 27 Jan 2015. On 5/9/2018: Corrected in previous inspection. Floor loading plan has been prepared and posted to all floor level. Load was found within allowable limit of acceptable load plan On 05-Oct-2020: This issue was corrected in 1st follow up inspection. Load plan was produced as part of DEA which was accepted on 27-Jan-2015. During inspection, load was found within allowable limit of acceptable load plan (3 kPa in storage areas and 2 kPa for all other places). On 31-Jan-2024: Corrected previously. During the inspection, load plan was found posted on the floors and floor loading was found within the allowable limit (3kPa in the storage and 2kPa for all other places). | 6 Weeks | Corrected
Initial Inspection |  | 3 | Storage loading | Storage height restrictions (red line marking) to be checked by building engineer , with consideration to the density of material being stored, to ensure storage does not exceed the maximum design loading | DEA approved. | Apr 26 2015 | On 26/04/2015: Load capacity checked in DEA. We found loading condition within allowable limit. On 8/11/2015: Load capacity checked in DEA. We found loading condition within allowable limit. On 11/12/2016: During inspection load marking was observed for limiting storage in the storage area. On 5/9/2018: Corrected in previous inspection. Load height marking was found some of the storage areas. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. Storage height marking has been provided. Load plan was produced as part of DEA which was accepted on 27-Jan-2015. During inspection, load was found within allowable limit of acceptable load plan (3 kPa in storage areas and 2 kPa for all other places). Load plan was found posted on all floors. On 31-Jan-2024: Corrected previously. During the inspection, load plan was found posted on the floors and floor loading was found within the allowable limit (3kPa in the storage and 2kPa for all other places). Load restriction height marking was observed. | 6 Weeks | Corrected
Initial Inspection |  | 4 | Storage loading | •Building Engineer to create controlled loading plans for all floors. | Load capacity checked in DEA.We found loading conditioon within allowable limit | Apr 26 2015 | On 26/04/2015: Load capacity checked in DEA. We found loading condition within allowable limit. On 8/11/2015: Load capacity checked in DEA. We found loading condition within allowable limit. On 11/12/2016: Load plan was produce according to floor capacity. This issue has been covered in DEA. DEA was accepted on 27 Jan 2015. On 5/9/2018: Corrected in previous inspection. Floor loading plan has been prepared and posted to all floor level. Load was found within allowable limit of acceptable load plan On 05-Oct-2020: This issue was corrected in 1st follow up inspection. Load plan was produced as part of DEA which was accepted on 27-Jan-2015. During inspection, load was found within allowable limit of acceptable load plan (3 kPa in storage areas and 2 kPa for all other places). Load plan was found posted on all floors. On 31-Jan-2024: Corrected previously. During the inspection, load plan was found posted on the floors and floor loading was found within the allowable limit (3kPa in the storage and 2kPa for all other places). | 6 months | Corrected
Initial Inspection |  | 5 | Verify concrete strengths in internal columns at Ground Floor | Factory Engineer to review design, loads and columns stresses in area identified above. | Load capacity checked in DEA.We found loading conditioon within allowable | Apr 26 2015 | On 26/04/2015: Load capacity checked in DEA. We found loading condition within allowable limit. On 8/11/2015: Load capacity checked in DEA. We found loading condition within allowable limit. On 11/12/2016: This issue has been covered in DEA. DEA was accepted on 27 Jan 2015. As per accepted DEA columns are adequate under existing loading. On 5/9/2018: Corrected in previous inspection. This issue has been covered in accepted DEA. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. DEA of the factory was accepted on 27-Jan-2015. On 31-Jan-2024: Corrected previously. | 6 months | Corrected
Initial Inspection |  | 6 | Verify concrete strengths in internal columns at Ground Floor | Verify insitu concrete stresses either by cores (min of 4 no. 100mm dia. Cores)or existing cylinder strength data | DEA was approved for 10 storey building.Presently they are constructing lift core. | Apr 26 2015 | On 26/04/2015: DEA was approved for 10 storey building. Lift core construction complete. On 8/11/2015: DEA was approved for 10 storey building. Lift core construction complete. On 11/12/2016: Cores were taken and covered in DEA. 6 cores were taken from roof level and 3 cores were taken from lower floor levels. On 5/9/2018: Corrected in previous inspection. Concrete core cutting locations from column and slab were observed. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. Cores were collected and incorporated in DEA. DEA of the factory was accepted on 27-Jan-2015. On 31-Jan-2024: Corrected previously. Concrete cores were taken. | 6 months | Corrected
Initial Inspection |  | 7 | Verify concrete strengths in internal columns at Ground Floor | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | DEA was approved for 10 storey building.Presently they are constructing lift core. | Apr 26 2015 | On 26/04/2015: DEA was approved for 10 storey building. On 8/11/2015: DEA was approved for 10 storey building On 11/12/2016: During inspection it was observed that load plan was posted in the floor areas and load was observed below the limit mentioned in accepted load plan. On 5/9/2018: Corrected in previous inspection. Floor loading plan has been prepared and posted to all floor level. Load was found within allowable limit of acceptable load plan On 05-Oct-2020: This issue was corrected in 1st follow up inspection. Load plan was produced as part of DEA which was accepted on 27-Jan-2015. During inspection, load was found within allowable limit of acceptable load plan (3 kPa in storage areas and 2 kPa for all other places). Load plan was found posted on all floors. On 31-Jan-2024: Corrected previously. During the inspection, load plan was found posted on the floors and floor loading was found within the allowable limit (3kPa in the storage and 2kPa for all other places). | 6 months | Corrected
Initial Inspection |  | 8 | Slender Columns under Stair Core | •Design check of 2 external columns supporting stair core to be carried out by the building engineer. | Column capacity checked in DEA | Apr 26 2015 | On 26/04/2015: Column capacity checked in DEA On 8/11/2015: Column capacity checked in DEA On 11/12/2016: This issue has been covered in DEA. As per accepted DEA the slender columns are adequate. On 5/9/2018: Corrected in previous inspection. This issue has been covered in accepted DEA. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. DEA of the factory was accepted on 27-Jan-2015. On 31-Jan-2024: Corrected previously. | 6 months | Corrected
Initial Inspection |  | 9 | Slender Columns under Stair Core | •Additional protection measures such as a barrier to be installed to reduce accidental impact risk | MS pipe used for vehical impact | Apr 26 2015 | On 26/04/2015: MS pipe used for vehicle impact On 8/11/2015: MS pipe used for vehicle impact On 11/12/2016: During inspection it observed that MS steel pipes were installed to protect the slender columns from vehicle impact. On 5/9/2018: Corrected in previous inspection. Protection measure was taken. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. On 31-Jan-2024: Corrected previously. | 6 months | Corrected
Initial Inspection |  | 10 | Water tank on roof | Building Engineer to check that slab has sufficient capacity to support fully filled water tanks. Punching shear at column heads to be checked (refer item 1 above) | Capacity of slab checked in DEA.As per DEA recommendation water tanks relocated | Apr 26 2015 | On 26/04/2015: Capacity of slab checked in DEA.As per DEA recommendation water tanks relocated. On 8/11/2015: Capacity of slab checked in DEA.As per DEA recommendation water tanks relocated On 11/12/2016: As per accepted load plan, factory is currently not using the water tanks. During inspection some plastic water tanks were observed but they were not in operation. On 5/9/2018: Corrected in previous inspection. The mentioned water tanks are not in operation. Some of the tanks were removed. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. No plastic water tanks were observed. On 31-Jan-2024: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 11 | Water tank on roof | Relocate tanks if necessary | 3000 ltr fire water tank on roof,building engineer calculation and building is safe. | Apr 26 2015 | On 26/04/2015: Capacity of slab checked in DEA.As per DEA recommendation water tanks relocated. On 8/11/2015: Capacity of slab checked in DEA.As per DEA recommendation water tanks relocated On 11/12/2016: As per accepted DEA load plan, factory is currently not using the water tanks. During inspection some plastic water tanks were observed but they were not in operation. On 5/9/2018: Corrected in previous inspection. The mentioned water tanks are not in operation. Some of the tanks were removed. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. No plastic water tanks were observed. On 31-Jan-2024: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 12 | Construction of top of stair core –incomplete & unsafe | Engineer to carry out punching shear calculation check on the building floor slabs. | Edge potection handrailing installed | Apr 26 2015 | On 26/04/2015: Lift core construction complete On 8/11/2015: Lift core construction complete On 11/12/2016: During inspection it was observed that handrails were installed in the up to level-8 and handrails were not installed in the upper level. However, the access to upper level was restricted. On 5/9/2018: Corrected in previous inspection. This issue has been covered in accepted DEA. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. DEA of the factory was accepted on 27-Jan-2015. On 31-Jan-2024: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 13 | Construction of top of stair core –incomplete & unsafe | Floor Loading plans to be created to indicate safe storage and building live load based on calculations (See item 4 below) | Temporary shed checked in DEA | Apr 26 2015 | On 26/04/2015: Temporary shed checked in DEA On 8/11/2015: Temporary shed checked in DEA On 11/12/2016: During inspection it was observed that the roof shed was demolished and new RC slab was constructed in that place. On 5/9/2018: Corrected in previous inspection. RC slab observed on stair core. On 05-Oct-2020: This issue was corrected in 1st follow up inspection. On 31-Jan-2024: Corrected previously. | 6 months | Corrected
Follow Up Inspection |  | 14 | New finding-1: Rasied floor on toilet zone | Floor Loading plans to be updated to indicate safe building live load based on calculations | DEA has re-accepted by Accord on March 19, 2020. | Mar 19 2019 | On 5/9/2018: Raised floor was observed on several floor level which did not matched with accepted as-built drawings. Also, as-built drawing of partition wall layout did not matched. The factory is required to update the as-built drawings & DEA documents and submit to Accord. On 05-Oct-2020: Factory has revised the as-built drawings including the raised floor. DEA of the factory was re-accepted on 19-March-2020 including loads for the raised floors. No further discrepancy was found. On 31-Jan-2024: Corrected previously. During the inspection, load plan was found posted on the floors and floor loading was found within the allowable limit (3kPa in the storage and 2kPa for all other places). | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 15 | New finding-2: Column susciptable to vehicle impact | Protection barrier to be provided | We have provided protection barrier. | Oct 20 2018 | On 5/9/2018: The columns of main building are susceptible to vehicle impact. To protect the columns from vehicle impact barrier is required to be provided. On 05-Oct-2020: Protection was provided to prevent vehicle impact loading around the columns susceptible to vehicle impact. On 31-Jan-2024: Corrected previously. During the inspection, protection barrier was observed on the suspected columns. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 16 | New finding-3: Proposed vertical extension of existing eight storied Garments Building. | The building engineer is required to carry out the remedial works as per the accepted EA (if any) | We have already sent the updated DEA link to RSC engineering team on 13th December for their review; however, we have not yet received any response. After receiving their guidelines or suggestions, further action will be taken. | Aug 15 2024 | On 31-Jan-2024: The factory submitted the EA to RSC considering the proposed ten storied (vertical extension) Garments Building. As per the review comment on the submitted EA documents, factory is required to submit the revised EA to RSC within 15-Feb-2024. The factory is required to carry out the remedial works as per the accepted EA (if any). RPO Comments: On 5-Jan-2026 the design documents EA are currently under RSC’s review. | (within 6 months) | In Progress

## Fire
Date
05-Jan-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.G. Dresses Ltd., Plot-9, Block C, Tongi Industrial Area, Himardighi, Tongi, Gazipur,Dhaka, Gazipur, Dhaka
Date of Inspection |  | 2014-03-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Areas used for combustible storage are not separated by fire rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire rated construction. | Corrected | Mar 7 2016 | Present Status: Corrected. Defined storage area has been provided. On 11-12-16: Corrected. On 12/07/2017: Corrected as per previous follow-up. On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected as per previous follow-up. On 24-01-2021: Corrected as per previous follow-up. On 13/03/2024: Issue refer to SL 32. | Within 3 months | Corrected
Initial Inspection |  | 2 | The exit stairs are not separated from work areas and other spaces on each floor by fire rated construction | Provide minimum 1.5 hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit hardware where serving production floors. | Corrected | Mar 7 2016 | Present Status: Corrected.(Factory has installed the listed fire rated door according to Accord guide line). On 11-12-16: Corrected. On 15/10/2017: Corrected as per previous follow-up. This issue will also reflect by the issue no 26. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected as per previous follow-up. On 24-01-2021: Corrected as per previous follow-up. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected as per site condition. | Within 3 months | Corrected
Initial Inspection |  | 3 | Unsealed penetrations and openings are located in the fire -rated floor/celling assemblies. | Provide a minimum 2 hr-fire rated shaft to separate the utility risers from each floor level. | Corrected | Mar 7 2016 | Present Status: Corrected.(Factory has installed the listed fire rated door and removed all penetration work according to Accord guide line). On 11-12-16: Corrected. No such penetration has been found during follow up inspection. On 12/07/2017: Corrected. On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | The boiler and generator rooms are not separated by fire-rated construction(openings, on-rated doors, penetrations.) They are open to egress paths. | Separate the boiler and generator rooms by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain the required fire separations. | Corrected | Mar 30 2016 | On 07/March/2016: Partially Corrected.(Factory installed the listed fire rated door but they did not separate between transformer room and generator room ). On 10/April/2016: Corrected. 10 ft. brick wall has been provided. On 11-12-16: Corrected as per previous follow up. On 12/07/2017: Corrected as per previous follow-up. On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected as per previous follow-up. On 24-01-2021: Corrected as per previous follow-up. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 03 months | Corrected
Initial Inspection |  | 5 | The exit discharge path serving NW exit is less than 10 ft wide and is not separated from the building interior. Along this path are the generator rooms and electrical rooms. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way(only include this if feasible). | Corrected | Mar 7 2016 | Present Status: Corrected.(Factory installed the listed fire rated door and removed all penetration work according to Accord guide line). On 11-12-16: Corrected as per previous follow up. On 15/10/2017: Corrected as per previous follow-up. This issue will also reflect by the issue no 22. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected as per previous follow-up. On 24-01-2021: Corrected as per previous follow-up. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Referred to Issue-22. | Within 06 months. | Corrected
Initial Inspection |  | 6 | Egress doors/ gates with locking features are provided at building exits, exit stairs, along egress routes, and exit discharge. | Removes locking features from all egress doors/ gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | Storage was located in the North West exit stair. | Remove all storage from exit stairs and egress path. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Exit capacity is not adequate for the occupant load on the 6th floor. Occupant load-890 Capacity-676 | Reduce occupant load to not more than available exit capacity(676). | Corrected | Mar 7 2016 | On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 9 | Collapsible gates /sliding doors are provided at building exits, exit stairs, along egress routes, exit discharge. | Replace all gates /sliding doors along the means of egress with side-hinged, swinging egress doors. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 10 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notifications features consistent with acceptable standards. | Replace the fire alarm system with anew, listed addressable fire alarm system in accordance with NFPA 72. | Corrected | Mar 30 2016 | On 30/January/2018: Corrected as per previous follow-up. Note: Some modifications recommended based on the physical observation as: As-built drawing shall be updated as it does not match with the actual, battery calculation shall be modified and battery shall be upgraded following the calculation if required, device shall be added on missing places including location modifications, alarm audibility shall be upgraded especially on sewing floors, exposed wiring shall be protected which were found in several locations, control panel room shall be maintained clean and upgraded schematic diagram shall be posted there. On 05/09/2018: No action taken after last follow-up for the modification of the system. Issue re-opened. On 19/03/2019: Refer to issue no. 29 On 24-01-2021: Refer to issue no. 29. | Design within 4 months, install within 9 months. | Corrected
Initial Inspection |  | 11 | Inspection, testing, and maintenance for the fire alarm system it was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site.in accordance with NFPA 72. | Corrected | Mar 7 2016 | On 12/07/2017: Corrected. On 30/January/2018: Factory management shall keep the record for installed fire alarm & detection system with authentic information which shall reflect the exact picture of the installed system On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 3 months. | Corrected
Initial Inspection |  | 12 | The building is equipped with single -station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automated fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the building in accordance with NFPA 72. | Corrected | Mar 7 2016 | On 12/07/2017: Corrected on 4th follow-up. On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected as per previous follow-up. On 24-01-2021: Corrected as per previous follow-up. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 6 months. | Corrected
Initial Inspection |  | 13 | Manual on-off switch is provided for exit signage units. | Remove manual on/off switches from exit signage units to prevent them from being switched off. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 14 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. It is required to increase the number of emergency lights. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 15 | Exit sign not provided at exit. | Provide exit signs above all exits to the exterior and all doors to the exit stairs. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with the ACCORD standard. | Inspect, test and maintain the emergency lighting system in accordance with the ACCORD standard. Keep written records on-site. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 17 | New Finding: The width of aisle is less than 36 in. in second and third floor. | Provide a minimum aisle width of 36 in. | Corrected | Mar 7 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 18 | New Finding: The compressor room, electrical room located in the NW exit stair in all floors, fire pump room, gas meter room located in the egress path are not separated by fire rated construction (openings, non rated door, penetration etc.) | Separate the Compressor, electrical, fire pump and gas meter rooms by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain the required fire separations. | Corrected | Mar 7 2016 | On 12/07/2017: Corrected as per previous follow-up. On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 19 | New Finding: The building has an occupiable floor greater than 10 meter (33 feet) and is not provided with standpipe system as per NFPA14. | Provide standpipe system as per NFPA14. | We completed the installation of our fire-listed motor pump by May 31, 2025. | Nov 9 2020 | On 24-01-2021: Reportedly installation completed and factory applied for T&CVI to RSC on 13/01/2021. On 25-02-2024: T&CVI found that the system is not approved. See T&CVI report for details. On 13/03/2024: Factory shall follow last T&C VI report & apply for further T&C VI after rectification the non-compliances. On 09-Jan-25: SUPS found active and Fire Pump Controllers were in normal condition during the inspection. The Factory has planned to extended the building vertically up to 9-storied (currently 7-storied) and they have already submitted the DEA to RSC for review. After the vertical extension sprinkler system will be required in addition with standpipe system for the factory building. So, factory wants to change the electric fire pump motor based on the requirement of sprinkler system. However factory has rectified rest of the non-conformity of SUPS as per last conducted T&CVI (conducted on 25 Feb 2024). RPO Comments on 9-July-2025: This factory is determined as ready for Testing & Commissioning for the Fire Protection system. | Design within 2 months, installation within 6 months | Pending Verification
Follow Up Inspection |  | 20 | New Finding (3rd Follow up ): Dining room is not separated by fire-rated construction having non rated door and unsealed penetrations and openings. | Separate the dining room by 2- hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. | Corrected | Jul 20 2016 | On 12/07/2017: Proper separation for dining area has not been provided yet. On 15/10/2017: Fire separation has not been completed yet. On 30/January/2018: Corrected On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 21 | New Finding (3rd Follow up ): Unsealed penetrations and openings are located in exit stair enclosures. Location: First Floor. | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | Corrected | Jul 20 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Corrected as per previous follow-up. On 19/03/2019: Corrected. Penetration has been sealed. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 22 | New Finding (3rd Follow up ): Exit passageway is not separated by fire rated construction. Location: Ground Floor North Side. | Separate the exit passageway (ceiling, floor, wall etc.) by 1/2- hr. fire-resistance rated construction and shall terminate at an exit discharge. | We have now arranged the certificate according to the latest RSC follow-up inspection report. | Jul 21 2020 | On 15/10/2017: It has been found same as the previous follow up. Factory will ensure third party certification of the installed fire damper. On 30/January/2018: Corrected On 05/09/2018: Exit discharge path of north and south side of the building are not properly separated yet. Unseal penetrations observed. On 19/03/2019: Not corrected. Still unsealed penetrations observed. On 24-01-2021: Not corrected. Unsealed penetration observed. Factory shall separate the exit passageway as per standard. On 13/03/2024: Generator radiator duct has been protected by listed damper. but proper documents weren't found at site & inspection accessibility has not ensured . Damper size based on opening doesn't match with provided certificate. On 09-Jan-25: Corrected. The factory has provided the UL certificate and other documents. Inspection accessibility has been ensured for verification. The damper size has been confirmed based on the general information from the UL directory. However, the factory shall collect the manufacturer's declaration for the installed damper size. | Within 1 month | Corrected
Follow Up Inspection |  | 23 | New Finding (4th Follow up ): Shutter gate is provided at building main exit discharge ( South-west side). | Replace shutter door along the means of egress with side hinged, swinging egress doors. | Corrected | Oct 10 2016 | On 15/10/2017: Corrected as per previous follow-up. On 30/January/2018: Corrected On 05/09/2018: Semi swing (non-complaint) door with locking features were observed in the main exit. On 19/03/2019: Corrected as per site observation. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 24 | New Finding(6th Follow-Up): Unsealed elevator shafts are located inside the working place at all floors . | Provide a minimum 2-hr fire- rated elevator shaft to separate from each floor level and seal all penetrations in floor/ceiling assemblies to maintain the fire separation. | Corrected | Feb 12 2017 | On 15/10/2017: Fire separation has not been completed yet. On 30/January/2018: Corrected On 05/09/2018: Corrected. On 19/03/2019: Corrected. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 25 | New Finding (6th Follow up): Penetration has been found unsealed in storage room ( through light). | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | Corrected | Jan 12 2017 | On 15/10/2017: Opening and penetration have been found from store room to embroidery section, day care room and north side of store room on ground floor. On 30/January/2018: Sealed On 05/09/2018: Corrected. Sealed. On 19/03/2019: Corrected. Sealed. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 26 | (6th Follow Up): Exit stairs are not properly separated by office area in 6th floor, idle machine storage room and lift control room (newly constructed). Fire door has been found manually open with external source. | Stair shall be enclosed with a minimum 1.5 hr fire-rated construction. Seal all unprotected openings and provide minimum 2 hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | We have done all fire door interfacing and closing work properly as per RSC standard. | Jul 21 2020 | On 05/09/2018: In progress. Stair-2 and 3 are not properly separated yet from ground floor. Production section , office section, medical and childcare were observed open with the exit stairs. Besides electrical DB was observed in the exit stair enclosure which shall be removed. Discharge shall be directly outside. Unseal penetrations along the discharge path shall be sealed.( Store window on ground floor with SW exit stair.). Maintenance of the fire doors are required. On 19/03/2019: Not corrected. Some fire doors were found not credible due to interfacing improper, door coordinators not functional and few of them observed not properly self closing. On 24-01-2021: Not corrected. During follow-up inspection some fire rated doors found not interfacing properly and some of them were observed not self closing properly. Factory shall ensure that all the fire rated doors are functional as per standard. On 13/03/2024: Door was found functional & corrected. On 09-Jan-25: Corrected. Fire Doors were found functional and interfaced with FACP during the inspection. | Within 2 months | Corrected
Follow Up Inspection |  | 27 | New Finding (6th Follow Up): Building did not have stair designation signs at required locations. | Provide stair designation signs at required locations. | Corrected | Jul 22 2017 | On 30/January/2018: Corrected On 05/09/2018: Corrected On 19/03/2019: Corrected as per previous follow-ups. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 28 | New Finding (8th FUI): Stair-01 exit enclosure has unprotected window opening within 10 feet from the production area on each floor level | Seal all the unprotected opening within 10 feet of exit stair enclosure from the production area to provide required 2 hr. fire rated separation | Corrected | Feb 28 2018 | On 30/January/2018: New Finding On 05/09/2018: In progress. Unseal penetrations were observed with production floor at stair-3 On 19/03/2019: Corrected. Sealed. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding in 11th Follow-up: Installed fire alarm and detection system does not provide alarm and notification features system in accordance with NFPA 72. (As built design mismatched with actual site plan, wrong battery calculation, PA system not interfaced, Exhaust not interfaced properly, wrong selection of detector, inadequate sounder, MCP, detector are missing where required, improper spacing in few places.) | Modification of the fire alarm and detection system shall be in accordance with NFPA 72. Re-testing and commissioning is required for the system. | Corrected | Nov 9 2020 | New Finding On 19/03/2019: T&C VI found that, Fire alarm system was not yet ready for inspection and testing. However, after completion of the system installation and modification work, the testing of the installation shall be conducted in accordance with NFPA72 acceptance testing requirements. Documents of all testing shall be submitted for review to the Chief Safety Inspector. The Owner shall notify ACCORD prior to conducting final acceptance testing of the Fire Alarm System installation to allow the ACCORD the option of witnessing this testing and conduct a final inspection of the installation. On 24-01-2021: Reportedly installation completed and factory applied for T&CVI to RSC on 13/01/2021. On 25-02-2024: T&CVI found that the system is approved. See T&CVI report for details. On 13/03/2024: Corrected on last T&C VI. System was found functional. On 09-Jan-25: Corrected. FADS was found active and free of abnormal conditions during the inspection. | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New Finding in 11th Follow-up: Manual on-off switch is provided for most of the exit signage units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Corrected | Oct 5 2018 | New Finding On 19/03/2019: Corrected. Removed. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding in 11th Follow-up: Storage was located in the exit stair and egress path. | Remove storage from the exit stairs and egress path | Corrected | Sep 7 2018 | New Finding On 19/03/2019: Corrected. Removed. On 24-01-2021: Corrected. On 13/03/2024: Corrected as per site condition. On 09-Jan-25: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 32 | New Finding: Areas used for combustible storage on the several floors are not separated by fire rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire rated construction. | Corrected | Jul 21 2020 | On 19/03/2019: New Finding. On 24-01-2021: Not corrected. During follow-up inspection storage area was found not separated from work areas on 5th floor. On 13/03/2024: In-process storage doesn't maintained as per standard at 2nd & 4th floor. On 09-Jan-25: Corrected. In-process storage was found within the limits during the inspection. | Within 1 month | Corrected
Follow Up Inspection |  | 33 | New Finding (12th FUI): Unsealed/unprotected penetrations are located in the fire-rated floor/ceiling assemblies due to plumbing pipe. Location: Ground floor Mezzanine store room. | Seal/protect all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's guideline. or, Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | We sealed unprotected ceiling penetrations caused by plumbing pipes with a firestop collar as per RSC guidelines on 2nd September 2025. | May 14 2024 | New Finding On 09-Jan-25: No action has been taken yet. RPO Comments: On 29-Oct-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 34 | New Finding (12th FUI): Occupants from Stair -02 & Stair-03 discharge through parking area which is not separated. | Separate the parking area by 2-hr fire separation . or, Provide a 1-hr fire rated corridor from stair-02 & stair-03. Or, Relocate the parking area from this area to a safe location. | Corrected | May 14 2024 | New Finding On 09-Jan-25: Corrected. Car parking area has been relocated from the exit discharge of Stair-2 & Stair-3. | Within 2 months | Corrected
Follow Up Inspection |  | 35 | New Finding (12th FUI): Occupants from fabric inspection room at ground floor discharge through store area without rated corridor. | Provide a 1-hr fire rated corridor from fabric inspection room to nearest exit Or, Relocate the fabric inspection area from this location to a safe location ensuring safe exit. | We completed the transfer of our fabric inspection room to the northwest side of the mezzanine floor by 27 June 2025. | May 14 2024 | New Finding On 09-Jan-25: The Factory has planned to shift the fabrics inspection room to the Mezzanine floor, but it is not shifted yet. RPO Comments on 9-July-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification

## Electrical
Date
05-Jan-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.G. Dresses Ltd., Plot-9, Block C, Tongi Industrial Area, Himardighi, Tongi, Gazipur,Dhaka, Gazipur, Dhaka
Date of Inspection |  | 2014-03-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | No cable tray in power shaft for cables. | Install a ladder to support the cables. Ensure the cables are tightly latched inside the ladder and provide covers made of noncombustible material preferably metallic sheet to protect the cables 'insulation from physical damage as well as prevent the ingress of debris, dust and lint. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 3 month | Corrected
Initial Inspection |  | 2 | Wires lay on floor unprotected. | Install a ladder (on floor at safe location)to support the cables. Ensure the cables are tightly latched inside the ladder and provide covers made of noncombustible material preferably metallic sheet to protect the cables 'insulation from any physical damage as well as prevent the ingress of debris, dust and lint. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 3 month | Corrected
Initial Inspection |  | 3 | Combustible material is used for battery in Generator room. | Remove all the combustible materials from electrical equipment. Generator Battery must be placed on the battery stand made of noncombustible material (sheet fabricated). | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 1 month | Corrected
Initial Inspection |  | 4 | Earth conductor passing through the window. | Earth conductor should be passed through PVC or steel pipe (through wall) and it should be supported by suitable means. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 3 month | Corrected
Initial Inspection |  | 5 | Cable trenches are not protected. | Provide cover made of non combustible material preferably metallic sheet (checkered plates) to protect the cables 'insulation from physical damage as well as prevent the ingress of debris, dust and lint. | Corrected | Jul 23 2015 | Verified at 2nd follow up visit. | Within 3 month | Corrected
Initial Inspection |  | 6 | HT cable dropping from 11kV pole not supported to the pole. | Install a ladder/pipe made properly supported with pole for supporting the service cables 'insulation from any physical damage. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 3 month | Corrected
Initial Inspection |  | 7 | Cable is supported in an improper way. | Use PVC or steel pipes(preferably on floor),clamped with saddle, for carrying cables. Wire shall not be used for tying the cables. | Corrected | Mar 9 2015 | Verified at 2nd follow up visit. | Within 3 month | Corrected
Initial Inspection |  | 8 | Wires connected to bus bar without using cable lug. | Cables should be connected to terminals only by soldered/welded lugs according to the size of the respective cables. Proper crimping tools must be used to punch the socket. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 1 month | Corrected
Initial Inspection |  | 9 | Multiple cables connected at a terminal of the busbar. | Terminate single cable (lugs/socket) on a single point of busbar to get better electrical continuity and avoiding loose connection. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 1 month | Corrected
Initial Inspection |  | 10 | Panel doors not connected with earth bond. | Provide earth connection for body of metallic distribution boards using green cables preferable braid so that the metallic door and body remain at zero potential all the time. | Corrected | Jun 25 2015 | Verified at 2nd follow up visit. | Within 3 month | Corrected
Initial Inspection |  | 11 | Excessive dust and lint deposit in transformer room. | Establish a routine cleaning program to keep neat and clean the transformer room. Shut the power of the transformer and clean the exterior of the transformer at scheduled period. | Corrected | Jun 25 2015 | Verified at 2nd follow up visit. | Within 1 month. | Corrected
Initial Inspection |  | 12 | Flexible conduit used for cable protection. | Install cable duct or tray to support the cables and provide covers made of non-combustible material preferably metal to protect the cables 'insulation from any physical damage as well as prevent ingress of debris. Dust and lint. | Corrected | Aug 15 2015 | Verified at 2nd follow up visit. | Within 1 month | Corrected
Initial Inspection |  | 13 | Silica gel in transformer breather, discolored. | Replace the silica gel or perform the maintenance to remove the moisture from the silica gel. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 1 month | Corrected
Initial Inspection |  | 14 | Lighting fixture's location is not proper. | Use PVC pipe for carrying wiring used for the noted lighting with proper support. | Corrected | Jul 4 2014 | Verified at 1st follow up. | Within 1 month | Corrected
Follow Up Inspection |  | 15 | New Finding: Inadequate space around transformer for performing maintenance work | Ensure minimum 1.07m working space around the transformer (and related electrical installations) | Corrected | Jul 15 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 16 | New Finding: Transformer Arcing horns are not aligned | Transformer arcing horn should be aligned. | Corrected | Jul 15 2015 | Verified at 2nd follow up visit. | 1 month | Corrected
Follow Up Inspection |  | 17 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Corrected | Apr 15 2016 | Verified at 3rd follow up visit. | 4 months | Corrected
Follow Up Inspection |  | 18 | New Finding: Generator output supply terminal box open. | Cable terminating at the generator box must be fixed bottom plate with cable gland. | Corrected | Jul 15 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 19 | New Finding: Generator frame is not earthed by 2 separate and distinct earth. | Generator must be connected to earth securely at least two points. | Corrected | Jul 15 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 20 | New Finding: Flexible PVC pipe has been used inside the panel to cover cables. | Remove all the flexible PVC pipes from inside of the panel | Corrected | Jul 31 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 21 | New Finding: Phase barrier/separator has not installed. | Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. | Corrected | Jul 15 2015 | Verified at 2nd follow up visit. | 2 months | Corrected
Follow Up Inspection |  | 22 | New Finding: Power cables are bent excessively | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Corrected | Aug 31 2015 | Verified at 2nd follow up visit. | 3 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Panel identification and danger signs not marked on the panels. | Panels must be identified and danger signs marked on the panels. Each panel must be provided with schematic diagram of the panel showing branch circuits. | Corrected | Jan 31 2016 | Verified at 3rd follow up visit. | 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding: Compressor machine mounted on wheel. | Compressor machine mounted on wheel must be anchored or the wheels must be locked to prevent from trolling. | Corrected | Jul 31 2015 | Verified at 2nd follow up visit. | 2 months | Corrected
Follow Up Inspection |  | 25 | New Finding: Multiple cables connected in the bus bar through single lugs. | Each cable must be connected in the bus bar through single lugs. | Corrected | Aug 31 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 26 | New Finding: Multiple cables terminated at MCCB terminals. | Terminate each power cable at single terminal and use proper sized cable lug (where applicable) | Corrected | Aug 5 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 27 | New Finding: Motor/Pumps are not earthed and not fixed properly | Ensure earthing connection for all motor/ pumps coil and body. Fix the Motor/Pump on a base properly. | Corrected | Jul 9 2015 | Verified at 2nd follow up visit. | 2 months | Corrected
Follow Up Inspection |  | 28 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9m apart from hot area. | Corrected | Jul 31 2015 | Verified at 2nd follow up visit. | 2 months | Corrected
Follow Up Inspection |  | 29 | New Finding: Earth cables are terminated at a single terminal instead of using any earth bus bar. | Each earthing cable must be connected in the proper size earth bus bar through single lugs. | Corrected | Aug 31 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 30 | New Finding: Cable color coding is not available. | Remove the insulation tape from the cable. Use colorful insulation cable (red, yellow, blue) instead. | Corrected | Aug 31 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 31 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s) | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this | Corrected | Dec 31 2015 | Verified at 3rd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 32 | New Finding: Lightning Protections System (LPS) is inadequate for the factory | Redesign/modify LPS for your factory to increase safety; Factory have to submit LPS design to Accord before starting | Corrected | Jun 12 2016 | On 07/03/2016: LPS drawing is found but not installed yet. New committed timeline to install LPS is given till 15 May, 2016. On 10/04/2016: This is still pending. The committed timeline is yet to be due. They have committed to complete this issue by May 15, 2016. On 11/12/2016: Few modifications are needed. Prepare an as-built drawing. On 12/07/2017: Not corrected. Need to bond with all metal part and provide another parallel path for the air terminals. On 15/10/2017: Not Corrected.Bonding needed with all metal parts and install parallel paths for the air terminals. Higher sized rods need to trim. On 30/01/2018: Not Corrected. All exposed column rods need to be bonded with main conductor. On 05/09/2018: Not corrected. Installation done. Inadequate connection between conductor and baseplate. Replace rusted nut bolts. On 19/03/2019: Corrected. | 4 months | Corrected
Follow Up Inspection |  | 33 | New Finding: Insulation resistance test of electrical equipment is not performed | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off) | Corrected | May 15 2016 | On 07/03/2016: Factory has a report on insulation resistance test which is improper due to missing of sufficient data. So, this issue is not corrected yet & new committed timeline is given till 15 April, 2016. On 10/04/2016: This is still pending. The committed timeline is yet to be due. They have committed to complete this issue by April 15, 2016. On 11/12/2016: Corrected | 3 months | Corrected
Follow Up Inspection |  | 34 | New Finding: Earth Pit resistance record is unavailable | Record earth pit resistance for all the earth pit and do once in a year | Corrected | May 15 2016 | On 07/03/2016: Improper earth pit resistance report is found. Earth pit resistance test is done for earthing cables of distribution boards but not for earthing pit. New committed timeline is given till 15 April, 2016. On 10/04/2016: This is still pending. The committed timeline is yet to be due. They have committed to complete this issue by April 15, 2016. On 11/12/2016: Corrected | 3 months | Corrected
Follow Up Inspection |  | 35 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location | Corrected | Jul 31 2015 | Verified at 2nd follow up visit. | 2 months | Corrected
Follow Up Inspection |  | 36 | New Finding: Thermo graphic scanning of the entire electrical system has not been tested and recorded. | Thermo graphic scanning for the entire electrical system must be performed on a bi-annual basis and recorded | Corrected | Oct 9 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 37 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance) | Corrected | Jul 31 2015 | Verified at 2nd follow up visit. | 2 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Transformer Oil Test report is unavailable | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Corrected | Jul 15 2015 | Verified at 2nd follow up visit. | 3 months | Corrected
Follow Up Inspection |  | 39 | New Finding: Earth lead cable & Earth Continuity Conductor size is inadequate & undersize. | Resize earth lead cable and ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | Corrected | Feb 28 2016 | Verified at 3rd follow up visit. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered | Corrected | Jun 15 2016 | On 11/12/2016: Corrected | 2 months | Corrected
Follow Up Inspection |  | 41 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Corrected | May 30 2016 | On 11/12/2016: Corrected | 1 month | Corrected
Follow Up Inspection |  | 42 | New Finding: Transformer neutral and system earthing are not segregated. | Ensure separate earthing connection for all neutrals, generator body, transformer body, electrical system and Lightning Protection System. Need to provide identification for all of them. | Corrected | May 15 2016 | On 11/12/2016: Corrected | 1 month | Corrected
Follow Up Inspection |  | 43 | New Finding: Inadequate working space around (or in front of) board/panels. | At least 1 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Corrected | Jan 22 2017 | On 12/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Renovation work doesn't reflect on existing SLD | Electrical SLD must be updated properly; all the required information must be mentioned there; and it shall be updated when you do substantial amount of changes of your electrical system. | Corrected | Nov 15 2017 | On 15/10/2017: Not Corrected. Timeline has been extended till 15/11/2017. On 30/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Electrical power cables/circuits and panels are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables/circuits used in the system according to SLD. | Corrected | Nov 15 2017 | On 15/10/2017: Not Corrected. Timeline has been extended till 15/11/2017. On 30/01/2018: Not Corrected. On 05/09/2018: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Hot Spots were observed at several points | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Nov 15 2017 | On 30/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Lights in the store room / storage areas are uncovered/unprotected. | Lights in the store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. And a secure cabling shall be ensured. | Corrected | Nov 15 2017 | On 30/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | Corrected | Nov 15 2017 | On 30/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Power cables entering to or exiting from Distribution board/panel are not properly fixed. | Power cables entering to or exiting from distribution board/panel must be fixed through Panel base/top plate using cable glands (metal/PVC). You may use cable tray/ladder to support cables. | Corrected | Mar 10 2018 | On 05/09/2018: Not corrected On 19/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Distribution Board's top/bottom is left open (typical issue) | Seal each distribution board's top/bottom; and use cable glands holding/supporting cables. | Corrected | Mar 10 2018 | On 05/09/2018: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Apr 30 2019 | On 24/01/2021: Corrected. Not found this issue in this follow-up. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Tap off box (TOB) are not identified properly | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on TOB used in the system according to SLD. | Corrected | Apr 30 2019 | On 24/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Circuit is drawn from bus bar without any protective means | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). | Corrected | Apr 30 2019 | On 24/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Panel/distribution board is not firmly fixed with the foundation (Panel kept on brick). | Each electrical installation in the facility shall be grouted properly | Corrected | Apr 30 2019 | On 24/01/2021: Corrected. | 1 Month | Corrected

## Boiler
Date
05-Jan-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.G. Dresses Ltd., Plot-9, Block C, Tongi Industrial Area, Himardighi, Tongi, Gazipur,Dhaka, Gazipur, Dhaka
Date of Inspection |  | 2022-08-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 3214 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | Boiler registration No. 3214 has been cancelled, and the boiler has been permanently shut down. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 3688 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | The boiler manufacturer’s nameplate with accurate technical information and the manufacturer’s name in standard language will be arranged and installed within 3 months. | Nov 16 2025 | Comments on 17-Nov-2025: Factory given timeline is not accepted. The new timeline is 16-Dec-2025. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 3 | BB 3214 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Boiler registration No. 3214 has been cancelled, and the boiler has been permanently shut down. | Dec 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 3214 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Boiler registration No. 3214 has been cancelled, and the boiler has been permanently shut down. | Dec 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 3688 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | A separate and clearly visible LLWL marking has been installed beside the gauge glass as per standard boiler safety requirements. The marking ensures that operators can easily identify the LLWL position during boiler operation. | Dec 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 3688 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | All required documentation, including manufacturing drawings and calculations, P&ID, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operation and maintenance logbook, O&M manual, water treatment design and calculation, flue gas analysis report, and water treatment report will be collected, organized, and made available within 3 months to verify the current condition of the boiler. | Dec 16 2025 | Comments on 17-Nov-2025: Factory given timeline is accepted. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 7 | BB 10213 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Boiler registration No. 10213 has been cancelled, and the boiler has been permanently shut down. | Dec 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 10213 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Boiler registration No. 10213 has been cancelled, and the boiler has been permanently shut down. | Dec 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 12605 | Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. | The safety valve outlet line has been properly redirected and extended to a safe discharge location, ensuring that it does not obstruct the emergency discharge path and is free from the danger of scalding. The modification was completed in compliance with safety standards. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 12605 | Nameplates for safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | All nameplates of safety valves have been permanently fixed in clearly visible positions and made easily readable. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 12605 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | All unused and unprotected steam lines have been properly terminated, insulated, or sealed in accordance with standard safety requirements to eliminate any risk of burn hazards to operators. | Oct 30 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 12605 | Inconsistency was observed between the nameplate data and the CIoB provided certificate copy for the boiler regarding boiler’s maker’s number. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | The information on the nameplate and the CIoB certificate has been verified and made consistent. Any changes have been approved by CIoB, and the approved copy has been maintained on-site. | Dec 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 14936 | Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. | The safety valve outlet line has been properly redirected and extended to a safe discharge location, ensuring that it does not obstruct the emergency discharge path and is free from the danger of scalding. The modification was completed in compliance with safety standards. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 3688 | Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. | The safety valve outlet line has been properly redirected and extended to a safe discharge location, ensuring that it does not obstruct the emergency discharge path and is free from the danger of scalding. The modification was completed in compliance with safety standards. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 3688 | Visual flame monitoring glass was out of order. | The visual flame monitoring glass shall be replaced with an appropriate one. | The existing visual flame monitoring glass has been replaced with an appropriate, safety-compliant glass to ensure clear visibility of the flame during operation. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 3688 | The safety valve was found to be mounted using a tee/elbow joint. | Safety valves must be mounted directly onto the boiler shell without any branch connections in between. | All safety valves have been properly mounted directly onto the boiler shell without any branch connections in between, in compliance with safety standards and manufacturer specifications. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 17 | BB 14936 | Salt and soft scale formation was observed on the waterside of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | The boiler has been cleaned, a water treatment station is now in operation, feed and boiler water quality are being regularly verified and monitored, and the boiler is operated with proper blowdown procedures. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 18 | BB 14936 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | A Steam Pressure Limiter has been installed and tested to ensure it is fully functional, maintaining safe boiler pressure limits. | Nov 16 2025 | Comments on 17-Nov-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification