## Structural
Date
29-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Refat Garments Ltd - Extension (Previously THAT'S IT Sweater Ltd)., 119 – 145 Narshinghapur, Ashulia, Savar, , Narshinghapur, Dhaka, Dhaka
Date of Inspection |  | 2015-03-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Slender columns were found in ancillary building but no drawing and design was available. | Engage a qualified structural engineer to confirm structural performance of the structure. | Corrected | May 30 2016 | On 23/07/2017: This is issue is required to be covered under DEA report. DEA of this factory had been reviewed and accepted by Alliance on 7th feb, 2016. Remediation has been completed as per accepted drawing. Factory got retrofitting completion certificate from consultant. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. DEA was prepared and approved by Alliance on 07/02/ 2016. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: DEA was accepted from Alliance on 7the February 2016. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. Structural performance was checked in DEA and DEA was accepted by Alliance on 7-Feb-2016. Issue remains corrected. On 20-Oct-2022: Corrected from the previous inspection. This issue has been covered in the accepted DEA. On 23-Aug-2023: Corrected from previous inspection. This adequacy check for slender columns was covered in the accepted DEA. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 2 | The structural document confirms the conformance of BNBC 1993 for shed-3. But no credible structural documentation was available for shed-1 and shed-2. | Engage a qualified structural engineer to develop the required documents to confirm the structural integrity of the buildings. Documents must comply with Alliance Standard Part 8 Section 8.19 and 8.20. | Corrected | Mar 20 2016 | On 23/07/2017: This is issue is required to be covered under DEA report. DEA of this factory had been reviewed and accepted by Alliance on 7th feb, 2016. Remediation has been completed as per accepted drawing. Factory got retrofitting completion certificate from consultant. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. DEA was prepared for shed-1, 2 & 3 and approved by Alliance on 07/02/ 2016. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: DEA was accepted from Alliance on 7the February 2016. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. Structural integrity was checked in DEA and DEA was accepted by Alliance on 7-Feb-2016. Issue remains corrected. On 20-Oct-2022: Corrected from the previous inspection. This issue has been covered in the accepted DEA. On 23-Aug-2023: Corrected from previous inspection. This issue has been covered in the accepted DEA. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 3 | Credible sets of structural design documents were available for shed-3 but no structural design documents were available for shed-1, shed-2 and ancillary building. | Have a qualified structural engineer prepare credible as-built documents based on the requirements of Part 8 Section 8.19 of the Alliance Standard. | Corrected | Mar 20 2016 | On 23/07/2017: A set of structural drawing has been prepared and submitted to Alliance along with DEA report. DEA of this factory had been reviewed and accepted by Alliance on 7th feb, 2016. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. As built drawings have been prepared as part of DEA for shed-1, 2 & 3 and approved by Alliance on 07/02/ 2016. No discrepancy was found during inspection. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: A set of as-built drawing has been prepared along with DEA. DEA was accepted from Alliance on 7the February 2016. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. As-built drawings were prepared and accepted with DEA by Alliance on 7-Feb-2016. Issue remains corrected. On 20-Oct-2022: Corrected from the previous inspection. As-built drawings have been prepared and accepted along with DEA. On 23-Aug-2023: Corrected from previous inspection. As-built drawings have been prepared and accepted along with DEA. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 4 | Standing water was noticed on roof top of ancillary building. | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Corrected | Apr 15 2015 | On 23/07/2017: Standing water was not observed during inspection and proper drainage was found. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. No standing water was found on the roof top. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: No water ponding was found at roof top. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. No signage of water ponding was observed. Issue remains corrected. On 20-Oct-2022: Corrected from the previous inspection. No signage of water ponding was observed on the roof. On 23-Aug-2023: Corrected from previous inspection. During inspection, no water ponding was observed on roof of the Ancillary Building. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. Factory has provided water proofing layer on roof and drainage was also found improved. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 5 | The roof slab of ancillary building and some part of shed-3 are made of MCAC exposed to rainfall but have not been coated with a protective coating to prevent water intrusion. | Provide a protective coating at the structural elements constructed with MCAC exposed to rainfall or other sources of water. Have protective coating approved by the Alliance or a qualified structural engineer. | Corrected | Apr 15 2015 | On 23/07/2017: Protective coating has been provided on roof top of ancillary building. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. No standing water was found on the roof top. Protective coating has been provided on roof top of ancillary building. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: Protective coating has been provided at roof top of the ancillary building. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. Protective coating was applied. Issue remains corrected. On 20-Oct-2022: Corrected from the previous inspection. Protective coating on the roof slab has already been applied. On 23-Aug-2023: Corrected from previous inspection. During inspection, water proofing layer was observed on roof slab. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. Factory has provided water proofing layer on roof and drainage was also found improved. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 6 | 3 nos of 2000 ltrs plastic water tank was found in the roof top of ancillary building but no structural documentation was available. | Engage a qualified structural engineer to confirm and document that provisions have been made to accommodate concentrated loads. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Corrected | Mar 20 2016 | On 23/07/2017: No water tank was found on roof top. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. No water tank was found on roof top. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: No water tank was found at roof top. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. No water tank was observed. On 20-Oct-2022: Corrected from the previous inspection. No water tank was observed on the roof. On 23-Aug-2023: Corrected from previous inspection. Factory has removed the water tanks from roof. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. No water tank was observed on the roof. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 7 | Racks in the storage area of shed-1 were not anchored to the resist earthquake forces. | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Corrected | Apr 15 2015 | On 23/07/2017: Non structural element has been anchored. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. Non structural element has been anchored. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: Non-structural elements were found properly anchored. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. On 20-Oct-2022: Corrected from the previous inspection. Anchorage of non-structural elements were observed. On 23-Aug-2023: Corrected from previous inspection. During inspection, remediation works were observed on-going. On 12-Mar-2024: Corrected previously. Non-structural elements were found adequately anchored. On 21-Oct-2024: Corrected previously. Anchorage of non-structural elements were observed. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 8 | Shed-3 was constructed in 2010 but the structural documents confirm conformance to BNBC 1993 not BNBC 2006. No structural documents was available for shed-1 and shed-2. | Have a qualified structural engineer document compliance with the seismic and wind requirements stated in the 2006 BNBC. | Corrected | Mar 20 2016 | On 23/07/2017: This is issue is required to be covered under DEA report. DEA of this factory had been reviewed and accepted by Alliance on 7th feb, 2016. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. DEA was prepared for shed-1, 2 & 3 and approved by Alliance on 07/02/2016. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: DEA was accepted from Alliance on 7the February 2016. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. On 20-Oct-2022: Corrected from the previous inspection. This issue has been covered in the accepted DEA. On 23-Aug-2023: Corrected from previous inspection. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 9 | The structural document confirms the conformance of BNBC 1993 for shed-3. But no credible structural documentation was available for shed-1 and shed-2. | Engage a qualified structural engineer to confirm satisfactory structural performance of the buildings under wind loading. | Corrected | May 30 2016 | On 23/07/2017: This is issue is required to be covered under DEA report. DEA of this factory had been reviewed and accepted by Alliance on 7th feb, 2016. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. DEA was prepared for shed-1, 2 & 3 and approved by Alliance on 07/02/2016. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: DEA was accepted from Alliance on 7the February 2016. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. On 20-Oct-2022: Corrected from the previous inspection. This issue has been covered in the accepted DEA. On 23-Aug-2023: Corrected from previous inspection. During inspection, it was observed that factory has completed around 90% remediation work for shed 3, On 12-Mar-2024: Corrected previously. (See item no 12) On 21-Oct-2024: Corrected previously. (See item no 12) On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 10 | Geotechnical reports were available and kept on site for shed-1 and shed-3 . The recommendation is 1.75 TSF at a depth of 8ft from EGL for some bore holes and 1.25 TSF at a depth of 8ft from EGL for some bore holes. But no geotechnical report was available for shed-2. | Under guidance from a qualified structural engineer arrange geotechnical investigation at close vicinity of the structure and make the report available for review. | Corrected | Oct 30 2015 | On 23/07/2017: Geotechnical report was found, which is incorporated in DEA report. DEA of this factory had been reviewed and accepted by Alliance on 7th feb, 2016. On 30/09/2018: This issue has been corrected as per 1st follow up inspection. DEA was prepared for shed-1, 2 & 3 and approved by Alliance on 07/02/2016. On 29/09/2019: Corrected in previous follow up inspection. On 26-Dec-2021: DEA was accepted from Alliance on 7the February 2016. Issue remains corrected. On 31-Aug-2022: This issue was corrected in previous follow-up inspection. On 20-Oct-2022: Corrected from the previous inspection. Geotechnical investigation was carried out. On 23-Aug-2023: Corrected from previous inspection. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Initial Inspection |  | 11 | Occupancy certificate for buildings were not available during this inspection. | Apply to appropriate authority in an expeditious manner for issuance of the Certificates of Occupancy for each building and ancillary structure according to building use. | Corrected | Dec 31 2016 | On 23/07/2017: Not applicable. On 30/09/2018: N/A. On 29/09/2019: N/A. On 26-Dec-2021: N/A On 31-Aug-2022: N/A On 20-Oct-2022: Corrected from the previous inspection. On 23-Aug-2023: Corrected from previous inspection. On 12-Mar-2024: Corrected previously. On 21-Oct-2024: Corrected previously. On 12-Mar-2026: Previously corrected. | May 31 2015 | Corrected
Follow Up Inspection |  | 12 | New finding-1: Revised DEA documents required to be submitted to ACCORD | DEA and retrofitting drawing (if necessary) is required to be revised considering the issues mentioned in retrofitting verification report and carry out any further remediation arising from revised DEA | Corrected | Apr 17 2019 | On 30/09/2018: During inspection, it was found that factory has not strengthened several members as per accepted retrofitting drawing (Detail in retrofitting verification report). Later, factory completed the remediation works and sent pictorial evidence. But, while checking analysis file, some observations were found regarding design consideration, overstressed member and assignments of loading. Factory is required to revise DEA and retrofitting drawing (if necessary) considering the issues mentioned in retrofitting verification report and submit to ACCORD. Factory shall carry out any further remediation as per recommendation of reaccepted DEA report after receiving acceptance from ACCORD. On 29/09/2019: Factory has submitted the revised DEA to Accord. DEA review comment has been sent from Accord on 22 August 2019. Factory was required to submit the revised DEA within 30 September 2019. Till Date of inspection, factory didn't submit the DEA to Accord. On 26-Dec-2021: EA documents of the Single Storied Shed-1, Shed-2, Shed-3, Shed-4, Shed-5 (Part-1 & 2), and Sub-station room have been reviewed & accepted by RSC on 13th November 2021. However, factory sent mail on 23rd December 2021 declaring that they are planning for demolition of these structures. During inspection, no demolition works were found started yet. On 31-Aug-2022: Factory submitted Engineering Assessment (EA) and the EA was accepted (Single Storied Shed-1, Shed-2, Shed-3, Shed-4, Shed-5 (Part-1 & 2), and Sub-station room) by RSC on 13-Nov-2021 with retrofitting timeline-15 March 2022 for 5 no's of sheds; single storied Shed-1, Shed-2, Shed-3, Shed-4, Shed-5 (Part-1 & 2). On 23 Dec 2021, factory sent mail declaring that all shed buildings of the "That` s It Sweater Ltd (RSC ID:11605)" will be demolished within the period of July to August-2022. On 17 April 2022, factory sent another mail asserting that they will start shifting machines within 20-Nov-2022, start demolition work within 1-Dec-22 and complete demolition work within 30-Dec-22. On 31st Aug 2022, through email factory sent demolition plans of the five sheds where starting and finishing timelines of the demolition were 15-Nov-2022 and 31 -Dec-2022 accordingly. Till the last inspection date (31-Aug-2022), factory did not start the demolition work. As per extended timeline from RSC factory is required to complete the demolition work within 30 November 2022. On 20-Oct-2022: The factory management stated that they will demolish the five sheds (Shed-1,2,3,4&5) instead of remediation. The factory shared a demolition schedule with RSC on 1st September 2021. As per schedule demolition will be started from 1 Nov 2022 and ended on 31 Dec 2022. However, the sheds are as previous conditions. On 23-Aug-2023: EA for shed 1,2,3,4 & 5 was accepted on 13th Nov 2021 and the extended timeline for remediation work was 31st Dec 2022. During inspection, it was observed that factory has completed around 90% remediation work for shed 3&5, around 30% for shed 1 & 4 and demolished shed 2. Factory needs to complete all the remediation works without further delay. On 12-Mar-2024: EA for shed 1,2,3,4 & 5 was accepted from RSC on 13th Nov 2021. As per EA recommendation remediation is required for Shed- 1, 3, 4 & 5. During inspection, retrofitting was found completed for Shed 1, 3, 4 & 5 and Shed 2 was found demolished. However, some discrepancy was found between retrofitting drawing and on-site condition of Shed 1. Proposed cable bracing was found installed 16 mm instead of 22mm. Factory is required to install all proposed cable bracing as per accepted retrofitting drawing or revised the design documents as per on site condition. On 21-Oct-2024: EA for shed 1,2,3,4 & 5 was accepted from RSC on 13th Nov 2021. Factory completed the retrofitting work for Shed 1, 3, 4 & 5 and demolished Shed 2. During inspection, no discrepancy was observed with retrofitting drawing and onsite remediation work. Factory has installed 22 mm cable bracings as per accepted drawing. On 12-Mar-2026: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 13 | New finding-2: Newly constructed structure Lack of desgin documents. (Finishing shed)(Shed 06) | The building engineer is required to prepare a set of design report with a set of structural drawing in compliance with section 1.9.1.1 and section 1.9.1.2 (part 6, BNBC). |  | May 2 2024 | On 12-Mar-2024: During inspection, a newly constructed structure was found in the premises named Finishing shed (Shed 06). At the time of inspection, no design documents were available. Building engineer is required to prepare a set of design documents in compliance with BNBC and submit to RSC. Implement remedial measure after getting acceptance from RSC (if any). On 21-Oct-2024: Factory has submitted the design documents of Finishing shed (Shed 06) to RSC on 31st August 2024 which is currently under review. On 12-Mar-2026: The EA of Shed-6 was accepted by RSC dated 13-January-2026. During the inspection, as-built drawing was found satisfactory with the site condition. Retrofitting works are just started (15% retrofitting progress). The factory is required to complete the retrofitting works within the extended timeline 30-April-2026. Progress Status: 65%. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 14 | New finding-3: Newly constructed ancilery structures. Lack of as-built drwaing (2 nos canopy, undocumented extended shed beside shed 1, apparently non engineered watch tower, Single storied security and fire pump room. (RCC)) | The building engineer is required to prepare as-built drawing. | Corrected | May 2 2024 | On 12-Mar-2024: During inspection, newly constructed several ancillary structures were found in the premises. At the time of inspection, no as built drawing was found onsite. Building engineer is required to prepare a set of as built drawing and submit to RSC. On 21-Oct-2024: Factory demolished the extended shed beside shed 1, watch tower and submitted prepared as-built drawings of 2 nos canopy, Single storied security and fire pump room to RSC on 31st August 2024 which is currently under review. During inspection, mismatch was observed between as-built drawings and onsite condition which will be addressed in the next review comment. During inspection, a newly constructed single storied steel stair was found adjacent to Shed-1. Factory needs to prepare as-built drawings for this structure and submit with the next EA submission. On 12-Mar-2026: The EA of Canopy-1 & Canopy-2, along with the as-built drawings of the Security & Fire Pump Room and Steel Stair, was accepted by RSC on 13 January 2026. During the inspection, the as-built drawings were generally found to be consistent with the site conditions, except for Canopy-1 and the Steel Stair. For the Steel Stair, a mismatch was observed in the steel beam and stringer section sizes. Additionally, for Canopy-1, discrepancies were noted in the grid distance and the position of one cantilever truss. However, the assessment was subsequently reviewed considering these mismatches and was found to be satisfactory. The factory is required to keep the updated drawings available on-site. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 15 | New finding-4: Newly constructed ancilery structures. Lack of as-built drwaing (2 nos canopy, undocumented extended shed beside shed 1 & apparently non engineered watch tower) | Building engineer is required to check the member adequicy and uplift capacity of the connections for uplift forces. | Corrected | May 2 2024 | On 12-Mar-2024: During inspection, newly constructed several ancillary structures were found in the premises. At the time of inspection, no design documents were found onsite. The building engineer is required to check the member and connection adequacy of these structures for lateral forces. On 21-Oct-2024: Factory submitted the member adequacy check of 2 nos canopy to RSC on 31st August 2024 which is currently under review. After the acceptance, factory needs to complete the remediation works if required. On 12-Mar-2026: The EA of Canopy-1 and Canopy-2 were accepted by RSC dated 13-January-2026. The factory has completed the retrofitting works for both shed which are found satisfactory as per the accepted drawings. Retrofitting completion certificate was available. The factory has demolished the extended shed beside Shed-1 and Watch Tower. | (within 6 weeks) | Corrected

## Fire
Date
29-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Refat Garments Ltd - Extension (Previously THAT'S IT Sweater Ltd)., 119 – 145 Narshinghapur, Ashulia, Savar, , Narshinghapur, Dhaka, Dhaka
Date of Inspection |  | 2015-03-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Collapsible gates, steel rolling shutter, and steel sliding doors are installed in some of the exits in the means of egress. | All steel sliding door, steel rolling shutter and collapsible gates in the means of egress shall be replaced with required fire rated side-hinged swinging self-closing type doors that swing in the direction of egress per Alliance Standard Section 6.8. Doors shall be free from general locking arrangements. | Corrected | Jul 18 2015 | On 26/11/2015: Corrected. Factory have installed side hinged swing doors. On 30/03/2016: Corrected. On 13/03/2017: Corrected. Non-compliant gate has not been observed during follow-up inspection. On 19/06/2017: Corrected. Non-compliant gate has not been observed during follow-up inspection. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. Not found during inspection. | Jul 18 2015 | Corrected
Initial Inspection |  | 2 | Doors in the path of egress are unlocked in the direction of egress only in working hour. Hasps, locks, other locking devices are provided on the doors. | Keep the doors unlocked in the direction of egress under all conditions. All hasps, locks, slide bolts and other locking devices shall be removed as required. | Corrected | Jul 18 2015 | On 26/11/2015: Corrected. On 30/03/2016: Corrected. On 13/03/2017: Corrected. Non-compliant locking feature has been removed. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 9 2015 | Corrected
Initial Inspection |  | 3 | Unprotected openings were observed in the separation wall between the winding section and the yarn bond store. | Provide required fire resistance rated opening protection (Door, Window, Hatch Cover etc.) at openings and penetrations through fire rated assemblies or close the unprotected openings with fire-resistance rated barrier as per requirements. Consult a qualified fire protection engineer to design the required rated opening protection. | Corrected | Mar 30 2016 | On 26/11/2015: Partially corrected. Some unprotected exhaust fans are found in the egress route (which are less than10 feet) beside sheds. On 30/03/2016: Civil work has been going. On 13/03/2017: Still few unprotected openings have been found in the egress routes. On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 30/03/2016. On 19/06/2017: Work is going on. On 07/03/2018: Corrected On 30/09/2018: Not found. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Issue has been reopen. See SL No 22 | Jul 18 2015 | Corrected
Initial Inspection |  | 4 | Pull stations at egress points: Manual fire alarms are installed. Push switches are used as fire alarm call points. Smoke detectors: Only standalone smoke alarms are installed in the building. Audible and Visual devices: Audible and visual devices are provided. | Install initiating devices and notification appliances as required by the Alliance Standard and NFPA 72. This includes electrical supervision of all valves controlling fire protection systems (sprinklers, fire pumps, water supplies, etc.). Connect devices to an automatic fire alarm and detection system for the facility. All fire alarm installations shall be submitted for review by the Alliance prior to commencement of installation. | Corrected | Jun 7 2016 | On 13/03/2017: Partially corrected. Installation was almost completed. Factory could not provide any third party certification for installed fire alarm cable during follow-up inspection. On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work. On 19/06/2017: The factory has installed non-listed fire alarm cable. Single station smoke detectors have been found in few places. On 07/03/2018: Awaiting T&Cx. On 30/09/2018: In Progress. Alarm cable replacement is going on. On 31/03/2019: (Not Limited To): Cable in and out of FACP shall be protected from damage. On initiation of fire alarm, it was observed that the sound level for fire alarm is inadequate considering the working noise of production areas (Jacquard section) and others. Cable used for interfacing the auxiliary power extender with control panel shall be 3rd party certified. Detection devices were zip tied to the purlin (store shed). Device shall be provided as per NFPA 72. As built drawing shall be updated providing section view of shed. On 25/09/2019: Installation complete, after resolving the cable credibility issue factory shall re-apply for Pre-T&C. On 13/10/2020: Corrected. On 23/08/2023: Refer issue no. 23. | Jul 18 2015 | Corrected
Initial Inspection |  | 5 | 40 workers have been trained from Fire Service and Civil Defence and 40 workers have been trained from BGMEA out of 649 workers. | Provide training for the required number of people (25% of total workers) certified in firefighting, first aid, and rescue training by the appropriate authority. | Corrected | Feb 23 2016 | On 26/11/2015: In progress. Total manpower= 900 persons approximately. 25% of them should be trained as per recommendation. On 30/03/2016: Partially corrected. 200 person has been trained. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | Oct 10 2015 | Corrected
Initial Inspection |  | 6 | Only standalone smoke alarms are installed but the number of detectors is insufficient. No central station monitoring service is available. | Install an automatic fire detection and alarm system throughout the factory. Until that time a central station monitoring service or direct connection to the Fire Service and Civil Defence can be set up; a person shall to be assigned to contact the fire department in the event of fire alarm activation. An annunciator shall be located in a constantly attended location to alert this person. Trouble or alarm notifications shall be indicated on the fire alarm control panel. | Corrected | Jun 7 2016 | On 30/03/2016: Installation work of fire alarm system has been almost done. Factory management has confirmed installation shall be completed within committed timeline. On 13/03/2017: It is an integrated part of fire alarm system. On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work. On 19/06/2017: It is an integrated part of fire alarm system. On 07/03/2018: Awaiting T&Cx On 30/09/2018: It is an integrated part of fire alarm system. On 31/03/2019: See item no 4. On 25/09/2019: It is an integrated part of fire alarm system. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 23 2015 | Corrected
Initial Inspection |  | 7 | An emergency evacuation plan has not been developed and communicated to all employees. | Develop and execute an emergency evacuation plan which includes all necessary components required by the Alliance Standards. Provide sufficient communication and training to all employees. | Corrected | Apr 10 2016 | On 26/11/2015: In progress. On 30/03/2016: In progress. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 23 2015 | Corrected
Initial Inspection |  | 8 | Emergency egress maps are posted at the entrances to exits or main points of egress but not at all the exits. | Post emergency egress maps at the entrances to each exit or main point of egress. | Corrected | Jun 18 2015 | On 26/11/2015: Corrected. On 30/03/2016: Corrected. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 23 2015 | Corrected
Initial Inspection |  | 9 | No testing plan and records were provided during this inspection. | Develop a testing and maintenance program that ensures the emergency power for exit signs is tested at least once per year. If battery operated signs are used, these lights are tested on a monthly basis. Functional testing of battery powered signs is provided for a minimum 90 min once per year. | Corrected | Dec 15 2015 | On 26/11/2015: In progress. On 30/03/2016: Corrected. On 13/03/2017: Corrected. The factory is maintaining a checklist as per standard. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 23 2015 | Corrected
Initial Inspection |  | 10 | Only the inspection checklists with the monthly dates on each extinguisher were being verified. Not all of the requirements of NFPA 10 are being met. While interviewing the person responsible for this, it was found that only the pressure gauges (where available) and expiration dates are being checked. | Establish an inspection, testing and maintenance program for all fire extinguishers. Program must comply with the requirements of NFPA 10. | Corrected | Dec 15 2015 | On 26/11/2015: In progress. On 30/03/2016: Corrected. On 13/03/2017: Corrected. The factory is maintaining a checklist as per standard. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | Oct 10 2015 | Corrected
Initial Inspection |  | 11 | No testing plan and records were provided during this inspection. | Develop a testing and maintenance program that ensures the operation of all means of egress lights are verified at least once per year. If battery-operated lights are used, these lights shall be tested on a monthly basis. Functional testing of battery powered lights shall be provided for a minimum 90 min once per year. | Corrected | Dec 15 2015 | On 26/11/2015: In progress. On 30/03/2016: Corrected. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 23 2015 | Corrected
Initial Inspection |  | 12 | Occupant loads are not posted for any assembly or the production floor in a conspicuous space near the main point of egress. | Post the occupant load for every assembly and production floor in a conspicuous space near the main exit or exit access doorway for the space. | Corrected | Jun 18 2015 | On 26/11/2015: Corrected. On 30/03/2016: Corrected. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 9 2015 | Corrected
Initial Inspection |  | 13 | The illumination levels and contrasting graphics of exit signs were observed to not be in compliance with Alliance standard. | Provide illumination and contrast per Alliance standards. Exit signs may be illuminated either by lamps external to the sign or by lamps contained within the sign. The source of illumination shall provide not less than 50 lux at the illuminated surface with a contrast of not less than 0.5. Approved self‐luminous signs which provide evenly illuminated letters having a minimum luminance of 0.2cd/m2 may also be used. | Corrected | Jun 18 2015 | On 26/11/2015: Corrected. On 30/03/2016: Corrected. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | Oct 10 2015 | Corrected
Initial Inspection |  | 14 | Fire license: Valid up to 30 June 2015; Trade license: Valid up to 30 June 2015; Industry license: Valid up to 31 December 2015; Boiler license: One boiler, validity expired on 10 Feb 2015, also applied for renewal on 02 Feb 2015; BERC license: Valid up to 24 Jan 2016, Capacity of generators were 4.12 MW. | Collect all applicable permits and licenses and keep them up to date including boiler license. | Corrected | Dec 12 2015 | On 26/11/2015: Partially corrected. Boiler & generator license renewal are not done. Factory have applied for that. On 30/03/2016: Corrected. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 23 2015 | Corrected
Initial Inspection |  | 15 | Occupancy certificate for buildings were not provided during this inspection. | Apply to appropriate authority in an expeditious manner for issuance of a Certificate of Occupancy for each building and ancillary structure according to each building use. | Corrected | Feb 26 2017 | On 26/11/2015: In progress. On 30/03/2016: In progress. On 13/03/2017: Not applicable. On 19/06/2017: Not applicable. On 07/03/2018: N/A On 30/09/2018: N/A On 31/03/2019: N/A. On 25/09/2019: N/A. On 13/10/2020: Corrected. On 23/08/2023: Not Applicable. | Jun 6 2015 | Corrected
Initial Inspection |  | 16 | Fire Department pre-planning has not been completed. | Complete fire department pre-planning activities with the local Fire Service and Civil Defence. | Corrected | May 25 2016 | On 26/11/2015: In progress. Factory have applied to Fire Service & Civil Defence for it. On 30/03/2016: In progress. On 13/03/2017: Corrected. Completed. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | May 23 2015 | Corrected
Initial Inspection |  | 17 | A written housekeeping policy is not established or enforced. | Establish written corporate and plant policies on housekeeping to ensure scheduled cleaning for floor, wall, ceiling, supply and return air ventilation systems. Promptly reschedule skipped cleanings. Provide a documented line of authority for authorizing a cleaning delay and rescheduling. | Corrected | Jan 2 2015 | On 26/11/2015: Corrected. On 30/03/2016: Corrected. On 13/03/2017: Corrected. On 19/06/2017: Corrected. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | Jan 2 2016 | Corrected
Follow Up Inspection |  | 18 | New finding (2nd followup): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | May 30 2016 | On 30/03/2016: New Finding On 13/03/2017: Adequate illumination for emergency lighting system has not been observed during follow-up inspection. On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work 30/05/2016. On 19/06/2017: It was found same as last (3rd) follow-up. On 07/03/2018: Corrected On 30/09/2018: Corrected as per previous follow up. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 19 | New finding (2nd followup): The width of egress aisles is less | Provide minimum aisle widths of 36-in. | Corrected | May 30 2016 | On 30/03/2016: New Finding On 13/03/2017: Not corrected yet. On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work 30/05/2016. On 19/06/2017: Not corrected yet. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 20 | New Finding (3rd Follow up): Inspection, testing, and maintenance for the fire alarm system is not in accordance with NFPA 72 or as per Accord standard. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72 or as per Accord standard. | Corrected | Apr 13 2017 | On 13/03/2017: New Finding On 13/06/2017: Factory sent a CAP where they have mentioned that they have completed the work 15/04/2017. On 19/06/2017: Corrected. The factory is maintaining a checklist as per standard for the existing system. On 07/03/2018: Corrected On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected, shall follow table 14.3.1 of NFPA-72. On 13/10/2020: Corrected. On 23/08/2023: Corrected as per previous follow-up. However, It is an integrated part of fire alarm system. | Within 1 month | Corrected
Follow Up Inspection |  | 21 | New Finding (3rd Follow up): Areas used for combustible storage are not separated by firerated construction. | Provide dedicated storage rooms separated by minimum 1- hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows:- Maximum height of 2.4m and maximum area of 23m2- If sprinkler protected: maximum height of 3.66m and maximum area of 93m2Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Apr 3 2017 | On 13/03/2017: New Finding On 13/06/2017: Factory sent a CAP where they have mentioned that they have completed the work 15/04/2017. On 19/06/2017: No action has been taken yet. On 07/03/2018: Corrected. Maintained as per standard. On 30/09/2018: Corrected. On 31/03/2019: Corrected. On 25/09/2019: Corrected. On 13/10/2020: Corrected. On 23/08/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 22 | New Finding (9th Follow up): Unprotected openings were observed in the separation wall between the IT Room and the store. | Provide required fire resistance rated opening protection (Door, Window, Hatch Cover etc.) at openings and penetrations through fire rated assemblies or close the unprotected openings with fire-resistance rated barrier as per requirements. Consult a qualified fire protection engineer to design the required rated opening protection. | Corrected | Nov 13 2020 | On 13/10/2020: NF On 23/08/2023: Corrected. During follow-up inspection it was observed that the factory has removed IT room from the shed-1 and retrofitting work was ongoing in the shed-1, 3 & 4. | Within 1 month | Corrected
Follow Up Inspection |  | 23 | New Finding (On 23/08/2023): During follow up inspection it was observed the factory has replaced previous approved fire alarm system (HOCHIKI) and installed same brand new fire alarm system in the factory shed building-5. The factory has dismantaled approved fire alarm system from the shed-1, 3 & 4 due to retrofitting work. Fire alarm and detection system (FADS) installation requires to detailed review to confirm compliance with NFPA 72 and RSC standard. | Submit drawings, testing records, equipment certification and other relevant documentation to the RSC for review and approval. | Corrected.. T&C document of FADS had already been prepared and the document was submitted to RSC on 26-Jan-26 for RSC review. Pictorial evidence of submission is attached separately. | Nov 23 2023 | On 23/08/2023: New Finding Note: During follow-up inspection it was observed that retrofitting work was ongoing in the shed-1, 3 & 4 and the factory has demolished shed-2. Production is running only in shed-5. RPO Comments on 01 Mar 2026- The design documents have been reviewed by RSC on 27 Apr 2025. The factory submitted the T&CVI documents on 26 Feb 2026 which are under RSC review. | Design submission (Within 1 month), Modification within 2 months (if required) | In Progress
Follow Up Inspection |  | 24 | New Finding (On 23/08/2023): Rooms used for combustible storage are not separated by fire rated construction in shed-5. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected. Storage room for combustible storage had already been separated by minimum 1-hr fire rated construction. Pictorial Evidence of correction is attached separately. | Sep 23 2023 | On 23/08/2023: New Finding RPO Comments on 09 Nov 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification

## Electrical
Date
29-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Refat Garments Ltd - Extension (Previously THAT'S IT Sweater Ltd)., 119 – 145 Narshinghapur, Ashulia, Savar, , Narshinghapur, Dhaka, Dhaka
Date of Inspection |  | 2015-03-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | A lightning protection system has not been installed. The calculated risk index for this facility is 43, where for the requirement of lightning protection system, marginal risk index is 40. | Have a qualified electrical engineer design a lightning protection system according to the BNBC requirements. Have a licensed electrician install the designed system. | Corrected | Dec 20 2015 | On 26/11/2015: Not Corrected. On 30/03/2016: All of LPS drawing for 5 Sheds are approved by Alliance, installation is pending. New committed timeline is given till 30/05/2016. On 13/03/2017: Corrected. | Jul 8 2015 | Corrected
Initial Inspection |  | 2 | Earthing busbar without earthing connection to equipment was found in SDB-02 and SDB-06. Also, earthing cable was found undersized in LT Panel and multiple distribution boards. | Provide earthing of equipment at required locations and connect to required number of electrodes. | Corrected | Dec 30 2015 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 3 | Single Line Diagram was available but electrical layout drawing was not found. | Have a qualified electrical engineer develop an as-built single line diagram and electrical layout drawings detailing key components and capacity of the electrical system. | Corrected | Oct 31 2015 | Corrected on 2nd follow up. | Jun 10 2015 | Corrected
Initial Inspection |  | 4 | Adequate space was not available behind LT Panel in Substation Room. | Provide a minimum of 1 m clearance on required sides of electrical panels to ensure ease of maintenance work. | Corrected | Apr 25 2016 | On 26/11/2015 Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 5 | SDB-01 in Washing Section was found within 2.5 m of the washing machine. | Relocate the panel to a safe location so that the panel is not in risk of being affected by water. | Corrected | Jul 31 2015 | Washing section has relocated from this location Corrected on 2nd follow up. | Jun 10 2015 | Corrected
Initial Inspection |  | 6 | During thermographic scan, some hotspots were observed at multiple locations. Refer to Thermographic Survey Report for detailed information. | Suggested plan for specific issues have been incorporated in the Thermographic Survey Report. | Corrected | Jul 31 2015 | On 26/11/2015: Not Corrected. On 30/03/2016: This is not corrected yet. New committed timeline is given till 15/05/2016. On 13/03/2017: Not Corrected. On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 15/03/2016. On 19/06/2017: Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 7 | Part of the cable trench was found uncovered in Substation Room. Also, cable trench was covered using a metal grill. | Provide metal cover throughout the length of cable trench. Use solid checkered plate instead of metal grill. | Corrected | Jul 31 2015 | On 26/11/2015 Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 8 | Components of the emergency power system do not have proper identification. | All boxes and enclosures (including transfer switches, generators, and power panels) for emergency circuits shall be permanently marked so they will be readily identified as a component of an emergency circuit or system. The required marking can be by color code, the words “emergency system,” or any other method that identifies the box or enclosure as a component of the emergency system. | Corrected | May 31 2015 | On 26/11/2015 Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 9 | All metal parts have not been connected to the building earthing system. | Provide an earthing connection to all exposed-conductive parts (metal) related to/in close proximity to electrical equipment/installation and utility service such as metallic water/gas/steam pipes etc. such that all the metals remain at a substantially same potential of building earthing system. | Corrected | Jan 5 2016 | This issue is not done yet. New committed timeline is given till 30-01-16 to close the issue. Corrected on 2nd follow up. | Jun 10 2015 | Corrected
Initial Inspection |  | 10 | A wooden table was found inside the substation room. | Remove all combustible materials and other unnecessary materials from substation room. | Corrected | Oct 31 2015 | On 26/11/2015 Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 11 | Neutral cables do not have identification, so it cannot be determined whether all circuits have dedicated neutrals. | Provide individual neutral connection for each circuit. Also, provide identification/ tagging for each circuit using approved means. | Corrected | Feb 20 2016 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 12 | No identification was provided for electrical wiring/cables. Also, color code was not maintained. For example, cables without identification and color coding were found in SDB-14. | Provide identification/tagging mentioning the equipment/machines name (i.e. Sewing Machine Line-1 or Lighting Line-2) and type of conductor (i.e. L1, L2, L3, N, PE) for every cable at its termination point, or maintain the color-coded at its termination point (providing colored cable-sleeves) for identification of conductor-type (i.e. Red/Yellow/Blue for phase cable, Black for neutral cable, Green for earthing cable). (Labelling-cable-tie/Marker-tie can be used for cable identification). | Corrected | Mar 31 2016 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 13 | No record of previous thermographic scan was found. | Complete thermographic scans at least on a three year cycle. Thermographic scans should be completed in accordance with the Standard for Infrared Inspection of Electrical Systems & Rotating Equipment and NFPA70B or a comparable standard. | Corrected | Apr 30 2016 | This issue is not done yet. New committed timeline is given till 30-12-15 to close the issue Corrected on 2nd follow up. | May 6 2015 | Corrected
Initial Inspection |  | 14 | Some distribution boards have space in DIN-rail channel to install additional over-current devices. | Calculate and display the information of the capacity & panel-schedule of the distribution boards, and then provide a physical means to prevent the installation of additional circuit breakers. | Corrected | Apr 25 2017 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 15 | Transformer neutral grounding and body grounding were not separated. LT Panel earthing was also connected to this earth terminal (MET). | Provide separate grounding of transformer neutral and body earthing using separate earth terminals. Also separate LT Panel earthing from transformer neutral grounding. | Corrected | Apr 25 2017 | On 26/11/2015 Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 16 | Improperly stored materials were found inside the substation room. | Remove all unnecessary materials from the substation room and keep the room clean. | Corrected | Apr 25 2017 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 17 | Substation room did not have adequate ventilation. No exhaust fan was provided for the substation room. | Provide means of ventilation for the substation room. Consult a qualified electrical engineer to determine the required ventilation rates based on the installed equipment. | Corrected | Apr 25 2017 | This issue is not done yet. New committed timeline is given till 30-01-16 to close the issue. Corrected on 2nd follow up. | Jun 10 2015 | Corrected
Initial Inspection |  | 18 | Plastic sheet over busbar was found tied to a cable connected to the busbar in SDB-14. | The plastic cover shall be supported from the panel enclosure to avert additional strain on the cable. | Corrected | Dec 30 2015 | This issue is not done yet. New committed timeline is given till 30-12-15 to close the issue. Corrected on 2nd follow up. | May 20 2015 | Corrected
Initial Inspection |  | 19 | Multiple cables are terminated to same point of MCCB using a single lug. Also, empty cable sockets connected to busbar were found in some panels. | Use cables of appropriate size with proper cable lugs to terminate cables. Put lug on cable using appropriate lug puncher. Remove unnecessary cable sockets from busbar. | Corrected | Dec 20 2015 | On 26/11/2015 Corrected. | May 19 2015 | Corrected
Initial Inspection |  | 20 | Cables inside some of the distribution boards were kept haphazardly. For example, cables inside SDB-14 were not properly arranged. | Arrange the cables inside all panels properly by installing PVC wiring-duct (slotted) so that the cables can be supported and latched inside the duct. | Corrected | Dec 30 2015 | This issue is not done yet. New committed timeline is given till 30-12-15 to close the issue. Corrected on 2nd follow up. | May 20 2015 | Corrected
Initial Inspection |  | 21 | Cable socket without cable was found in some distribution boards. For example, such cable socket was found in SDB-10. | Remove unnecessary cable sockets from busbar. | Corrected | Oct 31 2015 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 22 | No light fixture was provided in room for Iron Section SDB. | Provide light fixture in all required areas using approved means. | Corrected | Apr 25 2016 | Factory has been fixed LED Light. Corrected on 2nd follow up. | May 6 2015 | Corrected
Initial Inspection |  | 23 | Some dust was found inside SDB-01 in Washing Section and Iron Section-SDB. | Disconnect the panel from the electrical service and clean interior components of all dust and debris. Seal all openings within the enclosure to prevent dust and debris from entering. | Corrected | Jul 31 2015 | On 26/11/2015 Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 24 | Electrical panels in substation room do not have base plates. Also, cable entry holes were found open in some distribution boards, i.e. SDB-12, SDB-13. | Make a circular hole at the base plate of panels and provide a cable gland according to the respective cable size for cable entry and exit, so that the cables are not stressed on the sharp edges of the hole in panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands. | Corrected | Jul 31 2015 | On 26/11/2015 Corrected. | May 6 2015 | Corrected
Initial Inspection |  | 25 | Some of the electrical panels do not have a separate door earthing connection. For example, door earthing was not provided in SDB-01. | Check all the doors for an earthing connection and provide an earthing connection to the panel enclosure as per BNBC Table 8.2.11. Provide earthing connection to doors of metallic distribution boards using green cables (preferably braided) so that the metallic door remains at zero potential all the time. | Corrected | Jul 31 2015 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 26 | A capacity information label has been provided, but for some panels the number of MCBs in the capacity information label does not match the number of MCBs inside the panel. | Provide a capacity information label which contains the current carrying capacity and size of main cable, rated capacity of circuit breaker, the busbar (with dimension) and the number of circuit breakers. | Corrected | May 31 2015 | On 26/11/2015 Corrected. | May 20 2015 | Corrected
Initial Inspection |  | 27 | Documents regarding inspection, maintenance and testing of IPS were not found. | Establish an inspection testing, and maintenance program for the Uninterruptable Power Supply (UPS) and associated components. The program must based on the following: (1) Manufacturer's recommendations (2) Manufacturer's instruction manuals (3) Minimum Requirements of NFPA 111 Chapter 8 (4) Minimum Requirements of NFPA 70B Chapter 28. | Corrected | Jan 5 2016 | On 26/11/2015 Corrected. | Jun 10 2015 | Corrected
Initial Inspection |  | 28 | Meters and indicator lamps were not working properly in some distribution boards. For example, voltmeter and ammeter were not working in SDB-14 and ammeter was not working in SDB-15. | Replace/repair faulty lamps and meters where necessary and provide connection to indicator lamps through protective device (fuse box). | Corrected | Oct 31 2015 | On 26/11/2015 Corrected. | May 20 2015 | Corrected
Follow Up Inspection |  | 29 | New Finding: New Issue(1st Follow-up): Light in store room /storage areas is uncovered. | Light in store room /storage areas shall be covered. | Corrected | Feb 20 2016 | Corrected on 2nd follow up. | 3 Months | Corrected
Follow Up Inspection |  | 30 | New Finding: New Issue(1st Follow-up): Transformer Arcing horn has not installed. | Install transformer arcing horn with proper alignment(maintain not less than 2 inch gap between two horns). | Corrected | Mar 31 2016 | Corrected on 2nd follow up. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: New Issue(2nd Follow-up): Cable duct is filled with fluffs (Lint/dust) and left open. | Cover it with electrical graded materials, clean it at certain interval and keep records of cleaning. | Corrected | Apr 30 2016 | On 13/03/2017: Not Corrected. On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 30/04/2016. On 19/06/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 32 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Corrected | Apr 25 2017 | On 11/06/2017: Factory sent a CAP where they are asking for 30/07/2017 which is not accepted. Hence corrective action plan shall have to be completed within 25/04/2017. On 19/06/2017: Not Corrected. On 07/03/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Periodicity of Thermography survey is not continued. | Thermography survey must be done and recorded at least twice in a year. | Corrected | Apr 25 2017 | On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 30/04/2017. On 19/06/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Corrected | Apr 25 2017 | On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 30/04/2017. On 19/06/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Apr 25 2017 | On 11/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 30/04/2017. On 19/06/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Corrected | Jun 30 2019 | On 25/09/2019: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Earth pit test did not cover all pits. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Corrected | Apr 30 2019 | On 25/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Interlocking scheme is unable to prevent accidental coupling of unsynchronized active sources. | Interlocking scheme must be capable of preventing accidental coupling of unsynchronized active sources. | Corrected | May 31 2019 | On 25/09/2019: Not corrected. On 13/10/2020: Not Corrected. Breaker locking is done which is not interlocking. On 23/08/2023: Not Corrected. Factory has designed interlocking arrangement in SLD which is accepted. They will implement it soon. On 12-Mar-2024: Corrected as per satisfactory pictorial evidence provided by factory. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | May 31 2019 | On 25/09/2019: Not corrected. On 13/10/2020: Not Corrected. On 23/08/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Oct 31 2019 | On 13/10/2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected | Oct 31 2019 | On 13/10/2020: Not Corrected. On 23/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Earth Pit resistance record is incomplete.(Not done for all pits). | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Corrected | Nov 20 2020 | On 23/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all required information by qualified engineer and get it reviewed by Accord. It shall be an as-built drawing (if currently modified) in the factory. | Corrected. As-built electrical SLD had already been updated and updated SLD was submitted to RSC on 24-Feb-26 for RSC review. Pictorial evidence of SLD submission is attached separately. | Dec 20 2020 | On 23/08/2023: Not Corrected. SLD found accepted but cables are not identified at LT panel. On 12-Mar-2024: Significant changes are observed from the accepted SLD due to newly constructed shed (Finishing shed), changes of cabling system from channel to BBT and changes of production layout in the shed-1, 3 and 4. Re-submission of as-built SLD is required for further acceptance. On 07/08/2025: Not corrected. The SLD had been accepted and field implementation started. However, discrepancies were observed in the current condition, including mismatches in breaker adjustments and the earthing system. Additionally, a few consumer boxes needed to be included in the SLD. Approximately 40% progress observed. RPO Comments on 01 Mar 2026- The design document reviewed and accepted on 08 Sep 2024. The factory has completed the implementation or installation work as per accepted design and last inspection comments. On 24 Feb 2026, the factory submitted the As-Built SLD documents which are under RSC review. | 2 Months | In Progress
Follow Up Inspection |  | 44 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Corrected | Nov 20 2020 | On 23/08/2023: Corrected. Breakers found adjusted. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Transformer Breather oil cup is empty. | Fill the transformer breather oil cup by transformer oil. | Corrected | Nov 20 2020 | On 23/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | Corrected | Nov 20 2020 | On 23/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Circuit breaker rating is not identifiable. | Replace the old breaker with a new one so that anyone can know the ampacity of the breaker. | Corrected | Nov 20 2020 | On 23/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. | Corrected | May 31 2024 | On 07/08/2025: Corrected. The factory installed LPS on all structures. | 2 Months | Corrected