## Structural
Date
07-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Alif Industries Ltd. (Previously Alif Casual Wear Ltd), 69, Vogra, Gazipur Sadar, Gazipur., Gazipur, Dhaka
Date of Inspection |  | 2015-03-21
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | N/W cantilevered slabs not shown on Structural Drawings resulting in high stresses in Columns (I1 and I2) and supporting suspended slabs | Factory Engineer to reduce Live Load to 1kPa in area X specified on next page | Done | Jul 6 2016 | On 02-Sep-2016: They removed load from marked area. On 20-Nov-2016: Found Corrected in previous follow-up inspection. Loading was observed below 1 kpa in mentioned area. On 12-july-2017: Corrected in the previous follow up report. Load was found under acceptable limit. On 11-02-2018 :Corrected in previous follow-up inspection . During inspection no heavy loading was found . On 18th September 2018: Corrected from previous follow-up. Factory DEA has been accepted. During inspection, load was found below acceptable limit( 42 psf). On 24th April 2019: Found corrected from previous follow up inspection. During inspection, floor load was found below allowable limit (42 psf) of load plan. On 13-Jan-2020: Corrected in previous follow up inspection. During inspection load plan was found posted to each floor and overall loading was found below the allowable accepted loading plan (42 psf). On 09-Dec-2020: This issue was corrected from previous inspection. During inspection, floor load was found below allowable limit (42 psf) of load plan. On 02-Nov-2021: Floor loading was found below the allowable limit (42psf). Issue was found corrected from previous follow up inspection. On 13-Mar-2022: Corrected from previous inspection. During inspection live load was found below the allowable limit (42 psf). On 19-Jun-2023: Corrected from previous inspection. During inspection floor live load was found below the allowable limit (42 psf). On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. During inspection floor loading was found below the allowable limit (42 psf). | Immediately | Corrected
Initial Inspection |  | 2 | N/W cantilevered slabs not shown on Structural Drawings resulting in high stresses in Columns (I1 and I2) and supporting suspended slabs | Detailed Engineering Assessment (DEA) to be commenced | It has Reviewed | Jul 6 2016 | On 02-Sep-2016: They did DEA before initial inspection but it is not as per Accord standard. Therefore they will revise the DEA and submit. On 20-Nov-2016: Factory have conducted DEA and DEA report got acceptance from Accord on 06-June-2016. DEA verification inspection conducted by Accord team and found some inconsistence in DEA. A DEA Verification report was sent to factory. Factory requires to submit the revised DEA report within given timeline in DEA verification report. On 12-july-2017: Revised DEA of this factory has been prepared and submitted to Accord for review and factory got re acceptance from Accord On 11-02-2018 :Corrected in previous follow-up inspection .DEA has been accepted by Accord On 18th September 2018: Corrected from previous follow-up. On 24 April 2019: Found corrected from previous follow up inspection. DEA documents of the factory were accepted by Accord. On 13-Jan-2020: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from Accord on 11-June-2017. On 09-Dec-2020: This issue was corrected from previous inspection. Factory management got DEA re-acceptance from Accord on 11-June-2017. On 02-Nov-2021: Factory management got DEA re-acceptance from Accord on 11-June-2017. Issue was found corrected from previous follow up inspection. On 13-Mar-2022: Corrected from previous inspection. Factory got DEA re-acceptance from Accord on 11th June 2017. On 19-Jun-2023: Corrected from previous inspection. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | Immediately | Corrected
Initial Inspection |  | 3 | N/W cantilevered slabs not shown on Structural Drawings resulting in high stresses in Columns (I1 and I2) and supporting suspended slabs | Factory Engineer to arrange for Structural Consultant to verify insitu concrete stresses either by 100mm dia. cores for 1I and 2I Columns or 100mm dia. cores from 4 columns or alternate size as specified in ACI 562 | Done | Jul 6 2016 | On 02-Sep-2016: Core test done before initial inspection. So we couldn't verify core cutting location but they showed us core test report. On 20-Nov-2016: Found corrected in previous follow up inspection. However some inconsistence found, which has described in CAP Item no 10. On 12-july-2017:Corrected in the previous follow up report. On 11-02-2018 :Corrected in previous follow-up inspection .Core test was done as a part of DEA .DEA was accepted by Accord . On 18th September 2018: Corrected from previous follow-up. On 24th April 2019: Core was taken as a part of concrete strength evaluation and core test location was verified in previous inspection. The issue is corrected as per previous inspection On 13-Jan-2020: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from Accord on 11-June-2017. Core test had been done as a part of DEA. During inspection original core test reports were found onsite. On 09-Dec-2020: This issue was corrected from previous inspection. On 02-Nov-2021: Cores were taken as a part of DEA. Factory management got DEA re-acceptance from Accord on 11-June-2017. Issue remains corrected. On 13-Mar-2022: Corrected from previous inspection. Cores were taken and covered in DEA. On 19-Jun-2023: Corrected from previous inspection. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 4 | N/W cantilevered slabs not shown on Structural Drawings resulting in high stresses in Columns (I1 and I2) and supporting suspended slabs | Factory Engineer to arrange for Structural Consultant to develop as- build drawings for cantilevered slabs at all suspended floor levels and carry out analysis/design to verify structural adequacy | It has Reviewed | Jul 6 2016 | On 02-Sep-2016: Will cover in DEA report. On 20-Nov-2016: Factory have conducted DEA and DEA report got acceptance from Accord on 06-June-2016. DEA verification inspection conducted by Accord team and found some inconsistence in DEA. A DEA Verification report was sent to factory. Factory requires to submit the revised DEA report within given timeline in DEA verification report. On 12-july-2017: This issue is covered under DEA. Revised DEA of this factory has been prepared and submitted to Accord for review and factory got re acceptance from Accord on 11 June, 2017. As per DEA recommendation remediation were required and remediation works must be completed within 6th July 2017. Till now factory did not take any step regarding remediation. On 11-02-2018 :This issue is covered in DEA .DEA has been accepted by Accord .Remedial works were completed . On 18th September 2018: Corrected from previous follow-up. On 24 April 2019: Found corrected from previous follow up inspection. This issue was covered in DEA report which was accepted by Accord. On 13-Jan-2020: Corrected in previous follow up inspection. As built drawings were found prepared as a part of DEA. Factory management got DEA re-acceptance from Accord on 11-June-2017. So this issue had been covered in DEA report. On 09-Dec-2020: This issue was corrected from previous inspection. On 02-Nov-2021: A set of as-built drawing has been prepared along with DEA. Factory management got DEA re-acceptance from Accord on 11-June-2017. Issue was found corrected from previous follow up inspection. On 13-Mar-2022: Corrected from previous inspection. As-built drawing had been produced as a part of DEA which had been re-accepted from Accord on 11th June 2017. On 19-Jun-2023: Corrected from previous inspection. As-built drawing had been produced as a part of DEA. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 5 | N/W cantilevered slabs not shown on Structural Drawings resulting in high stresses in Columns (I1 and I2) and supporting suspended slabs | DEA to be completed | It has Reviewed | Jul 6 2016 | On 02-Sep-2016: They did DEA before initial inspection but it is not as per Accord standard. Therefore they will revise the DEA and submit. On 20-Nov-2016: Factory have conducted DEA and DEA report got acceptance from Accord on 06-June-2016. DEA verification inspection conducted by Accord team and found some inconsistence in DEA. A DEA Verification report was sent to factory. Factory requires to submit the revised DEA report within given timeline in DEA verification report. On 12-july-2017: Revised DEA of this factory has been prepared and submitted to Accord for review and factory got re acceptance from Accord on 11 June, 2017. As per DEA recommendation remediation were required and remediation works must be completed within 6th July 2017. Till now factory did not take any step regarding remediation. On 11-02-2018 :DEA has been accepted by Accord .All remedial works were completed . On 18th September 2018: Corrected from previous follow-up. On 24 April 2019: Found corrected from previous follow up inspection. On 13-Jan-2020: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from Accord on 11-June-2017. As per DEA recommendation factory management had completed retrofitting works of column. On 09-Dec-2020: This issue was corrected from previous inspection. On 02-Nov-2021: Factory management got DEA re-acceptance from Accord on 11-June-2017. As per DEA recommendation factory management had completed retrofitting works of column. Issue was found corrected from previous follow up inspection. On 13-Mar-2022: Corrected from previous inspection. Factory got DEA re-acceptance from Accord on 11th June 2017. Also, factory had completed the retrofitting work as per accepted drawing. On 19-Jun-2023: Corrected from previous inspection. Factory had completed the retrofitting work as per DEA. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 6 | Apparently Non-Engineered structure on Roof | Factory Engineer to check design of existing non-engineered enclosure on Roof | Done | Jul 6 2016 | On 02-Sep-2016: Will cover in DEA report. On 20-Nov-2016: Factory have removed non engineered structure from roof. On 12-july-2017: Corrected in the previous follow up report. Non engineered structures have been removed . On 18th September 2018: Corrected from previous follow-up. On 24 April 2019: Found corrected from previous follow up inspection. Non engineered structure on roof had been demolished. On 13-Jan-2020: Corrected in previous follow up inspection. Factory management had demolished the non-engineered structure on roof top. On 09-Dec-2020: This issue was corrected from previous inspection. On 02-Nov-2021: Non-engineered structure has been demolished. Issue remains corrected. On 13-Mar-2022: Corrected from previous inspection. Factory had demolished the non engineered structures. On 19-Jun-2023: Corrected from previous inspection. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (within 6-weeks) | Corrected
Initial Inspection |  | 7 | Apparently Non-Engineered structure on Roof | As required by outcome of design check | Done | Jul 6 2016 | On 02-Sep-2016: Will cover in DEA report. On 20-Nov-2016: Factory have removed non engineered structure from roof. On 12-july-2017: Corrected in the previous follow up report. Non engineered structures have been removed . On 18th September 2018: Corrected from previous follow-up. On 24 April 2019: Found corrected from previous follow up inspection. Non engineered structure on roof had been demolished. On 13-Jan-2020: Corrected in previous follow up inspection. Factory management had demolished the non-engineered structure on roof top. On 09-Dec-2020: This issue was corrected from previous inspection. Non engineered structure on roof had been demolished. On 02-Nov-2021: Non-engineered structure has been demolished. Issue remains corrected. On 13-Mar-2022: Corrected from previous inspection. Factory had demolished the non engineered structures. On 19-Jun-2023: Corrected from previous inspection. Factory had demolished the non engineered structures. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 8 | Water tanks on Stair Roof | Factory Engineer to check design of existing Stair roof for Water tanks | Done | Jul 6 2016 | On 02-Sep-2016: Will cover in DEA report. On 20-Nov-2016: This issue is a part of DEA. Factory have conducted DEA and DEA report got acceptance from Accord on 06-June-2016. DEA verification inspection conducted by Accord team and found some inconsistence in DEA. A DEA Verification report was sent to factory. Factory requires to submit the revised DEA report within given timeline in DEA verification report. On 12-july-2017: This issue is covered under DEA. Revised DEA of this factory has been prepared and submitted to Accord for review and factory got re acceptance from Accord on 11 June, 2017. On 11-02-2018 :DEA has been re-accepted .Remedial works were completed . On 18th September 2018: Corrected from previous follow-up. On 24 April 2019: Corrected from previous follow up inspection. On 13-Jan-2020: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from Accord on 11-June-2017. So this issue had been covered in DEA report. On 09-Dec-2020: This issue was corrected from previous inspection. On 02-Nov-2021: Factory management got DEA re-acceptance from Accord on 11-June-2017. Issue remains corrected. On 13-Mar-2022: Corrected from previous inspection. Factory got DEA re-acceptance from Accord on 11th June 2017. On 19-Jun-2023: Corrected from previous inspection. Water tanks were placed on the roof as per accepted floor load plan. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (within 6-months) | Corrected
Initial Inspection |  | 9 | Stability of roof and masonry wall on west elevation | Factory Engineer to check design of existing roof and free- standing masonry wall on western elevation | 90% work has been done. Next 21 April-25 will finish 100%. | Jul 6 2016 | On 02-Sep-2016: They have a plan to demolish a part of office building and organize. So after demolition they will provide roof truss as per consultant’s advice. On 20-Nov-2016: Factory have demolished the free standing masonry wall on western elevation. But no design and analysis have provide along with DEA. Factory requires to submit analysis report of roof structure over office building to Accord. On 12-july-2017: Factory have demolished the free standing masonry wall on western elevation. But no design and analysis have provide along with DEA. Factory requires to submit analysis report of roof structure over office building to Accord. On 11-02-2018 :Free standing masonry walls has been demolished . No design and analysis of the existing roof was provided by factory authority . On 18th September 2018: This issue is required to be covered in EA. Factory last submitted revised EA on 15th July 2018 which is under review. On 24th April 2019: This issue is required to be covered in EA report. Factory is required to submit revised EA report as per the last review comment. On 13-Jan-2020: Factory management got DEA acceptance from Accord on 18-November-2019. As per DEA recommendation factory management had completed steel retrofitting works but QC certificate was not kept onsite. It has to be mentioned that due to some survey limitations (False ceiling board & large height of shed) all members couldn't be verified. On 09-Dec-2020: Factory management got DEA acceptance from Accord on 18-November-2019. As per DEA recommendation factory management had not started steel retrofitting works of office building, where remediation timeline was 15th January 2020. Also, onsite architectural layout was found changed at 1st and 2nd floor, which was not matched with accepted drawing. Factory is required to update the architectural drawing and keep on site on next inspection. On 02-Nov-2021: DEA acceptance was provided on 7th June 2016 & re-acceptance on 11th June 2017. But after follow up inspection on 11th February 2018, the factory submitted the revised DEA of rooftop shed to Accord, which has been reviewed and accepted. Factory management got DEA acceptance of roof top shed from Accord on 18-November-2019. As per DEA recommendation factory management had started steel retrofitting works of office building but not completed as per accepted drawing, where remediation timeline was 15th January 2020. Angle along B grid at bottom chord not been installed. Also, gusset plate and single angle were required to be installed at the ridge of each grid which were not done. Factory is required to complete all the required remediation as per accepted retrofitting drawing as soon as possible. On 13-Mar-2022: DEA of roof top shed had been re-accepted from Accord on 18th Nov 2019. Factory had demolished the freestanding wall. As per accepted EA of the roof shed, factory has completed the retrofitting work. However, during inspection some discrepancies were found between as-built drawing and as-built condition; between retrofitting drawing and retrofitting work (See verification report). Factory is required to submit the revised EA within 14 days of receiving the report. On 19-Jun-2023: No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. On 17-Nov-2024: Factory submitted the safety check report to RSC and review comment sent from RSC for the Office Building. Now factory is required to submit the revised documents to RSC within 27-Nov-2024. On 21-May-2025: As per last review comment revised safety check report is required to be submitted to RSC. Extended timeline is 01 Jun 2025. The factory is required to submit the revised documents to RSC within the timeline. RPO Comments on 28-Dec-2025 : As per the comment from SSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: From the pictorial evidence, it appears that the factory has completed the remedial work as per the RSC-approved drawing & documents. A further inspection is required for confirmation of member size, connections etc. | (within 6-weeks) | Pending Verification
Follow Up Inspection |  | 10 | New Finding: N/W cantilevered slabs not shown on Structural Drawings resulting in high stresses in Columns (I1 and I2) and supporting suspended slabs | Factory Engineer to arrange for Structural Consultant to verify insitu concrete stresses either by 100mm dia. cores for 1I and 2I Columns or 100mm dia. cores from 4 columns or alternate size as specified in ACI 562 | As per mail communication We are shifting from the office building to Mian building. | Dec 10 2016 | On 20-Nov-2016: Total 4-nos of cores have been incorporated in DEA report. As per core test result all cores were taken from ground floor. On site, there were 5-nos of core cutting layout was observed instead of 4-no's of core and location was 1st floor. Mentioned core taken grid doesn’t exists. Factory requires to clarify the ambiguity of core test report and site observation. Also, clarify about no. of core taken and no. of core incorporated in DEA report. On 12-july-2017: Revised DEA of this factory has been prepared and submitted to Accord for review and factory got re acceptance from Accord on 11 June, 2017. On 11-02-2018 :Corrected in previous follow-up inspection .Core test was done as a part of DEA . On 18th September 2018: Corrected from previous follow-up. On 24 April 2019: Core was taken as a part of concrete strength evaluation and core test location was verified in previous inspection. The issue is corrected as per previous inspection On 13-Jan-2020: Corrected in previous follow up inspection. Factory management got DEA re-acceptance from Accord on 11-June-2017. Core test had been done as a part of DEA. During inspection original core test reports were found onsite. On 09-Dec-2020: This issue was corrected from previous inspection. On 02-Nov-2021: Factory management got DEA re-acceptance from Accord on 11-June-2017. Core test had been done as a part of DEA. During inspection original core test reports were found onsite. Issue remains corrected. On 13-Mar-2022: Corrected from previous inspection. Cores were taken and covered in DEA (re-accepted on 11th June 2017). On 19-Jun-2023: Corrected from previous inspection. Cores were taken. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | Immediately | Corrected
Follow Up Inspection |  | 11 | New finding-2: Water leakage was found in retaining wall of pump house | Factory engineer is required to find the reason and remedy of the leakage of retaining wall as soon as possible. | As per mail communication We are shifting from the office building to Mian building. | Jan 23 2020 | On 13-Jan-2020: During inspection water leakage was found in retaining wall of pump house. Factory management is required to take proper initiative to resolve the issue. On 09-Dec-2020: Factory had repaired the water leakage portion at pump house. During inspection no water ponding was found at pump room. On 02-Nov-2021: No water ponding was found during inspection. Water leakage was found repaired. Issue remains corrected. On 13-Mar-2022: Corrected from previous inspection. Factory has repaired the leakage and during inspection no leakage was observed. On 19-Jun-2023: Corrected from previous inspection. Factory has repaired the leakage. On 10-Jun-2024: Corrected previously. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 12 | New finding-3: Modification and discrepancy found at office building. | As part of EA, update as-built drawing, check the adequacy of columns and cantilever. | 90% work has been done. Next 21 April-25 will finish 100%. | Apr 30 2022 | On 13-Mar-2022: Factory had demolished some portion of Office Building at west side, large cantilever found at north-west corner and all columns were found 90 degree rotated from which is shown on as-built drawing. As part of EA, update as-built drawing, check the adequacy of columns, cantilever and submit to RSC for review. On 19-Jun-2023: No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. On 17-Nov-2024: Factory submitted the safety check report to RSC and review comment sent from RSC for the Office Building. Now factory is required to submit the revised documents to RSC within 27-Nov-2024. On 21-May-2025: As per last review comment revised safety check report is required to be submitted to RSC. Extended timeline is 01 Jun 2025. The factory is required to submit the revised documents to RSC within the timeline. RPO Comments on 28-Dec-2025 : As per the comment from SSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: From the pictorial evidence, it appears that the factory has completed the remedial work as per the RSC-approved drawing & documents. A further inspection is required for confirmation of member size, connections etc. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 13 | New finding-4: Modification and discrepancy found at office building. | Implement remediation work if required | 90% work has been done. Next 21 April-25 will finish 100%. | Sep 15 2022 | On 13-Mar-2022: Any remediation work raised from EA is required to be implemented after getting acceptance of EA. On 19-Jun-2023:No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. On 17-Nov-2024: After the acceptance of safety check report, the factory will carry out remedial works (if required). On 21-May-2025: Retrofitting work is required to be carried out after getting acceptance of Safety Check report by RSC (if any). RPO Comments on 28-Dec-2025 : As per the comment from SSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: From the pictorial evidence, it appears that the factory has completed the remedial work as per the RSC-approved drawing & documents. A further inspection is required for confirmation of member size, connections etc. | (within 6 months) | Pending Verification
Follow Up Inspection |  | 14 | New finding-5: Broken false ceiling found at shed area of office Building. | Replace all broken false ceiling with new one. | 90% work has been done. Next 21 April-25 will finish 100%. | Apr 30 2022 | On 13-Mar-2022: During inspection broken false ceilings were found at shed area of office Building. Factory is required to replace all broken false ceiling with new one. On 19-Jun-2023: No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. During the inspection, broken false ceiling could not be checked. On 17-Nov-2024: Factory submitted the safety check report to RSC and review comment sent from RSC for the Office Building. Now factory is required to submit the revised documents to RSC within 27-Nov-2024. On 21-May-2025: As per the last review comment revised safety check report is required to be submitted to RSC. During the inspection, the broken false ceiling could not be checked as the entry of the upper floor was restricted. However, this issue will be verified after the acceptance of the safety check report. RPO Comments on 28-Dec-2025 : As per the comment from SSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: From the pictorial evidence, it appears that the factory has completed the remedial work as per the RSC-approved drawing & documents. A further inspection is required for confirmation of member size, connections etc. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 15 | New finding-6: Non structural element found unbraced and not anchored. | Anchor/brace all non structural elements | 90% work has been done. Next 21 April-25 will finish 100%. | Apr 30 2022 | On 13-Mar-2022: During inspection non structural rack found unbraced and not anchored. Factory is required to anchor/brace all non structural elements within the factory premises. On 19-Jun-2023:No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. During the inspection, non-structural elements could not be checked. On 17-Nov-2024: During the inspection, entry was restricted to all locations of the Office building, so this issue could not be verified. The factory is using a portion of the building on the ground floor only for utility purposes. On 21-May-2025: During the inspection, the entry of the upper floor was restricted. However, this issue will be verified after the acceptance of the safety check report. RPO Comments on 28-Dec-2025 : As per the comment from SSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: From the pictorial evidence, it appears that the factory has completed the remedial work as per the RSC-approved drawing & documents. A further inspection is required for confirmation of member size, connections etc. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 16 | New finding-7: Apparently inadequate external steel stair (Office Building). | As part of EA check the adequacy of the steel stair. | Steel Stair has ben cut.Documrnt sent.Another Document is in Progress. | Apr 30 2022 | On 13-Mar-2022: During inspection the external steel stair (Office Building) was appeared to be inadequate. As part of EA Factory engineer is required to check the adequacy of the steel stair and submit to RSC for review. On 19-Jun-2023: No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. During the inspection, the external steel star was non-functional. On 17-Nov-2024: Factory has removed the steel stair. On 21-May-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 17 | New finding-8: Apparently inadequate external steel stair (Office Building). | Implement remediation work where required. | Steel Stair has ben cut.Documrnt sent. | Sep 15 2022 | On 13-Mar-2022: Any remediation work raised from EA is required to be implemented after getting acceptance of EA. On 19-Jun-2023: No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. During the inspection, the external steel star was non-functional. On 17-Nov-2024: Factory has removed the steel stair. On 21-May-2025: Corrected previously. | (within 6 months) | Corrected
Follow Up Inspection |  | 18 | New finding-9: Corrosion observed on steel members external steel stair (Office Building). | Provide rust proof paint on steel members. | 90% work has been done. Next 21 April-25 will finish 100%. | Apr 30 2022 | On 13-Mar-2022: During inspection corrosion observed on steel members external steel stair (Office Building). Factory is required to remove rust from steel and provide rust proof paint on steel members. On 19-Jun-2023: No action taken regarding the issue. A brick wall had build in front of the main entrance to restrict all the access to upper two floors of office building. However, the factory is using a portion of ground floor (4 rooms) for boiler, compressor, generator & sub-station purpose. The exit of the rooms are separate and open/directed to the outside of the building. There is no worker found inside the utility rooms of ground floor of the building. On 10-Jun-2024: The initial issue was to conduct the assessment of rooftop shed of the office building. The factory declared that three storied Office Building would be demolished, and which was accepted on ACCORD on 7th June 2016. Later the factory submitted the documents for steel roof top shed instead of demolition which was accepted with remediation on from ACCORD on 18th November 2019 and remedial works require to be completed on 15th January 2020. On follow-up inspection (13th March 2022) it was observed that factory constructed a new external steel stair adjacent to the Office Building and some portion of the Office building has been demolished which requiring the assessment of the building due to a large cantilever slab and structural modification. Also, some discrepancies have been found between retrofitting drawing and retrofitting work (See verification report), which requiring reassessment for the Office building. However, there are no as built drawing was found for Office building RCC part. The factory has not submitted the assessment report yet. After that, the factory provides a consent letter to demolish the office building except for the small portion of the ground floor (boiler, compressor, generator& sub-station). Again, a meeting was held on 11th July at RSC office with factory management representatives regarding the next step of Office building & external steel stair. As per the meeting discussion they have committed that they will submit full set of as built drawing with necessary safety check on 26 July 2024 and provide the detailed plan of floor uses and demolition of the steel stair. However, during inspection, all the entrances of the Office Building were found blocked by brick walls except a small portion of the ground floor. The factory is using small portions for boiler, compressor, generator & sub-station purposes. The exits of the rooms are separated and directed to the outside of the building. During the inspection, the external steel star was non-functional, but a sign of corrosion was observed from outside. On 17-Nov-2024: During the inspection, entry was restricted to all locations of the Office building, so this issue could not be verified. The factory is using a portion of the building on the ground floor only for utility purposes. On 21-May-2025: During the inspection, the entry of the upper floor was restricted. However, this issue will be verified after the acceptance of the safety check report. RPO Comments on 28-Dec-2025 : As per the comment from SSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: From the pictorial evidence, it appears that the factory has completed the remedial work as per the RSC-approved drawing & documents. A further inspection is required for confirmation of member size, connections etc. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 19 | New finding-10: Water ponding on the roof of Factory Building. | The factory is required to provide develop roof drainage system with proper slope and adequate water outlets. | In Progress. Need 30 days to be finished. | Dec 19 2023 | On 19-Jun-2023: Water ponding observed on the roof of Factory Building. The factory is required to develop roof drainage system with proper slope and adequate water outlets. On 10-Jun-2024: No action has been taken regarding this issue. During the inspection, water ponding was observed on the roof floor of the Factory Building. The factory is required to improve roof drainage system with a proper slope and adequate water outlets. On 17-Nov-2024: Factory did not provide the water proofing layer on the roof. During inspection, signage of water ponding was found. On 21-May-2025: The factory has applied water proofing on the roof. During the inspection, finishing work was found pending and discharge points were found under size. The factory is required to complete the finishing work and improve the discharge point accordingly. RPO Comments on 02-Mar-2026 : The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 months) | In Progress
Follow Up Inspection |  | 20 | New finding-11: Deflection of roof slab of northern (middle) stair of Factory Building. | The building engineer is required to investigate the reason of slab deflection and prepare an investigation report with proper remedial actions. Carry out remedial works as per the suggestion of investigation report. | In Progress. Need 15 working days to be finished. | Jul 31 2023 | On 19-Jun-2023: Deflection of roof slab was found in the northern (middle) stair of Factory Building. The building engineer is required to investigate the reason of slab deflection and prepare an investigation report with proper remedial actions. The factory is required to carry out remedial works as per the suggestion of investigation report. Before remediation, submit the investigation report to the RSC for review. On 10-Jun-2024: Factory has not produced investigation report regarding slab deflection (stair roof). The building engineer is required to investigate the reason of slab deflection and prepare an investigation report with proper remedial actions (if required). Carry out remedial works as per the suggestion of investigation report. On 17-Nov-2024: During the inspection, the deflected roof slab over the stair was found. No action has been taken yet. Building engineer is required to investigate the reason of deflection of slab and suggest proper remedial action. Factory will follow the recommendation of investigation report to carryout the remedial works. RPO Comments on 22-Apr-2025 : The design documents are pending to be submitted to RSC. After acceptance of EA documents by the RSC, the factory will do the remediation work based on the EA approval. On 21-May-2025: As per the provided calculation, the deflection is within the allowable limit. On the other hand, the factory provided additional brick column in the middle of the slab. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 21 | New finding-12: Crack in brick wall of the N-W cantilever area of Factory Building. | The factory is required to carry out suitable remedial works as per the suggestion of building engineer. | In Progress. Need 15 working days to be finished. | Jul 31 2023 | On 19-Jun-2023: Crack observed in brick wall of the N-W cantilever area. The factory is required to carry out suitable remedial works as per the suggestion of building engineer. On 10-Jun-2024: During the inspection, cracks were observed on the brick wall at several places in the Factory Building. The factory is required to carry out suitable remedial works as per the suggestion of the building engineer. On 17-Nov-2024: During inspection, crack were found in brick wall at several locations. Factory is required to repair the cracks. On 21-May-2025: The factory repaired some cracks. But during the inspection still some cracks were found on the facade wall at North. RPO Comments on 02-Mar-2026 : The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 22 | New finding-13: Dampness throughout the Factory Building. | The factory is required to identify the reason of dampness and carry out remedial works accordingly. | In Progress. Need 15 working days to be finished. | Jul 31 2023 | On 19-Jun-2023: Dampness observed throughout the building specially on peripheral façade and toilet zone walls. The factory is required to identify the reason of dampness and carry out remedial works accordingly. On 10-Jun-2024: No action was taken regarding this issue. During inspection, dampness was observed throughout the building on peripheral façade and toilet zone walls. The factory is required to identify the reason of dampness and carry out remedial works accordingly. On 17-Nov-2024: During the inspection, dampness was found at several locations of the buildings. Factory is required to repair the dampness. On 21-May-2025: Dampness has been repaired. During the inspection some damp area was also found. Later the factory repaired those areas and sent pictorial evidence by mail. An investigation report has also been prepared. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 23 | New finding-14: Corrosion in 1st floor slab edge rebar at north side of the Factory Building. | The factory is required to remove corrosion of rebar and carry out suitable remedial works as per the suggestion of building engineer. | Done | Jul 31 2023 | On 19-Jun-2023: Corrosion observed in 1st floor slab edge rebar at north side of the Factory Building. The factory is required to remove the corrosion of rebar and carry out suitable remedial works as per the suggestion of building engineer. On 10-Jun-2024: Factory repaired damaged edge of slab at north side of Factory Building. On 17-Nov-2024: Corrected previously. On 21-May-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 24 | New finding-15: Falling hazard in lift core of Factory Building. | The factory must immediately restrict access to the lift core and seal the lift door to prevent potential falling hazards. | In Progress. Need 15 working days to be finished. | Nov 21 2024 | On 17-Nov-2024: During inspection, falling hazard in lift core of Factory Building was found. The factory must immediately restrict access to the lift core and seal the lift door to prevent potential falling hazards. On 21-May-2025: The factory has provided double layer door on the lift opening. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 25 | New finding-16: Falling hazard in lift core of Factory Building. | The factory must include the current lift with one that incorporates necessary safety features, ensuring compliance with safety standards to eliminate the risk of falling hazards. | The facility has approved to install a new lift structure to make sure the safety & security. Work is in progress. Within 20 working days it will be finished. | Jan 15 2025 | On 17-Nov-2024: The factory must include the current lift with one that incorporates necessary safety features, ensuring compliance with safety standards to eliminate the risk of falling hazards. On 21-May-2025: The factory has proved double layer door on the lift opening. | (within 6 weeks) | Corrected

## Fire
Date
07-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Alif Industries Ltd. (Previously Alif Casual Wear Ltd), 69, Vogra, Gazipur Sadar, Gazipur., Gazipur, Dhaka
Date of Inspection |  | 2015-03-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The cargo elevator does not have the proper fire rating for the elevator door. | Provide the proper 1.5 hr. fire rating for the elevator door. |  | May 15 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected as per previous follow up. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected as per previous follow up. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | The boiler and compressor rooms on separated by fire rated construction due to openings and non-rated doors. | Separate the boiler and compressor rooms by 2-hr fire rated construction for high rise. Seal and/or protect all openings to maintain the required fire separations. When located to the exterior of a building, 3m (10 ft.) separation is required. Provide proper ventilation and consult a qualified engineer. |  | Nov 15 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected as per previous follow up. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Rooms used for combustible storage and wastage room on the ground, 1st and 2nd floors are not separated by fire-rated construction | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) - If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (305ft2). Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). |  | Apr 17 2016 | On 03/07/2018: Corrected. Note: Factory will ensure that installed fire doors are properly functional. On 22/01/2019: Corrected as per previous follow up. Note: Factory shall ensure that process goods storage areas are organized according to standard on 1st, 2nd & 7th floors. On 13.11.2019: Corrected as per previous follow up. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | All exit stair enclosures are not separated from parking area and exterior discharge paths on the ground floor by fire rated construction. | The exit stair enclosure shall be provided with a minimum of 2-hr fire resistance rating for buildings 4 or more stories |  | Feb 10 2015 | On 31/12/2017: In progress. On 16/04/2018 Factory asked for time extension which is not acceptable On 03/07/2018: Some small rooms at stair 01 (east side stair) has not been separated yet. On 22/01/2019: Not corrected yet. Unseal penetrations shall be sealed properly in east stair enclosure throughout the building. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | All exit stairs are not separated from work areas on each floor by fire-rated construction | Provide minimum 1.5-hr fire rated doors for buildings that are 4 or more stories. Seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic- closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | Done | May 4 2016 | On 13.11.2019: The fire door holder shall be full functional and the separation of the store room in the ground floor shall ensure 2-hr fire separation for the stair. On 17/11/2019: Factory informed that this issue is resolved but documents for pre-T&C are pending. Progress status will be changed to PV when factory submits the documents and is determined to be ready for pre-T&C by RSC engineers On 13/2/2022: Fire door installation has been done. Interfacing work with FACP almost done. On 08-Dec-2022: Not corrected yet but progress has been observed. Interfacing with FACP has been completed. Installation of fire rated door has not been done properly in few location where gap beneath the door has been found 25 mm on 7th floor and accessories and hardware of Fire rated door has been found not functional properly. On 10-Jun-2024: Not corrected. 4 out of 8 double leaf fire doors were not properly functional. Factory has also been working on interfacing of the fire doors with the FACP which is under installation & will be completed within 31 Jul 2024. On 21-Nov-24: Progress has been observed. Fire door coordinator were found functional and no external object has been found during inspection. But the fire door has not been interfaced with FACP as the fire alarm installation and modification work is on going reportedly. Factory also mentioned that they will complete installation work within 10-Dec-2024. On 21-May-25: Not corrected. During the Stage 2 advance meeting, the factory was given a timeline up to 30-Apr-2025 by the RSC to remediate this issue. However, exit stair enclosures are separated with fire-rated construction at all locations except stair-1 (North-East) due to unprotected opening from the maintenance room on the 2nd floor. RPO Comments on 28-Dec-2025 : As per the comment from FLSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: "From the pictorial evidence sent by factory, it seems that the factory has taken the required remediation action as per the recommendation. However, it will be verified during the next scheduled inspection." | Within 3 months | Pending Verification
Initial Inspection |  | 6 | Unsealed penetrations are located in the fire- rated floor/ceiling assemblies of the east and west exit stairs on each floor | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation. |  | Feb 10 2015 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13/2/2022: Corrected. On 13.11.2019: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 7 | Storage and boiler rooms discharges directly into east exit stair enclosure. | Openings from exit enclosure to storage and boiler spaces shall be provided with a vestibule with fire rated construction and openings. Provide a 1.5 hr. fire rated door on the exit stair side and a 1-hr. fire rated door on the storage and boiler room side. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure |  | Apr 17 2016 | On 03/07/2018: Boiler room has been separated but store room has not been properly separated due to non functional fire doors. On 22/01/2019: Corrected. Factory has installed fire door in exit stair enclosure and during inspection door was found closed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 8 | The exit discharge paths serving the north and west exit stairs are less than 3 m (10 ft.) wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way (only include this if feasible). |  | Oct 10 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected as per previous follow up. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 9 | The southeast exterior exit stair is not properly separated from the building. | Exterior exit stairs shall be separated from the building with a rating requirement of 1 hr. fire rating for 3 or fewer stories. The rating of the exterior wall shall extend 3.05 m (10ft) beyond the ends of the stair structure. |  | Feb 10 2015 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 10 | Building did not have stair designation signs and occupant load signs at required locations. | Provide stair designation signs and occupant load signs at required locations |  | May 10 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. Note: Factory shall posted stair designation sign and occupant load signs in all required location. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 11 | Egress doors and gates with locking features are provided at building exits, exit stairs and exit discharge. | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 and ACCORD standard 6.8.2. |  | Oct 9 2015 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. Removed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected as per previous follow up. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 12 | Sliding doors are provided at building exits, exit stairs and exit discharge. | Replace all gates and sliding doors along the means of egress with side-hinged, swinging egress doors in accordance with ACCORD standard 6.8.1. |  | Oct 9 2015 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. Replaced. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | Exit stairs serve more than 5 stories and do not have required re- entry provisions. | Every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. |  | Jul 9 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected as per previous follow up. Note: Factory shall post re-entry signs at required location. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 14 | Common path of egress travel exceeds limit from goods down storages on the ground floor. | Reconfigure the egress arrangement to reduce the maximum common path of travel to not more than 23 m (75 ft.) or 30 m (100 ft.) when complete sprinkler protection is provided. |  | Feb 10 2015 | On 31/12/2017: Corrected. On 03/07/2018: Corrected as per previous follow up. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 15 | The day-care room on the ground floor does not meet ACCORD standard 3.4.2.1.1. | Day-care shall be located on the ground floor with a maximum travel distance of 9 m (30 ft) or located one story above level of exit discharge with direct access to an exit enclosure. If the above is not possible provide a minimum 2-hr fire- rated exit corridor between the day-care room and exit stair with ACCORD approval. |  | Feb 10 2015 | On 03/07/2018: Corrected. Note: Factory will ensure proper separation and safe exit discharge from day-care room. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | Handrails are not provided on both sides of the exit stair. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.). |  | Oct 10 2016 | On 03/07/2018: Corrected. On 22/01/2019: Corrected. Provided. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 17 | All exit stairs discharge to the interior of the building. | Modify stair to discharge directly outside or Provide 2- hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). | Done | Feb 10 2015 | On 03/07/2018: Fire separation has not been completed yet. On 22/01/2019: Factory shall interface fire door properly with compliant fire alarm system in store room. On 13.11.2019: The fire door holder shall be full functional and the separation of the store room in the ground floor shall ensure 2-hr fire separation for the stair. On 13/2/2022: Fire door installation has been done. Interfacing work with FACP almost done. On 08-Dec-2022: Not corrected yet but progress has been observed. Fire Rated Door has been installed in all required location with proper interfacing with FACP but hardware has not been working properly so that separation has not been maintained. On 10-Jun-2024: Not corrected. Progress has been found. Fire door has been installed to separate the North-East (stair-1) from the store areas (vestibule). Factory has been working on interfacing of the fire doors with the FACP which is under installation & will be completed within 31 Jul 2024. However, power cable raceway has been installed in the exit discharge path from stair-1. South-West stair (Stair-2) discharges externally & South-East stair (Stair-3) is not being considered as an exit stair. On 21-Nov-24: Not Corrected. Progress was not significant. The exit discharge path were not protected from other occupancies due to cable tray has been observed at the Stair-1 discharge path. On 21-May-25: Not corrected. During the Stage 2 advance meeting, the factory was given a timeline up to 30-Apr-2025 by the RSC to remediate this issue. However, non-compliant installation due to unprotected cable trays throughout all the floors in stair-01 and maintenance room on the 2nd floor has been observed. Factory has installed Gypsum Boards for electrical cable raceway separation. Document related to gypsum board was submitted to RSC and rejected with observation on 22 Apr, 2025. No credible design or document was provided on-site for verification. RPO Comments on 28-Dec-2025 : As per the comment from FLSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: "From the pictorial evidence sent by factory, it seems that the factory has taken the required remediation action as per the recommendation. However, it will be verified during the next scheduled inspection." | Within 6 months | Pending Verification
Initial Inspection |  | 18 | The exits on the ground floor are not remotely located from each other such that a single fire event could compromise both exits. | Modify exit arrangement to meet ACCORD standard 6.6.6. or Provide additional exits to meet ACCORD standard 6.6.6. or Provide sprinkler protection in accordance with NFPA 13 to meet ACCORD standard 6.6.6. |  | Feb 10 2015 | On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Issue has been reopened at point no 48. On 08-Dec-2022: Refer to Issue# 48. On 10-Jun-2024: Refer to Issue no#48. | Within 6 months | Corrected
Initial Inspection |  | 19 | The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Done (All Ready submitted design & documents for Pre-T&C ) | May 19 2016 | On 13.11.2019: The deficiencies observed in the T&C has been re-solved which is informed by factory management. Factory applied for T&C. T&C is pending. On 17/11/2019: Factory informed that this issue is resolved but documents for pre-T&C are pending. Progress status will be changed to PV when factory submits the documents and is determined to be ready for pre-T&C by RSC engineers On 13/2/2022: Installation work almost done. Pending for pre T&C. On 15/12/2022 Comments from RCH:on 08 Dec 2022 based on Pre-T&C VI result the factory is not ready for full T&CVI requires again onsite pre T&C inspection. On 08-Dec-2022: During the day of FUiN, Pre T&CVI also has been conducted and found FADS requires another On Site Pre T&CVI. On 10-Jun-2024: A meeting has been conducted between the factory & RSC regarding delay in the Pre-T&CVI documents submission process on 16 May 2024. Factory has been granted an extended timeline until 31 July 2024 to complete the installation & modification works and submit the documents. Reportedly, installation is in progress & factory informed that they will submit the documents after completion of installation within the given timeline. On 21-Nov-24: Fire alarm detection system installation and modification work is on going reportedly. Factory also mentioned that they will complete installation and modification work within 10-Dec-2024 and will submit as-built drawings and required documents to RSC for review within 21-Dec-2024. On 21-May-25: Factory has stated that FADS installation work has been completed. During the inspection, it was observed that installation has been completed and the system was functional. However, several false fire alarms were observed during the inspection, and troubleshooting was ongoing. During the Stage 2 advance meeting, the factory was given timeline up to 15 Apr, 2025 for Pre-T&C document submission. Factory has submitted design & documents for Pre-T&C review on May 5, 2025 which is under review. RPO Comments on 02-Mar-2026 : The design documents (FADS) are pending to be submitted to RSC. | Design within 4 months, install within 9 months | In Progress
Initial Inspection |  | 20 | The high-rise building has an occupied floor greater than 23m (75 ft.) and is not provided with automatic sprinkler protection. The large occupant loads, heavy fuel loading and anticipated extended egress times warrant sprinkler protection. | Provide automatic sprinkler protection throughout the building in accordance with NFPA 13. |  | Mar 23 2016 | On 02.04.2017: Not applicable as the last occupiable floor height is less than 75ft. On 17-07-2017: N/A. On 31/12/2017: Corrected. Not required. On 03/07/2018: Corrected since it is verified earlier. On 22/01/2019: Corrected as per previous follow up. On 13.11.2019: Corrected. On 13/2/2022: Not applicable. On 08-Dec-2022: Corrected on previous follow ups. Note: Factory did not maintain the raised road level from all required area. Factory shall raised the height of the ground level from main entry road to stair -1 and all other required area. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Design within 6 months, install within 12 months | Corrected
Initial Inspection |  | 21 | Activation of the fire alarm system by a manual fire alarm station provides automatic occupant notification only on the floor of alarm and not throughout the building | Configure the fire alarm system to initiate automatic occupant notification on all floor levels to facilitate whole- building evacuation upon any manual fire alarm station activation | Done | Sep 27 2016 | On 13.11.2019: It is an integrated part of fire alarm system. On 17/11/2019: Factory informed that this issue is resolved but documents for pre-T&C are pending. Progress status will be changed to PV when factory submits the documents and is determined to be ready for pre-T&C by RSC engineers On 13/2/2022: It is an integrated part of fire alarm system. On 15/12/2022 Comments from RCH:on 08 Dec 2022 based on Pre-T&C VI result the factory is not ready for full T&CVI requires again onsite pre T&C inspection. On 08-Dec-2022: It is an integrated part of fire alarm system. Comments form RPO on 13/03/2023: Factory asked for time extension which is not accepted. On 10-Jun-2024: It is an integrated part of the Fire Alarm System. On 21-Nov-24: It is an integrated part of Fire Alarm System. On 21-May-25: It is an integrated part of Fire Alarm System. RPO Comments on 02-Mar-2026 : The design documents (FADS) are pending to be submitted to RSC. | Within 1 months | In Progress
Initial Inspection |  | 22 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10. |  | Feb 10 2015 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 23 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72. |  | May 19 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 24 | Fire department connection is not provided | Provide fire department connection in accordance with ACCORD standard 5.5.4. |  | Jun 18 2016 | On 02.04.2017: It is an integrated part fire fighting system. On 07/06/2017: Factory sent a CAP where they are asking for 30/06/2017 which is not accepted. Hence corrective action plan shall have to be completed within 18/06/2016 On 17-07-2017: It is an integrated part of fire fighting system. On 31/12/2017: Installation work progress is very slow. On 16/04/2018 Factory asked for time extension which is not acceptable On 03/07/2018: It is an integrated part of fire fighting system. On 22/01/2019: Corrected. Provided. On 13.11.2019: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 25 | Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 20. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 20. |  | Jun 18 2016 | On 16/04/2018 Factory asked for time extension which is not acceptable On 03/07/2018: It is an integrated part of fire fighting system. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 26 | Inspection, testing and maintenance of the automatic sprinkler system is not in accordance with NFPA 25. | Inspect, test and maintain the automatic sprinkler system and keep written records on- site, in accordance with NFPA 25. |  | Mar 15 2017 | On 03/07/2018: Corrected since it is not required. On 22/01/2019: Corrected as per previous follow up. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 27 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14. |  | Jun 18 2016 | On 31/12/2017: It is an integrated part of fire fighting system. On 16/04/2018 Factory asked for time extension which is not acceptable On 03/07/2018: It is an integrated part of fire fighting system. On 22/01/2019: It is an integrated part of fire fighting system. On 13.11.2019: Corrected. Maintaining. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 28 | Visible notification was not provided for the building in accordance with NFPA 72. | Provide visible notification for the building in accordance with NFPA 72. | Done | Oct 17 2016 | On 13.11.2019: It is an integrated part of fire alarm system. On 17/11/2019: Factory informed that this issue is resolved but documents for pre-T&C are pending. Progress status will be changed to PV when factory submits the documents and is determined to be ready for pre-T&C by RSC engineers On 13/2/2022: It is an integrated part of fire alarm system. On 15/12/2022 Comments from RCH:on 08 Dec 2022 based on Pre-T&C VI result the factory is not ready for full T&CVI requires again onsite pre T&C inspection. On 08-Dec-2022: It is an integrated part of fire alarm system. Comments form RPO on 13/03/2023: Factory asked for time extension which is not accepted. On 10-Jun-2024: It is an integrated part of the Fire Alarm System. On 21-Nov-24: It is an integrated part of the Fire Alarm System. On 21-May-25: It is an integrated part of the Fire Alarm System. RPO Comments on 02-Mar-2026 : The design documents (FADS) are pending to be submitted to RSC. | Within 3 months | In Progress
Initial Inspection |  | 29 | The required standpipe system is not installed in accordance with the ACCORD standard. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. | Done (All Ready submitted design & documents for Pre-T&C ) | Oct 19 2016 | On 13.11.2019: The deficiencies observed in the T&C has been re-solved which is informed by factory management. Factory applied for T&C. T&C is pending. On 17/11/2019: Factory informed that this issue is resolved but documents for pre-T&C are pending. Progress status will be changed to PV when factory submits the documents and is determined to be ready for pre-T&C by RSC engineers On 13/2/2022: Installation work is almost done. On 15/12/2022 Comments from RCH:on 08 Dec 2022 based on Pre-T&C VI result the factory is not ready for full T&CVI requires again onsite pre T&C inspection. On 08-Dec-2022: During the day of FUiN, Pre T&CVI also has been conducted and found Standpipe System requires another On Site Pre T&CVI. Comments form RPO on 13/03/2023: Factory asked for time extension which is not accepted. On 10-Jun-2024: A meeting has been conducted between the factory & RSC regarding delay in the Pre-T&CVI documents submission process on 16 May 2024. Factory has been granted an extended timeline until 31 July 2024 to complete the installation & modification works and submit the documents. Reportedly, installation is in progress & factory informed that they will submit the documents after completion of installation within the given timeline. On 21-Nov-24: Standpipe system installation and modification work has been completed reportedly. Factory also mentioned that they will submit as-built drawings and required documents to RSC for review within 21-Dec-2024. On 21-May-25: Factory has stated that SUPS installation work has been completed. During the inspection, it was observed that SUPS installation is completed and the system was active. However, gland pack installation is not complete for the Diesel Fire Pump. Clogged water was observed in the fire pump room as the centrifugal pump for sum pit was not working. Diesel Fire Pump battery installation is not as per the guidelines. During the Stage 2 advance meeting, the factory was given timeline up to 15 Apr, 2025, for Pre-T&C document submission. Factory has submitted design & documents for Pre-T&C review on May 5, 2025, which is under review. RPO Comments on 02-Mar-2026 : The design documents (SUPS) are pending to be submitted to RSC. | Within 6 months | In Progress
Initial Inspection |  | 30 | Exit signage was not provided along a path of egress on the ground floor. | Provide exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel where a change of direction is not obvious. |  | Feb 10 2015 | On 03/07/2018: Corrected. On 22/01/2019: Corrected. Provided. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 31 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The ACCORD standard | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. |  | Feb 10 2015 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 32 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes for the2nd floor. | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. |  | Feb 27 2017 | On 31/12/2017: Not corrected yet. On 03/07/2018: Corrected. Provided. On 22/01/2019: Corrected. Note: Factory shall ensure that emergency light illumination level on aisles are adequate. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 33 | New Finding (2nd Follow-up): The width of egress aisles is less than 36-in. Location: Second floor & Seventh Floor. | Provide minimum aisle widths of 36-in. |  | May 16 2016 | On 03/07/2018: Corrected. On 22/01/2019: Corrected. Provided. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 34 | New Finding (2nd Follow-up): Areas used for combustible storage are not separated by fire-rated Location: First Floor, Second floor & Seventh Floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Done | Feb 14 2017 | On 03/07/2018: No action has been taken yet. On 22/01/2019: Process goods storage areas were not organized according to standard on 1st, 2nd & 7th floors. On 13.11.2019: In-process storage not found as per recommendation. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Not Corrected. In-process storage was found more than allowable limit in several floor areas. Factory shall need to provide designated in-process storage areas within the allowable limit. On 21-Nov-24: Corrected. Factory shall maintain in-process storage management as per the recommendation on each floor. On 21-May-25: Not Corrected. Issue reopen. In process storage was found exceeding the allowable limit on the 1st & 7th floor. RPO Comments on 02-Mar-2026 : Though factory reported this CAP item as completed but the provided pictorial evidence against this CAP item is insufficient therefore the CAP item will remain in progress & hence the corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 35 | New Finding (2nd Follow-up): Storage was located in the exit stair. Location: Ground Floor. | Remove all storage from exit stairs and egress paths. |  | Oct 13 2016 | On 31/12/2017: Issue has been reopened. On 03/07/2018: Storage has been observed at north stair exit discharge on ground floor. On 22/01/2019: Corrected. Removed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 36 | New Finding (2nd Follow-up): A single means of egress is provided from the office building (Office room, Dining room, Sample room) where the occupant load exceeds 49 persons. | Provide additional means of egress. |  | May 10 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected as per previous follow up. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected as per previous follow up. On 10-Jun-2024: Corrected. Factory has informed that the office building is not in operation. On 21-Nov-24: Corrected On 21-May-25: Corrected. Office building was not in operation during the inspection. | Within 1 months | Corrected
Follow Up Inspection |  | 37 | New Finding (2nd Follow-up): Guards were not present on balcony on the 1st floor. | Provide guards on the balcony. |  | Apr 17 2016 | On 03/07/2018: Corrected. On 22/01/2019: Corrected. Provided. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. Factory has informed that the office building is not in operation. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 1 months | Corrected
Follow Up Inspection |  | 38 | New Finding (2nd Follow-up): Manual on-off switch is provided for emergency lighting units. This was reflected throughout the building in various locations. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Completed. It is already corrected waiting for RSC verification. | Apr 17 2016 | On 31/12/2017: Issue has been reopened. On 03/07/2018: Corrected. On 22/01/2019: Corrected. Removed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Issue reopened. Manual On-Off switch has been found on several location including 6th Floor. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 1 months | Corrected
Follow Up Inspection |  | 39 | New Finding (4th follow up): The factory is using/storing liquefied gas cylinders without proper separations | Remove them from the factory building. or Provide 2-hr rated room for using/storing liquefied gas cylinders and ensure proper ventilation of that room. Source of fire such as electrical connection is prohibited. | Done | Oct 3 2016 | On 31/12/2017: Corrected. Not found. On 03/07/2018: Corrected. Note: Factory will ensure that installed fire door is properly functional. On 22/01/2019: Corrected as per last follow up. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. Not found. On 10-Jun-2024: Corrected. LPG is stored in a 2-hr rated separated room. On 21-Nov-24: Corrected On 21-May-25: Not Corrected. Issue reopen. Maintenance room was loated inside the LPG storage room, and unsealed penetration was located between the LPG storage & compressor room. RPO Comments on 02-Mar-2026 : Though factory reported this CAP item as completed but the provided pictorial evidence against this CAP item is insufficient therefore the CAP item will remain in progress & hence the corrective action plan should be completed as per the given recommendation with immediate concern. | within 2 Months | In Progress
Follow Up Inspection |  | 40 | New Finding (4th follow up) : Non-compliance locking feature was observed in main discharge (office building) with pocket gate swing in the wrong direction | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 and ACCORD standard 6.8.2. & make the pocket door swing in the direction of egress travel. |  | Sep 1 2016 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected. Removed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Refer to Issue# 49. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | within 6 days | Corrected
Follow Up Inspection |  | 41 | New Finding (5th Follow-Up): Generator/ Transformer room is not properly separated by fire rated construction from each other | Generator/ bTransformer room shall be separated from the stair by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) shall be protected by 1.5-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or, relocate the utility room to a safe place. |  | Sep 2 2017 | On 31/12/2017: Corrected. On 03/07/2018: Corrected. On 22/01/2019: Corrected as per previous follow up. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 1 months | Corrected
Follow Up Inspection |  | 42 | New Finding (5th Follow-Up): Storage was located in the exit stair. Location: East exit stair | Remove all storage from exit stairs. |  | Jan 25 2017 | On 03/07/2018: Not corrected. On 22/01/2019: Corrected. Removed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. Not found. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 43 | New Finding (5th Follow-Up): Penetrations through floor/ceiling assemblies are found unsealed. Location(s):South-East corner of every floor | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required |  | Nov 30 2016 | On 31/12/2017: Issue has been reopened. On 03/07/2018: Corrected On 22/01/2019: Corrected. Sealed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. Not found. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 44 | New Finding (5th Follow-Up): In the exit stairs at all floors the staircase landing is blocked by fire door's leaf | Need to shift the fire door, so that the staircase landing will be free for emergency exit. |  | Jan 30 2017 | On 03/07/2018: Corrected. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 45 | New Finding (7th follow up): The factory is using/storing liquefied gas cylinders without proper separations | Remove them from the factory building.orProvide 2-hr rated room for using/storing liquefied gas cylinders and ensure proper ventilation of that room. Source of fire such as electrical connection is prohibited. |  | Apr 15 2017 | On 31/12/2017: Corrected. Not founded. On 03/07/2018: Corrected. Note: Factory will ensure that installed fire door is properly functional. On 22/01/2019: Corrected. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. Not found. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Refer to issue no#39. | Immediately | Corrected
Follow Up Inspection |  | 46 | New Finding (7th Follow-Up): The dining area is not separated from adjacent production floor area by fire rated construction. | Separate the dining area by a minimum 3-hr fire-rated construction having a direct access to exit stair. Seal and/or protected all openings to maintain the required fire eparations | Work In Progress 20-Nov-2024 | Jun 30 2017 | On 31/12/2017: No action has been taken yet. On 03/07/2018: Fire separation is going on. On 22/01/2019: Not corrected yet. Still openings observed between dining area and production floor. On 13.11.2019: Separation work is not completed yet. On 13/2/2022: Corrected. On 08-Dec-2022: Issue re open. Separation has not been observed as per recommendation on 3rd Floor between dining and production area. Factory shall comply with Table 3.2.1 BNBC2006. E4-small assembly occupancy (less than 300 person) shall be separated by 3-hr fire rated construction having direct access to exit stair for required exits. E-4 large assembly occupancy (more than 300 person) is not permitted. On 10-Jun-2024: Not corrected. No progressive action has been taken yet. On 21-Nov-24: Corrected. No dining area has been observed at 3rd floor production area. On 21-May-25: Corrected. Dining area was not found in the factory premises and the 3rd floor was replaced with storage area. | within 1 month | Corrected
Follow Up Inspection |  | 47 | New Finding (10th Follow-Up): The aisles along means of egress has interrupted by obstruction/storage on several floors. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. |  | Jun 7 2018 | On 03/07/2018: New Finding (10th Follow-Up) On 22/01/2019: Corrected. Removed. On 13.11.2019: Corrected. On 13/2/2022: Corrected. On 08-Dec-2022: Corrected. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 48 | New Finding (13th FUI): The exits on the ground floor are not remotely located from each other such that a single fire event could compromise both exits. | Modify exit arrangement to meet ACCORD standard 6.6.6. or Provide additional exits to meet ACCORD standard 6.6.6. or Provide sprinkler protection in accordance with NFPA 13 to meet ACCORD standard 6.6.6. |  | Dec 3 2022 | On 13/2/2022: New finding. On 08-Dec-2022: Corrected. New exit has been built on mid north side. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | within 1 month | Corrected
Follow Up Inspection |  | 49 | New Finding (14th FUiN): Doors along means of egress are provided with a non compliant locking feature. Location: Stair-2,3 of several floor and Warehouse on Ground Floor. | 1. Remove all non compliant locking features from egress doors. 2. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. 3. Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. 4. Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an M58occupant load exceeding 49 persons. | Completed. It is already corrected waiting for RSC verification. | Dec 11 2022 | On 08-Dec-2022: New Finding. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 50 | New Finding (14th FUiN): Obstruction has been identified on Exit discharge path. of Stair-2. Location - Ground Floor | Keep egress paths and egress discharge clear of obstructions. | Completed. It is already corrected waiting for RSC verification. | Dec 11 2022 | On 08-Dec-2022: New Finding. On 10-Jun-2024: Corrected. On 21-Nov-24: Corrected On 21-May-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 51 | New Finding (14th FUiN): Exit stair enclosures are not free from unusual unsealed penetrations and openings (Electric cable raceway). Location- Stair-1 | Penetrations into and through an exit enclosure shall be prohibited with the exception of required exit doors, sprinkler piping, standpipes, electrical raceway for fire alarm equipment, and electrical conduit serving the exit enclosure. Remove cable raceway/busbar riser/ plumbing pipes and electrical pipes from the exit stair enclosures. Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | Done | Jan 8 2023 | On 08-Dec-2022: New Finding. Comments form RPO on 13/03/2023: Factory asked for time extension which is not accepted. On 10-Jun-2024: Not Corrected. No progress has been found. On 21-Nov-24: Not Corrected. Exit stair enclosure has not been separated due to cable tray has been found at stait-1. On 21-May-25: Not corrected. During the Stage 2 advance meeting, the factory was given a timeline up to 30-Apr-2025 by the RSC to remediate this issue. However, non-compliant installation due to unprotected cable trays throughout all the floors in stair-01 has been observed. Factory has installed Gypsum Boards for electrical cable raceway separation. Document related to gypsum board was submitted to RSC and rejected with observation on 22 Apr, 2025. No credible design or document was provided on-site for verification. RPO Comments on 28-Dec-2025 : As per the comment from FLSE regarding the factory’s submitted pictorial evidence for the mentioned CAP Item: "From the pictorial evidence sent by factory, it seems that the factory has taken the required remediation action as per the recommendation. However, it will be verified during the next scheduled inspection." | within 1 month | Pending Verification
Follow Up Inspection |  | 52 | New Finding (15 FUI): Parapet height is less than 42 inches (32 inches available) | As per RSC Technical Guidelines (Standard) 6.12.2.4- All occupiable roofs shall be provided with parapets or guards with a minimum height of 1067 mm (42 in.). | In Progress | Sep 10 2024 | On 10-Jun-2024: New Finding On 21-Nov-24: Not corrected. No progress has been found during the inspection. On 21-May-25: Corrected. Adequate parapet height was found on-site. | Within 3 months | Corrected
Follow Up Inspection |  | 53 | New Finding (17th FUI): Finished good storage area on the 3rd floor (previously Production floor) discharges directly into the exit stair enclosure-1. | Openings from exit enclosures to Storage areas shall be provided with a vestibule with fire-rated construction and openings in accordance with section 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a min 1-hr fire-rated door on the exit stair side and a 1.5 hr. fire-rated door on the Store side . Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure as per RSC Technical Guidelines (Standard)¹ V1.0. section 6.14.3. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. | Done | Aug 21 2025 | On 21-May-2025: New Finding RPO Comments on 02-Mar-2026 : Though factory reported this CAP item as completed but the provided pictorial evidence against this CAP item is insufficient therefore the CAP item will remain in progress & hence the corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 54 | New Finding (17th FUI): Penetrations through floor/ceiling assemblies are found unsealed due to plastic plumbing penetrations on 3rd floor modified storage area (previously production) and ground floor storage area. | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating in accordance with section 4.7 of RSC Technical Guideline (Standard) Or, Provide a minimum 2-hr fire rated shaft to separate the penetration from each floor if required. | In Progress | Aug 21 2025 | On 21-May-2025: New Finding RPO Comments on 02-Mar-2026 : The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress

## Electrical
Date
07-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Alif Industries Ltd. (Previously Alif Casual Wear Ltd), 69, Vogra, Gazipur Sadar, Gazipur., Gazipur, Dhaka
Date of Inspection |  | 2015-03-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Electrical Single Line Diagram (SLD) has inadequate information, and thus is unusable. | Prepare an accurate SLD with all necessary information, so any experienced person will then be able to understand the system. |  | May 30 2016 | On 18/04/2016: Modified SLD is submitted to Accord. Time extension is 30/05/2016. On 16/02/2016: Prepare as built diagram & submit it at accord for approval. New timeline is 30th April, 2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected. On 12/10/2017: Factory is asking for 30-Oct-2017 which is not accepted. Not Corrected On 17/07/2017: Not Corrected. On 31/12/2017: Not Corrected. Drawing is not as-built. On 03/07/2018: Not corrected. Due to electrical rectification work factory cannot complete the SLD On 22/01/2019: Not Corrected. Circuits are not identified. On 13-Nov-2019: Not Corrected. Cable identification pending. On 09/12/2020: Corrected | 8 Weeks | Corrected
Initial Inspection |  | 2 | Insulation resistance test of electrical equipment is not performed. | Insulation resistance test of all power cables (up to Floor distribution board or SDB) must be performed in a periodic manner and recorded. |  | Jun 15 2015 | On 02/09/2015: Corrected. | 12 Weeks | Corrected
Initial Inspection |  | 3 | Electric safety program is not initiated. | Electrical safety training and awareness program for the electrical personnel and workers must be initiated and recorded. |  | Jun 19 2015 | On 02/09/2015: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 4 | Lightning Protection System (LPS) needed but has not been installed. | Lightning arrestor must be installed (according to NFPA 780) with proper size air termination network, down conductors and earth termination. Redesign LPS for your factory to increase safety. |  | Aug 30 2016 | On 18/04/2016: Not corrected. Time extension is 20/06/2016. On 16/02/2016: Not corrected. New timeline is 30th April,2016. On 22/08/2016: Not Corrected. On 30/10/2016: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 5 | Thermographic scanning of the entire electrical system has been performed but the record is outdated. | Thermographic scanning of the entire electrical system must be performed twice in a year. |  | Aug 30 2016 | On 18/04/2016: Not corrected. Time is 30/05/2016. On 16/02/2016: Not corrected. New timeline is 30th April,2016. On 18/08/2016: Not Corrected On 30/10/2016: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 6 | Earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. |  | Aug 30 2016 | On 18/04/2016: Corrected. On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 30th April,2016. | 8 Weeks | Corrected
Initial Inspection |  | 7 | Earth Pit resistance record is unavailable. | Record earth pit resistance for all the earth pit and do once in a year. |  | Aug 30 2016 | On 18/04/2016: Not corrected. Time extension is 30/05/2016. On 16/02/2016: Ambiguity in keeping records should be avoided. New timeline to resolve this issue is 30th April,2016. On 18/08/2016: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 8 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. |  | Jun 15 2015 | On 02/09/2015: Corrected. | 8 Weeks | Corrected
Initial Inspection |  | 9 | Maintenance records don’t reflect actual factory circumstances, the records are totally inaccurate. | Maintenance Manager or Safety Officer must keep accurate records and ensure that they reflect actual factory day to day operations. |  | Jun 19 2015 | On 02/09/2015: Corrected. | 10 Weeks | Corrected
Initial Inspection |  | 10 | Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test, this must be done twice a year and records kept. |  | Jul 19 2015 | On 02/09/2015: Corrected. | 10 Weeks | Corrected
Initial Inspection |  | 11 | HT service cable dropping from pole is not protected near the base of the pole, above ground level. | HT cable dropping from HT pole must be protected in steel pipe of required size at least 2m from the ground level to protect the cable from any physical damage. |  | Jul 13 2015 | On 02/09/2015: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 12 | Transformer guarded with wire mesh fencing. | Construct a separate room for the transformer by constructing barrier (brick) walls (fire rated wall) up to the ceiling; the minimum area of the transformer room should be 10-13sqm (according to BNBC 2006, Section-2.6.3). |  | Apr 30 2016 | On 18/04/2016: Corrected. On 16/02/2016: Expand the brick wall up to the ceiling. Maintain sufficient working space (preferably 1 meter) around the transformer. New timeline to resolve this issue is 30th April,2016. | 5 Weeks | Corrected
Initial Inspection |  | 13 | HT cable passed through permanent wall not protected. | The HT cable must be encased in steel pipe (conduit) when passed through the wall and seal the openings after the passage of conduit by fire rated material. |  | Apr 30 2016 | On 18/04/2016: Corrected. On 16/02/2016: This Issue is not corrected. Provide fire rate material in the remaining gaps. New timeline to resolve this issue is 30th April,2016. | 5 Weeks | Corrected
Initial Inspection |  | 14 | HT & Secondary cables laid on the floor. | Secondary cables must be laid in a cable trench covered by rigid (checkered plate/concrete slabs). |  | Apr 30 2016 | On 18/04/2016: Corrected. On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 30th April,2016. | 5 Weeks | Corrected
Initial Inspection |  | 15 | Cable trench covered with wooden board. | Provide cover made of non-combustible material preferably metallic plate (checkered plate) or concrete slabs to protect the cables’ insulation from physical damage. |  | May 19 2015 | On 16/02/2016: Corrected. | 1 Weeks | Corrected
Initial Inspection |  | 16 | Oil cup below transformer breather is empty. Silica gel has been removed. | Transformer oil must be filled to the required level. Preferably, Assign supplier company to take necessary steps as soon as possible. |  | Apr 30 2016 | On 18/04/2016: Corrected. On 16/02/2016: Silica gel has been removed. This Issue is not corrected. New timeline to resolve this issue is 30th April,2016. | 2 Weeks | Corrected
Initial Inspection |  | 17 | The earth cable for the transformer body terminated without lug. | The earth cable for the transformer body must be terminated using lug of suitable size. |  | May 19 2015 | On 16/02/2016: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 18 | Generator frame connected to one earth point. | Generator must be connected to earth at two points. Ensure the earthing cable size is not less than 35rm. |  | May 20 2016 | On 18/04/2016: Not corrected. Time extension is 20/05/2016. On 16/02/2016: Not corrected. New timeline 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 19 | Panel base plate removed to allow cable entry. | Panel base plate must be installed and cable(s) entering panel must be firmly fixed with cable gland. |  | May 15 2016 | On 18/04/2016: Not Corrected. Time extension is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016: Not corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected On 07/06/2017: Factory sent a CAP where they are asking for 30/06/2017 which is not accepted. Hence corrective action plan shall have to be completed within 15/05/2016 On 17/07/2017: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 20 | High earth loop impedance measured. | Check for loose earthing-connection and take necessary action accordingly. |  | Jul 18 2015 | On 02/09/2015: Corrected. | 10 Weeks | Corrected
Initial Inspection |  | 21 | Cables are not supported. | Cable tray or riser with protective metal cover must be installed to support the generator output cables. |  | Aug 13 2015 | On 16/02/2016: Corrected. | 1 Weeks | Corrected
Initial Inspection |  | 22 | Damaged PVC sanitation pipes used for supporting the power cables | Install covered cable ladder or tray to support and protect cables against weather and possible physical damages. |  | Aug 13 2015 | On 02/09/2015: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 23 | Panel doors not connected with earth bond. | All metal panel doors must have an earth connection of at least 4 rm earth cable. |  | May 19 2015 | On 02/09/2015: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 24 | Generator exciter batteries not encased and its terminals not insulated. | Keep the Batteries inside a metal casing (acid proof) and insulate its terminal by insulating material to protect it from short circuit which may occur due to falling foreign material on it. |  | Jul 31 2015 | On 16/02/2016: Corrected. | 2 Weeks | Corrected
Initial Inspection |  | 25 | Openings in the panel top and base plate. | Every panels’ top and base must be sealed and cable(s) entering panel must be firmly fixed with cable gland. |  | Jun 10 2016 | On 18/04/2016: Not corrected. Timeline is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected On 07/06/2017: Factory sent a CAP where they are asking for 30/06/2017 which is not accepted. Hence corrective action plan shall have to be completed within 10/06/2016 On 17/07/2017: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 26 | Cables termination from bus bars without using washer. | The cables from the bus bars must be terminated using suitable size of washer along with nut and bolt. |  | Jun 15 2015 | On 02/09/2015: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 27 | Ebonite sheet used for cable protection below the panel. | Rigid metallic (checkered plates) must be used for cable protection. |  | May 15 2016 | On 18/04/2016: Corrected. On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 15th April,2016. | 5 Weeks | Corrected
Initial Inspection |  | 28 | Cables entering/exiting the changeover switch are not supported. | Cables must be supported by covered cable- duct throughout its length. |  | Jun 18 2015 | On 16/02/2016: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 29 | Panels do not have earth bus bar (earth strip). | Earth bus bar should be installed inside all panels with earthing connection as per BNBC. |  | Oct 20 2016 | On 18/04/2016: Not corrected. Time extension is given till 10/06/2016. On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Corrected. | 2 Weeks | Corrected
Initial Inspection |  | 30 | Power contactor for the boiler not mounted inside the panel. | Power contactor for the boiler must be fixed on the din rail inside panel. |  | May 19 2015 | On 02/09/2015: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 31 | MCB inside the panel not firmly fixed. | MCB inside the panel must be firmly fixed. |  | May 19 2015 | On 02/09/2015: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 32 | Multiple cable termination in MCCB. Cables connecting to MCB inside panel without cable lugs (typical). | Remove all the multiple cable termination from the MCCB and bus bars must be installed if necessary. |  | May 19 2015 | On 16/02/2016: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 33 | Phase barrier/separator between different phases is not installed (typical). | Phase barrier between different phases supplied by the breaker manufacturer must be installed to avoid arc flashing. |  | Jul 18 2015 | On 16/02/2016: Corrected. | 10 Weeks | Corrected
Initial Inspection |  | 34 | Cables connecting to MCB inside panel without cable lugs. | Cables must be connected to terminals only by soldered/welded lugs according to cable size. |  | Jul 18 2015 | On 16/02/2016: Lugs have been provided where it's necessary. | 5 Weeks | Corrected
Initial Inspection |  | 35 | Openings in the panel door. | Opening in the panel door must sealed to prevent the ingress of lint/dust into the panel. |  | Jun 19 2015 | On 16/02/2016: Corrected. | 10 Weeks | Corrected
Initial Inspection |  | 36 | Control device(s) mounted on wall without enclosures. | MCB (electrical devices) mounted on the wall must be installed with protective enclosures made of metallic sheet of minimum 20 SWG thickness. |  | Jun 15 2015 | On 02/09/2015: Corrected. | 5 Weeks | Corrected
Initial Inspection |  | 37 | Power and control wiring of boiler are carried through flexible PVC pipe. | Use industrial graded (heat resistant) pipe for control and power wiring of boiler. |  | Apr 17 2016 | On 18/04/2016: Corrected. On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 30th April,2016. | 10 Weeks | Corrected
Initial Inspection |  | 38 | The panels are not installed with power indicator LED circuits. | The power indication LED circuit must be incorporated to indicate the existence of the power. |  | Jul 15 2015 | On 02/09/2015: Corrected. | 2 Months | Corrected
Initial Inspection |  | 39 | Cables passing through wall, supported in PVC sanitation pipe not protected and remaining gaps after passage of cables through wall not sealed. | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables preventing any smoke form passing thorough. |  | Jun 19 2015 | On 16/02/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Transformer Arcing horn has not been installed. | Install transformer arcing horn with proper alignment (maintain not less than 2 inch gap between two horns). |  | Apr 15 2016 | On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 15th April,2016. On 18/04/2016:Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 41 | New Finding: Panel/Distribution boxes are not readily accessible. | Take necessary initiative thus every panel/distribution board can be easily accessible. |  | Dec 12 2015 | On 16/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Multiple cables are connected in the bus bar through single lugs. | Each cable must be connected in the bus bar through single lugs. |  | Jan 1 2017 | On 18/04/2016: Not corrected. Time extension is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not Corrected. Multiple cable connected in single point of bus bar. On 02/01/2017: Not Corrected. On 02/04/2017: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: Rain water is dropping inside the generator & substation room. | Put an arrangement to protect the electrical equipment from water. |  | Nov 12 2015 | On 16/02/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: Earthing cable for transformer neutral is inadequate. | Earthing cable for transformer neutral needs to be at least 70 rm. You may use 10mm diameter solid bare copper conductor for neutral earthing. |  | Jun 10 2016 | On 18/04/2016: Not corrected. Time extension is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016 :Not Corrected. On 30/10/2016: Not corrected. Neutral and body earthing are not segregated. On 02/01/2017: Not Corrected. No earthing found at transformer neutral. On 02/04/2017: Not Corrected. On 17/07/2017: Not Corrected. Transformer equipment earthing is also inadequate. On 31/12/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 45 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). |  | Jun 10 2016 | On 18/04/2016: Not corrected. Timeline is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected On 07/06/2017: Factory sent a CAP where they are asking for 30/06/2017 which is not accepted. Hence corrective action plan shall have to be completed within 10/06/2016. On 17/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Cables inside distribution board is disorganized. | Organize all the power cables securely inside distribution board thus no chance of any electrical hazard. |  | Jun 10 2016 | On 18/04/2016: Not corrected. Timeline is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected On 07/06/2017: Factory sent a CAP where they are asking for 30/06/2017 which is not accepted. Hence corrective action plan shall have to be completed within 10/06/2016. On 17/07/2017: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 47 | New Finding: Distribution board/panel is filled with fluffs (lint/dust). | Keep always clean inside all the distribution boards/panels. Seal them properly and ensure adequate ventilation. |  | Aug 30 2016 | On 18/04/2016: Not corrected. Time extension is given till 10/06/2016. On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 15th April,2016. On 18/08/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 48 | New Finding: Wastage water drain in front of panel. | Put a arrangement to provide obstacle for water. Cover the drain or stop discharging waste water through this drain. Access route of the panel shall be free of water. |  | Sep 9 2015 | On 16/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 49 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. |  | Apr 15 2016 | On 18/04/2016: Not corrected. Timeline is 10/06/2016. On 16/02/2016: not corrected. New timeline is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected On 17/07/2017: Not Corrected. On 31/12/2017:Not Corrected. On 03/07/2018:Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 50 | New Finding: Loop connection has used powering multiple MCBs/MCCBs. | Eliminate loop cables; use single cable for each MCBs/MCCBs. You may use bus bar to avoid multiple termination. |  | Nov 12 2015 | On 16/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Flexible PVC pipe has been used inside the panel to cover cables. | Remove all the flexible PVC pipes from inside of the panel. |  | Aug 30 2016 | On 18/04/2016: Not corrected. Time extension is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 52 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Clean all the cable channels/ducts; then cover them (you may use checkered/ perforated plate at the bottom). And after each maintenance, keep record. |  | Aug 30 2016 | On 18/04/2016: Not corrected. Time extension is 10/06/2016. On 16/02/2016: Not corrected. New timeline is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 53 | New Finding: Cables in service are joined (splicing) between terminations. | Joints of cable shall be avoided. For unavoidable cases, existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. |  | Nov 12 2015 | On 16/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 54 | New Finding: Hot spots at terminations inside panel. | Find the cause of excessive heat-rise which may be the overloading, loose connection, unbalanced load and others and take action immediately. Thermo graphic scanning for the entire electrical system must be performed on a bi-annual basis and recorded. |  | Oct 30 2016 | On 18/04/2016: Not corrected. Time extension is given till 10/05/2016. On 16/02/2016: This Issue is not corrected. New timeline to resolve this issue is 15th April,2016. On 18/08/2016: Not Corrected. On 30/10/2016: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 55 | New findings: Cable duct is left open. | Cover it with the electrical graded materials, clean it at certain interval and keep records of cleaning. |  | Oct 30 2016 | On 18/04/2016: Not corrected. Time extension is given till 10/06/2016. On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Corrected. Cleaned and covered. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: There was no permanent identification found at each panel boards. | All distribution boards shall be marked permanently, as the case may be, provided a unique ID number (e.g. MDB-1) . |  | Oct 30 2016 | On 18/08/2016: Not Corrected. On 30/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: No capacity information in electrical panel board. List of circuit or SLD of existing circuits are not available in each electrical panel board. | List of circuit or SLD of existing circuits shall be available for each electrical panel board. |  | May 30 2016 | On 18/08/2016: Not Corrected. On 30/10/2016: Not corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected On 07/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 15/04/2017 On 17/07/2017: Not Corrected. Capacity information is given but SLD is not pasted. On 31/12/2017: Not Corrected. Capacity information is available but still SLD for each panel are not available yet. On 03/07/2018: Not corrected. On 22/01/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 58 | Cables passing through wall/ floor slab are not protected at the entry/ exit point(s). | Cables passing through permanent wall/ floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. |  | Oct 25 2016 | On 18/10/2016: Timeline Extended from 30/09/2016 to 25/10/2016 On 30/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Generator room is not properly seal against water/ rain water. | Take necessary steps to keep generator room free from water/ rain water. |  | Oct 3 2016 | On 30/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Generator output cables (laid on floor) are not protected and supported. Generator output box is not sealed properly. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. |  | Oct 16 2016 | On 30/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Sub station room has inadequate ventilation | Ensure/Arrange cross ventilation sub station room; You may use fire damper if you have to keep any opening on the corridors/ egress path/ exit. |  | Oct 10 2016 | On 30/10/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Cables in service are joint (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. |  | Oct 5 2016 | On 30/10/2016: Corrected. No such issue has found during follow-up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Exposed electrical connection. | Remove that connection and install insulated electrical appliances properly in order to prevent electrical hazard. |  | Oct 18 2016 | On 30/10/2016: Corrected. No such issue has found during follow-up inspection. | 2 Weeks | Corrected
Follow Up Inspection |  | 64 | New Finding: Light in store room/storage areas is uncovered. | Lights in store room / storage areas shall be covered. |  | Oct 17 2016 | On 30/10/2016: Not Corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Corrected | 2 Weeks | Corrected
Follow Up Inspection |  | 65 | New Finding: Looping was observed inside the panel at MCB/ MCCB terminals. | Remove multi looping of wiring/cables at circuit breakers within switchboards and/or distribution boards. |  | Jan 1 2017 | On 30/10/2016: Not Corrected. Multiple cables terminated at MCCB terminals also found. On 02/01/2017: Not Corrected. On 02/04/2017: Corrected. No loop connection found. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Changeover switches have no interlocking capabilities. | There must be an interlock arrangement for protecting electrical system from any electrical fault. |  | Oct 10 2016 | On 30/10/2016: Not Corrected. On 02/01/2017: Not Corrected. On 02/04/2017: Not Corrected On 17/07/2017: Not Corrected. On 31/12/2017: Corrected. 200KVA generator have been removed from this COS. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Transformer Oil Test (dielectric strength test) report is outdated. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. |  | Dec 10 2016 | On 02/01/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Personal Protective Equipment (PPE) for Electrical Work is not available. | Personal Protective Equipment (PPE) must be arranged by the factory management team for the safety of their employee and worker. |  | Dec 10 2016 | On 02/01/2017: Not Corrected. On 02/04/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Power Cables are hanging without support. Cable terminals may be in tension. | Cable tray/ladder must be used to support cables at any where to keep cables out of tension. Outdoor arrangement must be covered. |  | Feb 10 2017 | On 02/04/2017: Not Corrected On 17/07/2017: Not Corrected. On 31/12/2017: Not Corrected. On 03/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Each manually operated machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. |  | Jan 10 2017 | On 02/04/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Indicator lights are mounted without control device. | Indicator lights should be connected by control device such as rated fuse or MCB. |  | Feb 15 2017 | On 02/04/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. |  | Apr 24 2017 | On 17/07/2017: Not Corrected. Thermographic inspection report is outdated. On 31/12/2017: Corrected. | 2 Weeks | Corrected
Follow Up Inspection |  | 73 | New Finding: Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. |  | May 10 2017 | On 07/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 09/05/2017 On 17/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 74 | New Finding: Circuit is drawn from bus bar without any protective means. (For MDB connection from LT panel). | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). |  | May 10 2017 | On 07/06/2017: Factory sent a CAP where they have mentioned that they have completed the work on 15/05/2017 On 17/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Earth Pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. |  | Aug 25 2017 | On 14/11/2017: Factory is asking for 30-Nov-17 which is not accepted. On 31/12/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 76 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. |  | Mar 5 2019 | On 13-Nov-2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: Inadequate working clearance around the transformer(s). | Working clearance around each transformer shall be 1.07m. If multiple transformers are installed then the gap between two transformers must be equal to the width of bigger transformer. |  | May 5 2019 | On 13-Nov-2019: Not Corrected. On 09/12/2020: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 78 | New Finding: Wooden support used for electrical installation/ element. | Replace wooden support and it is preferable to fix each electrical devices with noncombustible support. |  | Mar 5 2019 | On 13-Nov-2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. |  | Jan 1 2020 | On 09/12/2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. |  | Jan 1 2020 | On 09/12/2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. |  | Jan 1 2020 | On 09/12/2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 82 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. |  | Feb 22 2023 | On 09/11/2023: Not Corrected. SLD has been submitted to RSC for review. On 08/05/2024: Not corrected. No progress has been observed. Factory has not submitted SLD to RSC for review yet. On 17/11/2024: Not Corrected. Factory has submitted SLD at RSC. RPO Comments on 23-Apr-2025 : The design documents (SLD) have been reviewed and accepted by RSC on 22-Apr-25. The remediation needs to be competed based on accepted design by 30-Apr-2025. On 21/05/2025: Not Corrected. Factory got their SLD "Accepted" from RSC on 22nd April 2025. 50% progress observed. Mismatches found (Oversized breaker, earthing cable identification missing, inadequate generator earthing, ECC info. missing, individual overload protection missing/oversized, load identification missing, short busbar info. missing, cable identification missing, power socket ampere rating missing, panel incoming breaker missing, equipment identification missing and ELD not as built, few earth pits are not identifiable) as per Accepted SLD. Factory needs to update their drawing with changes form. RPO Comments on 28-Dec-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 83 | New Finding: Lightning Protection System (LPS) is not maintained properly. (Air terminal missing/ Aluminium air terminal installed on copper base etc.) | Periodic maintenance shall be done to maintain LPS. | Done | Jan 22 2023 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 84 | New Finding: Power Cables are hanging without proper support. Power cables entering or exiting from Distribution board/panel are not properly fixed. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. Power cables entering or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). | Done | Jan 22 2023 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 85 | New Finding: Earth lead cable/ Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | Done | Jan 22 2023 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 86 | New Finding: Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Done | Jan 22 2023 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 87 | New Finding: Cable duct/ channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Done | Jan 22 2023 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 88 | New Finding: Electrical distribution box/ panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. | Done | Jan 22 2023 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 89 | New Finding: Oil leakage from transformer has been observed. | Oil leakage from transformer must be stopped and top of transformer must also be kept clean. | Done | Jan 22 2023 | On 09/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 90 | New Finding: PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Done | Dec 20 2023 | On 08/05/2024: Not corrected. Some progress has been observed but still unsafe wiring found in few areas in store room. RPO Comments on 28-Oct-2024 : The factory management reported the remediation completion. This item will be verified in the next inspection. On 17/11/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 91 | New Finding: Transformer Oil Test (dielectric strength test) report is unavailable. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Done | Jun 12 2024 | On 17/11/2024: Not corrected. The oil test report is available but not satisfactory. RPO Comments on 11-Feb-2025 : The factory management reported the remediation completion. This item will be verified in the next inspection On 21/05/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 92 | New Finding: Insulation resistance test of electrical power cables is not performed. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Done | Jun 12 2024 | RPO Comments on 28-Oct-2024 : The factory management reported the remediation completion. This item will be verified in the next inspection. On 17/11/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 93 | New Finding: Outdoor Cable are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. |  | Jul 12 2024 | On 17/11/2024: Not corrected. No progress was observed. RPO Comments on 23-Apr-2025 : Though factory reported this CAP item as completed but based on the observations received from RSC ESE engineer the provided pictorial evidence against this CAP item is insufficient therefore the CAP item will remain in progress & hence the corrective action plan should be completed as per the given recommendation with immediate concern. On 21/05/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 94 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Done | Jun 12 2024 | RPO Comments on 28-Oct-2024 : The factory management reported the remediation completion. This item will be verified in the next inspection. On 17/11/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 95 | New Finding: Inadequate working space around transformer for performing maintenance work. | Adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. Access needs to be restricted to qualified personnel wearing appropriate PPE (Personal Protective Equipment). |  | Jul 21 2025 | RPO Comments on 28-Dec-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 96 | New Finding: Cable channel covers are left open. | Cable channels and ducts must be kept clean and sealed to prevent any ingress of dust and debris. |  | Jun 21 2025 | RPO Comments on 28-Dec-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 97 | New Finding: Cables joint or tapping do not have adequate insulation and mechanical strength. | Cable joints shall be made through porcelain/PVC connectors with PIB tape wound around the joint in respect of conductivity, insulation, and mechanical strength. |  | Jun 21 2025 | RPO Comments on 28-Dec-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 98 | New Finding: Circuit breaker has no capacity information. | Each circuit breaker must be clearly labeled with its capacity information. |  | Jun 21 2025 | RPO Comments on 28-Dec-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 99 | New Finding: Power sockets are hung without support. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200mm above the floor level. |  | Jun 21 2025 | RPO Comments on 28-Dec-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress