## Structural
Date
10-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Sweater Ltd., Sorifpur Road Malekerbari, National University Gazipur, Gazipur
Date of Inspection |  | 2016-09-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Discrepancies between provided drawing and as built condition | Factory Engineer to update the drawings to “as-constructed” status. | Corrected in 4th follow-up inspection by accord on 17 December 2018. | Feb 15 2017 | On 27/09/2017: This issue is going to be covered in DEA. Factory is required to submit DEA report to ACCORD. On 18/04/2018: This issue is related to DEA .Factory submitted DEA to Accord on 17-04-2018 .DEA is currently under Accord review . On 22/10/2018: A set of as-built drawing was prepared along with DEA. Factory has submitted DEA to ACCORD which is currently under review. On 17/12/2018: As-built drawing has been prepared along with DEA. During inspection, as-built drawing was found satisfactory as per on site condition. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. As-built drawings was prepared as part of DEA which was accepted from ACCORD on 26/11/2018. On 22-September-2019: Corrected in previous follow up inspection. As built drawings were prepared as a part of DEA. Factory got DEA acceptance from ACCORD on 26-November-2018. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. | Within 6-weeks | Corrected
Initial Inspection |  | 2 | Discrepancies between provided drawing and as built condition | Building engineer to investigate the whole building and Conduct Engineering Assessment (EA ) especially for foundation. | Corrected We also submit the core layout plan and clarification certificate by attached pictureal avidance. | Feb 15 2017 | On 27/09/2017: This issue is going to be covered in DEA. Factory is required to submit DEA report to ACCORD. On 18/04/2018: This issue is related to DEA .Factory submitted DEA to Accord on 17 -04-2018 .DEA is currently under Accord review . On 22/10/2018: Factory has submitted DEA to ACCORD which is currently under review. On 17-Dec-2018: Factory has prepared DEA and submitted to ACCORD which was accepted on 26th November 2018. During inspection, extra cores were found at GF grid D/6 and 3F column c26, c20 which were not found in test report. Factory is required to provide clarification regarding these extra cores. On 02/07/2019: Factory has not prepared any documents regarding this issue. Factory is required to revise the core layout plan and a clarification regarding extra cores. On 22-September-2019: This issue had been covered in DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. Cylinder & rebar test reports were also available onsite. In addition, factory had revised core layout and a clarification letter also provided for extra core. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. | Within 6-weeks | Corrected
Initial Inspection |  | 3 | Discrepancies between provided drawing and as built condition | Implement remedial work if necessary. | Corrected Retrofitting work has been completed. | May 30 2017 | On 27/09/2017: This issue is going to be covered in DEA. Factory will implement remedial work after receiving acceptance from ACCORD if required. On 18/04/2018: This issue is related to DEA .Factory submitted DEA to Accord on 17 -04-2018 .DEA is currently under Accord review . Factory is required to carry out remedial works as per recommendation from accepted DEA . On 22/10/2018: Factory has submitted DEA to ACCORD which is currently under review. After DEA acceptance, factory is required to carry out remedial works (if necessary). On 17-Dec-2018: DEA was accepted on 26th November 2018. As per accepted DEA, factory is required to carry out remediation. During inspection, 2nos footing retrofitting works were found on going. Factory is required to complete the remediation within 10th March 2019. On 02/07/2019: DEA of the factory was accepted from ACCORD on 26/11/2018. As per recommendation of accepted DEA, factory required footing, grade beam, column and beam strengthening. Factory was required to complete all the remediation works within 10/03/2019. During inspection, it was observed that retrofitting works were on going. Factory is required to complete remediation works as soon as possible. On 22-September-2019: This issue had been covered in DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. Cylinder & rebar test reports were also available onsite. QC certificate was also kept onsite. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. | within 6-months | Corrected
Initial Inspection |  | 4 | Excessive column stresses in fully completed building (6 storeys) | Any extensions or modifications of the existing building needs to be carryout Details Engineering assessment by a Structural Engineer and in full compliance with the BNBC provision. | Corrected in 4th follow-up inspection by accord on 17 December 2018. | May 30 2017 | On 27/09/2017: This issue is going to be covered in DEA. In case of any extensions, factory is required to carry out detail engineering assessment in full compliance with the BNBC provision. On 18/04/2018: This issue is related to DEA .Factory submitted DEA to Accord on 17 -04-2018 .DEA is currently under Accord review . For any extension case ,factory is required to carry out DEA as per BNBC and submit to Accord . On 22/10/2018: Factory has submitted DEA to ACCORD which is currently under review. If they go for any vertical extension, factory is required to carry out DEA as per BNBC. On 17-Dec-2018: Factory management has provided a consent letter for not going any further vertical extension. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. Factory provided a consent letter against any further vertical extension. On 22-September-2019: Corrected in previous follow up inspection. Factory got DEA acceptance from ACCORD on 26-November-2018. Factory had provided a consent letter where it was mention that they will not go for any further vertical extension. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. No extension was found. The building is currently 5 storied. | within 6-months | Corrected
Initial Inspection |  | 5 | Cracks on 3 rd floor slab. | Building engineer to check the crack and analyze the slab capacity considering the crack. | Corrected in 4th follow-up inspection by accord on 17 December 2018. | Feb 15 2017 | On 27/09/2017: Factory has not taken any step regarding issue. During inspection, cracks were observed at 3rd floor slab and beam. On 18/04/2018: Cracks were found during inspection .Factory is required to repair the cracks with proper suitable method as per recommendation from factory engineer .Factory is required to produce crack investigation report. On 22/10/2018: During inspection, cracks were found in slab which were not repaired. Factory is required to prepare crack investigation report and submit to ACCORD. Also repair the cracks as per recommendation On 17-Dec-2018: Factory has prepared crack investigation report along with DEA which was accepted on 26th November 2018. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. Factory prepared crack investigation report with DEA which was accepted on 26/11/2018. On 22-September-2019: Corrected in previous follow up inspection. During inspection factory had provided a crack investigation report which was accepted on 26-November-2018. Cracks were found repaired at the time of inspection. On 06-January-2020: Corrected in previous follow up inspection. During inspection factory had provided a crack investigation report which was accepted on 26-November-2018. Cracks were found repaired at the time of inspection. Factory management needs continuous monitoring regarding these crack. On 06-Jan-2025: Corrected previously. (See CAP item-18). | Within 6-weeks | Corrected
Initial Inspection |  | 6 | Cracks on 3 rd floor slab. | Carry out remedial works resulting from engineering assessment . | Corrected, We have repaing the Cracks | May 30 2017 | On 27/09/2017: Factory has not taken any step regarding issue. During inspection, cracks were observed at 3rd floor slab and beam. On 18/04/2018: Cracks were found during inspection .Factory is required to repair the cracks with proper suitable method as per recommendation from factory engineer .Factory is required to produce crack investigation report On 22/10/2018: During inspection, cracks were found in slab which were not repaired. Factory is required to prepare crack investigation report and submit to ACCORD. Also repair the cracks as per recommendation On 17-Dec-2018: DEA was accepted on 26th November 2018. As per accepted DEA, factory is required to carry out remediation. Cracks are required to be repaired as per crack investigation report. During inspection, cracks were found at beam in several floors. On 02/07/2019: Factory has not repaired those cracks yet. On 22-September-2019: During inspection factory had provided a crack investigation report which was accepted on 26-November-2018. Cracks were found repaired at the time of inspection. On 06-January-2020: Corrected in previous follow up inspection. During inspection factory had provided a crack investigation report which was accepted on 26-November-2018. Cracks were found repaired at the time of inspection. Factory management needs continuous monitoring regarding these crack. On 06-Jan-2025: Corrected previously. (See CAP item-18). | within 6-months | Corrected
Initial Inspection |  | 7 | Overloaded storage areas | The quantity of the stored materials must be reduced up to 2KPa. | Corrected we have reduced live load and maintaing load plan for 2 Kpa | Feb 15 2017 | On 27/09/2017: During inspection, loads were observed above 2 KPa at 1st & 2nd floor. Factory is required to reduce loads up to 2 KPa. On 18/04/2018: During inspection ,over loading was found in several area. Factory is required to maintain load below 2kpa before acceptance of DEA . On 22/10/2018: Load plans were prepared along with DEA which is currently under review. Factory is required to reduce the load from bonded ware house up to 2 kpa till DEA acceptance. During inspection, floor loading was found below 42psf except storage area. On 17-Dec-2018: A set of load plan has been prepared along with DEA which was accepted on 26th November 2018. During inspection, floor loading was found below the allowable limit of existing load plan (42psf) except storage area. Factory is required to maintain final load plan after completing all the remedial works as per DEA recommendation. On 02/07/2019: Load plan has been prepared as part of DEA which was accepted from ACCORD on 26/11/2018. As per recommendation of accepted DEA, factory required footing, grade beam, column and beam strengthening. Factory has not completed all the remediation works yet. During inspection, floor loading was found below 2 kPa except storage area (Around 5kPa). Factory is required to maintain final load plan after completing all the remedial works. On 22-September-2019: Load plan had been prepared as a part of DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. Cylinder & rebar test reports were also available onsite. QC certificate was also kept onsite. However, load plan was found posted to each floor and overall loading was found below 2 kPa. On 06-January-2020: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. Cylinder & rebar test reports were also available onsite. QC certificate was also kept onsite. However, load plan was found posted to each floor and overall loading was found below 2 kPa. On 06-Jan-2025: Corrected previously. Load plan was found posted to each floor and overall loading was found below the load limit (2 kPa for typical floor, 5 kPa for storage area). | Within 6-weeks | Corrected
Initial Inspection |  | 8 | Overloaded storage areas | Building Engineer to prepare a Load Plan for each level | Corrected Retrofitting work has been completed. | Feb 15 2017 | On 27/09/2017: This issue is going to be covered under DEA. Factory is required to produce a load plan in accordance with ACCORD standard. During inspection, loads were observed above 2 KPa at 1st & 2nd floor. Factory is required to reduce loads up to 2 KPa. On 18/04/2018: Load plan has been prepared as a part of DEA .Factory submitted DEA to Accord on 17 -04-2018 .DEA is currently under Accord review . Heavy loading was found in several areas. On 22/10/2018: Load plans were prepared along with DEA which is currently under review. Factory is required to maintain existing load plan till DEA acceptance. During inspection, floor loading was found below 42psf except storage area. On 17/12/2018: A set of load plan has been prepared along with DEA which was accepted on 26/11/2018. During inspection, floor loading was found below the allowable limit of existing load plan (42psf) except storage area. Factory is required to maintain final load plan after completing all the remedial works as per DEA recommendation. On 02/07/2019: Load plan has been prepared as part of DEA which was accepted from ACCORD on 26/11/2018. As per recommendation of accepted DEA, factory required footing, grade beam, column and beam strengthening. Factory has not completed all the remediation works yet. During inspection, floor loading was found below 2 kPa except storage area (Around 5kPa). Factory is required to maintain final load plan after completing all the remedial works. On 22-September-2019: Load plan had been prepared as a part of DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. However, load plan was found posted to each floor and overall loading was found below 2 kPa. On 06-January-2020: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. Cylinder & rebar test reports were also available onsite. QC certificate was also kept onsite. However, load plan was found posted to each floor and overall loading was found below 2 kPa. On 06-Jan-2025: Corrected previously. Load plan was found posted to each floor and overall loading was found below the load limit (2 kPa for typical floor, 5 kPa for storage area). | Within 6-weeks | Corrected
Initial Inspection |  | 9 | Overloaded storage areas | Reduce loading to the recommendations of the loading plans | Corrected Retrofitting work has been completed. | May 30 2017 | On 27/09/2017: This issue is going to be covered under DEA. Factory is required to produce a load plan in accordance with ACCORD standard. During inspection, loads were observed above 2 KPa at 1st & 2nd floor. Factory is required to reduce loads up to 2 KPa. On 18/04/2018: During inspection ,over loading was found in several area. Factory is required to maintain load below 2kpa before acceptance of DEA . After acceptance of DEA ,factory is required to follow accepted load plan . On 22/10/2018: Overloading was found in the storage area. Factory is required to maintain existing load plan (42psf) till DEA acceptance. On 17/12/2018: A set of load plan has been prepared along with DEA which was accepted on 26th November 2018. During inspection, floor loading was found below the allowable limit of existing load plan (42psf) except storage area. Factory is required to maintain final load plan after completing all the remedial works as per DEA recommendation. On 02/07/2019: Load plan has been prepared as part of DEA which was accepted from ACCORD on 26/11/2018. As per recommendation of accepted DEA, factory required footing, grade beam, column and beam strengthening. Factory has not completed all the remediation works yet. During inspection, floor loading was found below 2 kPa except storage area (Around 5kPa). Factory is required to maintain final load plan after completing all the remedial works. On 22-September-2019: Load plan had been prepared as a part of DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. However, load plan was found posted to each floor and overall loading was found below 2 kPa. On 06-January-2020: Corrected in previous follow up inspection. Load plan had been prepared as a part of DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. Cylinder & rebar test reports were also available onsite. QC certificate was also kept onsite. However, load plan was found posted to each floor and overall loading was found below 2 kPa. On 06-Jan-2025: Corrected previously. Load plan was found posted to each floor and overall loading was found below the load limit (2 kPa for typical floor, 5 kPa for storage area). | Within 6-months | Corrected
Initial Inspection |  | 10 | Water ponding on roof slab. | Provide proper drainage and water proofing layer with appropriate water proofing materials. | Corrected we have repaired roof top drainage related issue | Feb 15 2017 | On 27/09/2017: Waterproofing layer with proper drainage system has not been provided yet. On 18/04/2018: Water proofing was not provided on rooftop .Factory is required to provide water proofing on rooftop with sufficient drainage system . On 22/10/2018: Water proofing was not provided yet. Factory is required to provide water proofing with proper drainage system. On 17-Dec-2018: Water drainage system has been provided at roof top. No water ponding was found. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. No water ponding was found. On 22-September-2019: Corrected in previous follow up inspection. Water proofing layer was seen and no water ponding was found. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. No water ponding was found. | Within 6-weeks | Corrected
Initial Inspection |  | 11 | Lack of edge protection of stair case | Provide edge protection as per suggestion of building engineer | Corrected we have provided hand railing to resolve this issue | Feb 15 2017 | On 27/09/2017: During inspection, edge protection at roof level was observed. On 18/04/2018: This issue corrected in previous follow-up inspection . On 22/10/2018: Edge protection has been provided. On 17-Dec-2018: Edge protection has been provided. Issue remains corrected. On 02/07/2019: This issue has been corrected as per 1st follow up inspection. Edge protection was provided. On 22-September-2019: Corrected in previous follow up inspection. Edge protection was provided. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. Edge protection was provided. | Within 6-weeks | Corrected
Initial Inspection |  | 12 | Dampness and water ingress through slab and walls | Factory Engineer to inspect water damaged structures and repair with a suitable methods. | Corrected . This issue completed by our factory team | May 30 2017 | On 27/09/2017: No step has been taken concerning this issue. During inspection, dampness was observed at several locations. On 18/04/2018: Dampness observed in several locations .Factory is required to repair the damaged area with proper suitable method . On 22/10/2018: Dampness was not repaired yet. On 17-Dec-2018: During inspection, dampness was found at toilet zone adjacent wall. Factory is required to repair those water ingress damage. On 02/07/2019: During inspection, dampness was found at several locations. Factory is required to repair water damage. On 22-September-2019: During inspection dampness was found in several facade wall including toilet zone. Factory is required to take proper initiative regarding this issue. On 06-January-2020: Factory management had repaired those dampness from toilet areas. During inspection dampness not found. On 06-Jan-2025: Corrected previously. Factory has repaired the dampness. | Within 6-months | Corrected
Initial Inspection |  | 13 | Discrepancy between value of boring log and value used in bearing capacity calculation of soil. | Factory engineer to revise the soil test report and assess the adequacy of all foundations considering the corrected bearing capacity. | Corrected in 4th follow-up inspection by accord on 17 December 2018. | Feb 15 2017 | On 27/09/2017: This issue is going to be covered in DEA. Factory is required to submit DEA report to ACCORD. On 18/04/2018: This issue is related to DEA .Factory submitted DEA to Accord on 17 -04-2018 .DEA is currently under Accord review . On 22/10/2018: Factory has submitted DEA to ACCORD which is currently under review. On 17-Dec-2018: DEA was accepted on 26th November 2018. Soil test report was incorporated with DEA. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. On 22-September-2019: Corrected in previous follow up inspection. DEA was accepted on 26th November 2018. Soil test report was incorporated with DEA. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. | Within 6-weeks | Corrected
Initial Inspection |  | 14 | Discrepancy between value of boring log and value used in bearing capacity calculation of soil. | Implement remedial work if necessary | Corrected Retrofitting work has been completed. | May 30 2017 | On 27/09/2017: This issue is going to be covered in DEA. Factory will implement remedial work after receiving acceptance from ACCORD if required. On 18/04/2018: This issue is related to DEA .Factory submitted DEA to Accord on 17 -04-2018 .DEA is currently under Accord review . Factory is required to carry out remedial works as per recommendation from accepted DEA . On 22/10/2018: Factory has submitted DEA to ACCORD which is currently under review. After DEA acceptance, factory is required to carry out remedial works (if necessary). On 17-Dec-2018: DEA was accepted on 26th November 2018. As per accepted DEA, factory is required to carry out remediation. During inspection, 2nos footing retrofitting works were found on going. Factory is required to complete the remediation within 10th March 2019. On 02/07/2019: DEA of the factory was accepted from ACCORD on 26/11/2018. As per recommendation of accepted DEA, factory required footing, grade beam, column and beam strengthening. Factory was required to complete all the remediation works within 10/03/2019. During inspection, it was observed that retrofitting works were on going. Factory is required to complete remediation works as soon as possible. On 22-September-2019: This issue had been covered in DEA report. Factory got DEA acceptance from ACCORD on 26-November-2018. During inspection it was found that factory had completed retrofitting works as per DEA recommendation. Cylinder & rebar test reports were also available onsite. QC certificate was also kept onsite. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. | Within 6-months | Corrected
Follow Up Inspection |  | 15 | New finding-1: Wall crack at ground floor | Engage a qualified structural engineer to confirm the causes of such distress and suggest appropriate remedial measures. | Corrected in 4th follow-up inspection by accord on 17 December 2018. | Oct 4 2017 | On 27/09/2017: During inspection, horizontal wall crack was observed at ground floor near gas meter room. Factory is required to investigate the crack and develop a remediation plan as suggested. On 18/04/2018: Wall cracks were observed .Factory is required to repair the crack with suitable method . On 22/10/2018: Wall cracks were repaired by removing plaster. On 17-Dec-2018: Wall cracks were repaired. Issue remains corrected. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. On 22-September-2019: Corrected in previous follow up inspection. During inspection wall crack was not seen. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. Factory has repaired crack on wall. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 16 | New finding-2: Exposed rebar at rooftop | For both durability and serviceability, rust proof paint or any appropriate method is recommended. | Corrected in 4th follow-up inspection by accord on 17 December 2018. | Nov 8 2017 | On 27/09/2017: During inspection, exposed rebar was observed at rooftop. Factory is required to provide rust proof paint or any suitable method regarding this issue. On 18/04/2018: Exposed rebars were observed on rooftop .Factory is required to provide rust proof paint on the rebars . On 22/10/2018: Exposed rebars were found painted. On 17-Dec-2018: Exposed rebars were painted. Issue remains corrected. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. On 22-September-2019: Corrected in previous follow up inspection. During inspection exposed rebars were found painted. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. Factory has provided rust proof paint. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 17 | New Findings-3: Undocumented shed at roof top | Building Engineer is required to incorporate the non-engineered shed in Design report | Corrected in 4th follow-up inspection by accord on 17 December 2018. | Dec 3 2018 | On 22/10/2018: During inspection, undocumented shed was found which was non-engineered and used as storage area. Factory is required to incorporate the shed in as-built drawing and analysis report and submit to ACCORD. On 17-Dec-2018: Factory has demolished the roof shed. On 02/07/2019: This issue has been corrected as per 4th follow up inspection. On 22-September-2019: Corrected in previous follow up inspection. Roof top shed had been demolished. On 06-January-2020: Corrected in previous follow up inspection. Same as earlier comment. On 06-Jan-2025: Corrected previously. Roof shed was demolished. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 18 | New Findings-4: Hairline crack on slab soffits at roof and 4th floor slab (Main Factory Building). | The building engineer to investigate the cracked area and repair it with a suitable method. | Corrected, We already repair all cracked area. | Feb 18 2025 | On 06-Jan-2025: During inspection hairline crack was found on slab soffits at roof and 4th floor slab (Main Factory Building). The building engineer to investigate the cracked area and repair it with a suitable method. RPO Comments: On 18-Mar-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 19 | New Findings-5: Non-structural storage racks found not anchored/braced (Main Factory Building). | Anchor/brace non-structural storage racks. | Corrected, We already provide Anchor/brace for non-structural storage racks. | Jun 6 2025 | On 06-Jan-2025: During inspection non-structural storage racks found not anchored/braced (Main Factory Building). The building engineer is required to anchor/brace non-structural storage racks. RPO Comments: On 18-Mar-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 months) | Pending Verification
Follow Up Inspection |  | 20 | New Findings-6: Undocumented structure in factory premises (Generator Shed-single storied shed-area 120 sft , Parking Shed-single storied shed-1000 sft, ETP-Shed over a single storied RC platform-area-240 sft). Generator Shed: Lack of as-built drawing. Unclear load path and inadequate member size (column). | For the Generator Shed, the building engineer is required to produce as-built drawing. Also, check the load path and member adequacy, propose a remediation plan and submit to RSC for review. | We have prepared an as-built drawing for the Generator shed and submitted it for RSC review. | Feb 18 2025 | On 06-Jan-2025: During inspection, undocumented structures were found in factory premises (Generator Shed-single storied shed-area 120 sft , Parking Shed-single storied shed-1000 sft, ETP-Shed over a single storied RC platform-area-240 sft). Generator Shed: Lack of as-built drawing. Unclear load path and inadequate member size (column). For the Generator Shed, the building engineer is required to produce as-built drawing. Also, check the load path and member adequacy, propose a remediation plan and submit to RSC for review. RPO Comments: On 9-Nov-2025: The factory is asking for an timeline extension which is not accepted. The design documents EA pending to be submitted to RSC. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 21 | New Findings-7: Undocumented structure in factory premises (Generator Shed-single storied shed-area 120 sft , Parking Shed-single storied shed-1000 sft, ETP-Shed over a single storied RC platform-area-240 sft). Parking Shed, ETP shed: Lack of as-built drawing. | Parking Shed and ETP shed: The building engineer is required to produce as-built drawing and keep on site. | We have prepared the parking & ETP shed as-built drawing, which are stored on the side. | Feb 18 2025 | On 06-Jan-2025: No as-built drawing was available on site for Parking Shed and ETP shed. The building engineer is required to produce as-built drawing and keep on site. RPO Comments: On 9-Nov-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 22 | New Findings-8: Corrosion on roof sheet (Generator Shed). | Provide rust-proof paint on the roof sheet. | Once the above tasks are complete, we will paint all parking lots & ETP sheds. | Feb 18 2025 | On 06-Jan-2025: During inspection corrosion was observed on the roof sheet (Generator Shed). Provide rust-proof paint on the roof sheet. RPO Comments on 9-Nov-2025:The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress

## Fire
Date
10-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Sweater Ltd., Sorifpur Road Malekerbari, National University Gazipur, Gazipur
Date of Inspection |  | 2016-09-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Exit stairs are not separated from work areas & other spaces on each floor by fire-rated construction due to unprotected openings and penetrations. | Separate the exit stairs from work areas and other building spaces on all floor levels by minimum 2- hr fire-rated construction. Provide minimum 1.5- hr fire rated doors and seal all unprotected openings and penetrations to maintain the fire separation. Ensure that all fire doors are self-closing and positive latching, and are provided with fire exit (panic) hardware where serving production floors or assembly occupancies. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Corrected All fire Doors are corrected with functional adjustment. | Jan 31 2017 | On 22/09/2019: Unprotected opening was found in exit stair enclosure. Moreover, gap below fire door shall not be exceed maximum allowable limit (19 mm). On 6-1-2020: Some of the fire doors require functional adjustment. On 04/03/2020 (Special Inspection): Not Corrected. Fire wall constructed properly, fire rated doors are installed at every required exit but all the doors were found open using external objects. Factory has provided magnetic door open holder device but interfacing facility was not active during inspection as the fire alarm system was not functional properly. On 26/08/2021: Corrected based on site conditions. Both stairs are separated from production floors by fire rated construction and fire rated doors. The factory has provided automatic-closing devices tied to the fire alarm system ( panel was functional during FUI). On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Egress gates on the all floor with locking features are provided at all exits & exit discharge. | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking features complying with ACCORD | Corrected We have removed locking feature | Dec 10 2016 | On 13/February/2018: Corrected Note: No visible non-compliant locking provisions were not observed during the 3rd FUI. Factory management is now keeping the exit discharge doors open all the time. Factory management may utilize push-bar at installed doors for their security purpose. On 09/10/2018: Corrected On 04/02/2019: Corrected. On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 3 | Storage on the second floor and fourth floor is not separated by a minimum 1-hr fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected in 4th Follow up inspection. | Jan 31 2017 | On 13/February/2018: Dedicated store room (Bonded warehouse) was found on 2nd Floor. Required civil work is done for bonded warehouse. As soon as fire doors will be in-housed, factory management shall install fire door at the bonded ware house room. On 09/10/2018: Corrected On 04/02/2019: Corrected. 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected we have properly seal all penetrations. | Jan 31 2017 | On 13/February/2018: Due to the electrical wiring, unsealed penetration & opening were present at the stair-01. Moreover, due to the newly installed DB on all floors, floor to floor penetration was present on all floor levels. On 09/10/2018: Same as before. On 04/02/2019: In progress. On 22/09/2019: Work is in progress. Opening was found unsealed in exit stair enclosure. Moreover, floor to floor penetration due to electrical riser shall be sealed properly. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | The boiler room and substation room on the ground floor is not separated by fire-rated construction. | Separate the boiler and sub-Station room by a minimum 2-hr fire-rated construction. Seal and/or protect all openings to maintain the required fire separations. Provide proper ventilation and consult a qualified engineer. If applicable: When located to the exterior of a building, separate the boiler by a minimum distance of 3m (10 ft). | Corrected Fire Rated door has been installed | Jan 31 2017 | On 13/February/2018: Boiler room & Switch room is present on Ground floor level. Required civil work is done at the boiler room. On 09/10/2018: Same as before On 04/02/2019: In progress. On 22/09/2019: Boiler or On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3months | Corrected
Initial Inspection |  | 6 | Collapsible gates, sliding doors and roll down shutter type doors are provided at the building exits, exit stairs, along egress routes and exit discharge. | Replace all gates, sliding Doors and rolling shutters along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected We have removed collapsible gate by installed sewing type gate | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected. On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected as per previous FUI. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 7 | Liquefied or compressed gas cylinders were located within the factory. | The storage or use of liquefied or compressed flammable gas cylinders shall be prohibited within the factory. | Corrected We have relocated the liquefied or compressed gas cylinder out site the building | Jan 15 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected. On 22/09/2019: Corrected. Not found. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. Not found during inspection. On 19/10/2022: Corrected. Not found during inspection time. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 8 | The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed automatic fire alarm system in accordance with NFPA 72 and ACCORD standards. | Corrected, We have installation a automatic fire alarm system as per RSC standards. | Feb 20 2017 | On 04/02/2019: T&Cx is pending. On 22/09/2019: Factory has informed that installation of the system almost completed. T&C is pending. On 6-1-2020: The system is not ready for final T&C verification. On 04.03.2020 (Special Inspection): Not Checked. 0n 25-March-2020: Factory mentioned that they have installed the FADS. On 26/08/2021: The FADS was functional and there was no fault signal. The factory has submitted an as-built drawing and necessary documents to the RSC on 21 May 2021 and awaiting Pre-T&C on site. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: FACP was found functional and free of abnormal condition. Factory is planning to start the modification work. On 19/10/2022: Factory management claimed that they have completed all the necessary modification work after the last Pre-T&C conducted on 30 May 2022. Additionally they committed to apply for further Pre-T&C very soon. On 26/06/2024: Pre-T&CVI was conducted & it was found that the factory is not ready for T&CVI. See the details in the Pre-T&CVI report. On 06-Nov-24: Modification work after last Pre T&C is on going. Reportedly, factory will submit the drawing & documents to RSC within 1st Dec 2024. On 29-Oct-25: Pre-T&CVI has been conducted and it was found that factory is ready for T&CVI. See the details in the Pre-T&CVI report. On 28-Jan-26: T&CVI has been conducted and the system is approved. See the details in the T&CVI report. | Design within 4 months install within 9 months | Corrected
Initial Inspection |  | 9 | Inspection, testing and maintenance of the automatic fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the automatic fire alarm system and keep written records on- site, in accordance with NFPA 72 (after installation). | Corrected. We are waiting for the RSC final T&CVI. | Jan 24 2017 | On 04/03/2020 (Special Inspection): Not Corrected. Fire alarm system installation complete a format of checklist found available and filled but it was improper. Moreover, the fire alarm system was not functional properly during inspection and the FACP was faulty. Factory is required to maintain the fire alarm system functional as per standard and follow checklist Table-14.3.1 of NFPA-72. On 26/08/2021: It is an integrated part of FADS. The FADS was functional and there was no fault signal. The factory has submitted an as-built drawing and necessary documents to the RSC on 21 May 2021 and awaiting Pre-T&C on site. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: It is an integrated part of FADS. FACP was found functional and free of abnormal condition. Factory is planning to start the modification work. On 19/10/2022: It is an integrated part of fire alarm system. On 26/06/2024: Pre-T&CVI was conducted & it was found that the factory is not ready for T&CVI. See the details in the Pre-T&CVI report. On 06-Nov-24: It is an integrated part of fire alarm system. On 29-Oct-25: Corrected. Factory is maintaining ITM of FADS as per recommendation. | Within 1 month | Corrected
Initial Inspection |  | 10 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the building, tied into the fire alarm system, in accordance NFPA 72 and ACCORD standards. | Corrected, We provide an automatic fire alarm Detection system as per RSC standards. | Jan 28 2017 | On 13/February/2018: Factory management has started the required wiring for installation of detectors On 09/10/2018: Integrated part On 04/02/2019: In progress. On 22/09/2019: It is an integrated part of fire alarm system. On 6-1-2020: The system is not ready for final T&C verification. On 04.03.2020 (Special Inspection): Not Checked. 0n 25-March-2020: Factory mentioned that they have installed the FADS. On 26/08/2021: The FADS was functional and there was no fault signal. The factory has submitted an as-built drawing and necessary documents to the RSC on 21 May 2021 and awaiting Pre-T&C on site. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: FACP was found functional and free of abnormal condition. Factory is planning to start the modification work. On 19/10/2022: Factory management claimed that they have completed all the necessary modification work after the last Pre-T&C conducted on 30 May 2022. Additionally they committed to apply for further Pre-T&C very soon. On 26/06/2024: Pre-T&CVI was conducted & it was found that the factory is not ready for T&CVI. See the details in the Pre-T&CVI report. On 06-Nov-24: It is an integrated part of fire alarm system. On 29-Oct-25: The issue is part of the integrated fire alarm system and has already been addressed under CAP-8. As the system is currently in the verification stage (Pre-T&C phase), the issue is considered resolved. | Design within 4 months install within 9 months | Corrected
Initial Inspection |  | 11 | The existing building has an occupied floor greater than 10m (33 ft) and is not provided with standpipe system. | Provide standpipe system protection throughout the building in accordance with NFPA 14 and ACCORD standards. | Corrected, We provide a standpipe system as per RSC standard. | Jan 28 2017 | On 04/02/2019: No action has not been taken since last follow-up inspection. On 22/09/2019: Factory has informed that installation of the system almost completed. T&C is pending. On 6-1-2020: The system is not ready for final T&C verification. On 04.03.2020 (Special Inspection): Not Checked. 0n 25-March-2020: Factory mentioned that they have installed the SUPS.. On 26/08/2021: The SUPS was active. The factory has submitted an as-built drawing and necessary documents to the RSC on 21 May 2021 and awaiting Pre-T&C on site. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Factory is planning to start the modification work. On 19/10/2022: Factory management claimed that they have completed all the necessary modification work after the last Pre-T&C conducted on 30 May 2022. Additionally they committed to apply for further Pre-T&C very soon. On 26/06/2024: Pre-T&CVI was conducted & it was found that the factory is not ready for T&CVI. See the details in the Pre-T&CVI report. On 06-Nov-24: Modification work after last Pre T&C is on going. Reportedly, factory will submit the drawing & documents to RSC within 1st Dec 2024. On 29-Oct-25: Factory has worked on the modifications recommended in the Pre-T&CVI report. Updated as-built design & documents have been submitted to the RSC for Pre-T&C on 22-Oct-2025, which is under review. System was found in active condition during inspection. | Design within 3 months install within 6 months | In Progress
Initial Inspection |  | 12 | Inspection, testing and maintenance of the fire pump system is not in | Inspect, test and maintain the fire pump system and keep written records on- site, in accordance with NFPA 20 (after installation). | Corrected. We are waiting for the RSC final T&CVI. | Jan 30 2017 | On 04/02/2019: Integrated part of Fire fighting system On 22/09/2019: Not started yet. On 6-1-2020: The system is not ready for final T&C verification. On 04/03/2020 (Special Inspection): Not Corrected. Fire pump installation complete. A checklist of inspection, testing & maintenance was shown during inspection but not properly filled. Moreover, pump room found flooded during inspection. On 26/08/2021: It is an integrated part of SUPS. The factory has submitted an as-built drawing and necessary documents to the RSC on 21 May 2021 and awaiting Pre-T&C on site. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: It is an integrated part of SUPS. Factory is planning to start the modification work. On 19/10/2022: It is an integrated part of fire protection system. On 26/06/2024: Pre-T&CVI was conducted & it was found that the factory is not ready for T&CVI. See the details in the Pre-T&CVI report. On 06-Nov-24: It is an integrated part of fire protection system. On 29-Oct-25: It is an integrated part of fire protection system. | Within 1 month | In Progress
Initial Inspection |  | 13 | Egress door serving 50 or more occupants but does not swing in the direction of egress travel At ground floor. | Modify swing direction of egress doors to the direction of egress travel. | We will modify the Doors swing direction to the direction of egress travel in accordance to accord guideline | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 14 | The width of egress aisles is less than 36-in at different floors. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m(36 in) | Corrected We have provided Clear 36" Aisles | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Refer to issue no: 31. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 15 | Handrails are not provided on both sides of both exit stairs. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | We will provide 36" height railing in both exit stair and will be completed with in 15/08/2017 | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | Occupiable roof is not provided with an adequate parapet / guard rail. | All occupiable roofs shall be provided with parapets or guards with a minimum height of 1067 mm (42 in.) | Corrected parapet wall have been constructed according to BNBC and Accord standard 42" | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 17 | Storage was located in the all exit stairs. | Remove all storage from exit stairs. | Corrected we have removed all storage from stair | Dec 10 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected as per previous FUI. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 18 | Fire evacuation maps is not posted at the entrance of the exits stairs of the building. | Fire evacuation maps shall be posted at the entrance to each exits and exit stairs. | Fire Evacuation map have been posted | Jan 30 2017 | On 13/February/2018: Provided On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected as per previous follow-up. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 19 | Egress aisles and egress paths were blocked and obstructed by storage. | Remove all storage from egress aisles and paths. Keep egress paths and stairs clear of storage. | Corrected We have cleared the egress aisles and egress path. | Jan 5 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected on previous follow-up. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 20 | Electrical panels are located inside the exit stairwell on ground floor. | Remove all electrical panels from the exit stairwells. | Corrected in 4th Follow up inspection on 9th October 2018 | Jan 30 2017 | On 13/February/2018: Changeover Switch has ben removed from the exit stair but electrical wiring was present on all floor level at Exit stair -01 On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Refer to issue no: 32. On 6-1-2020: Refer to issue no: 32. On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 21 | Exit signage not illuminated (burned out, broken, etc.). | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs. The source of illumination shall provide not less than 50 lux at the illuminated surface with a contrast of not less than 0.5.Approved self-luminous signs which provide evenly illuminated letters having a minimum luminance of 0.2 cd/m2 may also be used. | Corrected we have replaced broken / brunt out exit signage by new one | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected, | Within 1 months | Corrected
Initial Inspection |  | 22 | Directional exit signage were provided at south exit doors which indicating exits where none existed. | Provide exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel where a change of direction is not obvious. Remove directional exit signs From the exit doors and insure that lighted exit signs are only visible from the side that directs people toward an exit path. | Corrected we have provided Exit signage in proper position. | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected as per previous follow-up. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected as per previous FUI. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 23 | Emergency lighting did not function in test mode (burned out, broken,etc.). | Regularly test the emergency lighting system on each floor and replace/repair lights as needed. | Corrected in 2nd Follow up inspection. | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 24 | Manual on-off switch is provided for emergency lighting and exit signage units. | Remove manual on/off switches from emergency Lighting & exit signage units to prevent them from being switched off. | Corrected We have removed manual on of switch for emergency backup | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 25 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with ACCORD standards. | Inspect, test and maintain the emergency lighting system in the accordance with ACCORD standards. Keep written records on-site. | Corrected we are maintaining emergency lighting system in accordance to ACCORD standard | Feb 28 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected as per previous FUI. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 26 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. | Corrected in 3rd Follow up inspection on 13th February 2018 | Feb 28 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 27 | Building did not have stair designation sign, occupant load sign & floor level signs at required locations. | Provide occupant load sign, stair & floor designation signs at required locations. | Corrected We have provided stair designation sign, occupant load sign & floor level at each exit stair | Dec 10 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 28 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10. | Corrected we are maintaining Fire extinguisher checklist in accordance to ACCORD recommendation | Jan 30 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected as per previous FUI. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 months | Corrected
Follow Up Inspection |  | 29 | New Finding (2nd FU): Areas used for in-process storage of combustible materials are open to the surrounding occupancy. | Provide defined storage areas and limit the storage arrangement as follows:- Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. Or Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected We have arrange the storage as per RSC instructions. | Oct 28 2017 | On 13/February/2018:Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected as per previous follow-up. Note: Factory shall maintain defined storage area limit as per recommendation. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: The area used for the storage of combustible materials is found to exceed the limit on the fourth floor. On 24/01/2022 (Special Inspection): Not corrected. In process storage was not found within limit on 4th floor and ground floor. Factory shall maintain defined storage area limit as per recommendation. On 19/06/2022: Factory has started to re-arrange the in-process storage area but not completed yet. Non-compliant in-process storage areas were found on 1st and 4th floor. On 19/10/2022: In process storage was found within limit during the inspection. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. Factory shall maintain in-process storage as per recommendation. | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New Finding (2nd FU): Combustible storage/non essentials were located in the exit stair enclosure. | Remove all storage from exit stairs. | Corrected all storage removed from exit stair | Oct 28 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Corrected. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding (2nd FU): During the inspection egress aisles were obstructed by combustible storages and available clear width were found less than 36 inch. | Provide aisles free from obstructions and with minimum clear widths of 36-inch. | Corrected All aisle have been cleared and maintaining Properly | Oct 28 2017 | On 13/February/2018: Corrected On 09/10/2018: Corrected On 04/02/2019: Corrected On 22/09/2019: Issue is reopened. Few aisles were found less than 36 in. In few areas aisles mark were not clear or missing. On 6-1-2020: Corrected On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 32 | New Finding (6th FUI): Electrical panel and pump were located in exit stair enclosure. | Remove all electrical panels and pump from the exit stairwells. | Corrected We remove all electrical panel and pump from located area. | Oct 22 2019 | On 22/09/2019: New Finding On 6-1-2020: Corrected. Electrical panel has been removed. On 04.03.2020 (Special Inspection): Not Checked. On 26/08/2021: Corrected. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Within 1 month | Corrected
Special | Escalation | 33 | New Finding (Special inspection on 04.03.2020): Storage was noted inside stair enclosure. | Remove all storage from stair enclosures to ensure safe evacuation. | Corrected We remove all storage from stair enclosure. | Mar 12 2020 | On 26/08/2021: Corrected based on site conditions. On 24/01/2022 (Special Inspection): Not Checked. On 19/06/2022: Corrected. On 19/10/2022: Corrected. On 06-Nov-24: Corrected. On 29-Oct-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 34 | New Finding (11th FUI): Rooms used for combustible storage are not separated from surrounding occupancies by fire rated construction at 2nd floor. | Separate the dedicated storage rooms by minimum 1-hr fire-rated construction. Provide 0.75 hr. fire rated door and seal all penetrations and openings by 0.75 hr. (45 Minutes) fire rated fire rated barrier construction. | As per the advice of RSC, we have decided to install fire rated doors. Hopefully, we will complete the installation of our fire doors by september30, 2025. | Feb 6 2025 | On 06-Nov-24: New Finding On 29-Oct-25: Corrected. Factory has provided fire rated doors for opening protection. Installed fire doors were functional during the inspection. | Within 3 months | Corrected
Follow Up Inspection |  | 35 | New Finding (11th FUI): Unsealed penetrations and openings are located in the fire rated floor/ceiling assemblies due to pvc toilet pipe. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's guideline (Type-1 Construction). or, Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required (Type-1Construction). | Corrected, We already scaled all penetrations as per the RSC guide line. | Feb 6 2025 | On 06-Nov-24: New Finding On 29-Oct-25: Not Corrected. Factory has closed the shafts with fire-rated construction on all floors, except the ground and 1st floor. | Within 3 months | In Progress

## Electrical
Date
10-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Sweater Ltd., Sorifpur Road Malekerbari, National University Gazipur, Gazipur
Date of Inspection |  | 2016-09-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Electrical single Line Diagram(SLD) is unavailable in the factory. | As built Electrical SLD must be prepared, it must have factory's whole electrical installation information | Corrected, We prepared the as built SLD for full factory electrical instalation as per RSC review comments. | Feb 28 2017 | On 13/02/2018:Not Corrected. Sld is not amended. On 09/10/2018:Not Corrected. SLD need to be as built and power cable identification is required. On 04/02/2019:work's been started, but not finished yet. Not Corrected. On 22/09/2019:Not corrected. Factory is working to prepare as-built SLD. On 06-Jan-2020:Not Corrected. On 04/03/2020(Special Inspection):Not Corrected. SLD not as-built. Cable identification not done yet. On 26/08/2021: Not Corrected. Cable identification started but not completed. On 24/01/2022 (Special Inspection): Not Corrected. No progress observed since last follow-up inspection. SLD needs modification as it is not as built at few cases and cables/equipment are not identified accordingly. On 30-May-2022:Not Corrected. Still some Work is pending. Cable identification pending, cable mismatch found and SLD is needed to be reviewed by RSC. on 19/10/2022:Not Corrected. Factory got review comment " Need Minor Modification" on 29th Sep 2022. Now factory is working on it and plan to send to RSC for review very soon. On 29/05/2023: Not Corrected. Factory got the accepted copy on 30th Dec,22. Present copy dosent reflect the corrections mentioned in the approved copy On 07/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 2 | Lightning Protection System(LPS) drawing is unavailable | Factory has to design Lightning Protection System(LPS)for the whole factory(where the Risk index is more than 40). Once a LPS properly, installation must be done accordingly. | Corrected LPS drawing is available in side. | Mar 30 2017 | On 11/06/2017: Not Corrected. On 27/09/2017: Not Corrected. Factory has LPS drawing but LPS is not installed yet. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Not corrected. Installation done. Bi-metallic connector is missing. On 06-Jan-2020: Not Corrected. On 04/03/2020(Special Inspection): Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 3 | Electric safety training program has not initiated/conducted | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory has to continue to improve overall electrical safety situation for the staffs. | Corrected We have provided Cable tray and specific route for entering power cable to Distribution board | Feb 28 2017 | On 11/06/2017: Not Corrected. On 27/09/2017: Not Corrected. Safety training conducted, but no influence observed. On 13/02/2018: Not Corrected. Inadequate documentation. On 09/10/2018: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 4 | Insulation resistance test of electrical power cables is not performed | Insulation resistance test of all the cables(but not less than 25 sq.mm)must be performed once every 2 years cycle and recorded(this must require a complete power shut off) | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Feb 28 2017 | On 11/06/2017: Not Corrected. On 27/09/2017: Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 5 | Earth Pit resistance record is unavailable | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the inspector when required. | Corrected We have completed all earth pit resistance and also kept the record. | Feb 28 2017 | On 11/06/2017: Not Corrected. Earth pits are inadequate for the factory. On 27/09/2017: Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 6 | Thermography survey record is unavailable. Hot spots have been observed at some points. | Thermography survey must be done at least twice in a year. Hot spots must be removed as soon as possible. | Corrected We have removed office from substation area | Jan 15 2017 | On 11/06/2017: Not Corrected. Hotspot found at several panel. On 27/09/2017: Not Corrected. No progress observed. On 13/02/2018: Not Corrected. Report is outdated. On 09/10/2018: Corrected. | IMMEDIATE | Corrected
Initial Inspection |  | 7 | MCCBs are not adjusted according to load demand. | All the MCCBs must be adjusted according to cable current ampacity/load current. If adjustment is not possible, replacement will be the only way. | Corrected We have adjusted MCCB according to load demand. | Feb 28 2017 | On 11/06/2017: Not Corrected. On 27/09/2017: Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 2 MONTHS | Corrected
Initial Inspection |  | 8 | Panel/Distribution boxes are inaccessible or can not be opened to perform any maintenance work. | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base, and door opening shall be at least 90 degree. | Corrected We have provided earthing connection to exhaust fan | Feb 28 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 9 | Electrical distribution box/panels are full of fluffs(lint/dirt) | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs, but an adequate ventilation system must also be ensured. | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Jan 31 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 10 | Cables inside distribution board are disorganized. | Cables inside each distribution board shall be well organized to avoid misleading during any troubleshooting. Distribution board's form is appreciated. | Corrected we have organized cable inside distribution board. | Mar 30 2017 | On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 3 MONTHS | Corrected
Initial Inspection |  | 11 | Earth lead cable/Earth continuity conductor size is inadequate/ | Earth lead cable/Earth continuity conductor(ECC)must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Mar 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 12 | Generator body has been earthed by inadequate/improper sized (type)cable | Minimum two earthing connection for generator body with proper sized ECC need to be ensured(consult with your generator supplier) | Corrected Changeover switch gear provided with bearing gear | Jan 30 2017 | On 11/06/2017: Not Corrected. On 27/09/2017: Not Corrected. No progress observed. On 13/02/2018:Not Corrected. System earthing is also inadequate. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 13 | Instruction for CPR(Cardio Pulmonary Resuscitation)or Electrical shock restoration is not present | CPR instruction shall be hanged near all electrical installations(LT panel,MDB,FDB,DB,SDB) at visible location | Corrected We have provided Phase separator in MCCBs | Jan 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 14 | Earth pits are not identifiable | Each earth pit shall be properly identifiable and marked for periodic maintenance | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Jan 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 15 | Panel doors are not connected with earth | All metal installation which are part electrical system must be connected with earth to avoid electrical shock or electrocution. | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Jan 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 16 | Phase barrier/separators are missing in the MCCB/MCB | Phases must be separated by insulator(a rubber type no-flammable materials shall be used for it) | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Jan 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 17 | Distribution Board's top/bottom is left open(typical issue) | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs but an adequate ventilation system must also be ensured. | Corrected We have Completed the sealing work of Distribution board as per ACCORD Standard & Comments in last follow-up | Feb 28 2017 | On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Not corrected. Done at most panels except PFI panel. On 06-Jan-2020: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 18 | Multiple cables(came from different electrical consumers)terminated at MCCB terminals/Busbar | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Corrected We have properly terminated at single MCB / MCCB terminals. | Feb 28 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018:Not Corrected. On 09/10/2018:Not Corrected. On 04/02/2019work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 2 MONTHS | Corrected
Initial Inspection |  | 19 | Loop connection has been used powering multiple circuits through MCB/MCCBs. | Loop connection has been used powering multiple circuits through MCB/MCCBs. | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Jan 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 20 | No/Inadequate rubber(insulation) mat at the working area of distribution board/panel. | Electrical insulation(not less than 3 mm thick in case of rubber mat)at the working area of each electrical installation(Transformer/ LT panel/MDB/DB/SDB/other manual opera rated machineries)must be ensured. | Corrected we have ensured 3mm thick rubber mat. | Jan 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 21 | Multiple cables connected/terminated at the bus bar using single cable lug | Each power cable must be terminated at any point using single cable lug. | Corrected We have provided distribution marking | Feb 28 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 22 | Circuit is drawn from bus bar without any protective means for saving cables | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement(MCCB/ MCB) | Corrected We have properly used busbar with proper type protection . | Feb 28 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018:Not Corrected. On 09/10/2018:Not Corrected. On 04/02/2019:work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 2 MONTHS | Corrected
Initial Inspection |  | 23 | Cables terminated at electrical bus bar/MCCB without cable lugs | All the power/earth/neutral cable should be terminated with proper sized cable lug | Corrected We have providing proper size cable lug. | Feb 28 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018:Not Corrected. On 09/10/2018:Not Corrected. On 04/02/2019:work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 2 MONTHS | Corrected
Initial Inspection |  | 24 | Cable duct/channels are filed with fluffs(line/dust) | Cable channels/ducts must be kept neat and clean, these must be sealed properly thus no scope of ingression of fluffs. |  | Jan 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 25 | Service cables from grid network has inadequate support(or excessively sagged) | Power service cables must be draw using cable tray/ladder(in case of overhead drawing)covering is required for LT cables |  | Feb 28 2017 | On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected as the service cables are GI wires. | 2 MONTHS | Corrected
Initial Inspection |  | 26 | Cables in service are joined(splicing) between terminations. | Splicing in the power cables shall be avoided in unavoidable cases splicing must be made following proper guidance | Corrected We have splicing the power cable by proper guidance. | Feb 28 2017 | On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 2 MONTHS | Corrected
Initial Inspection |  | 27 | Power cables entering into or exiting from Distribution board/panel are not properly fixed. | Power cables entering into or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). | Corrected We have using proper size cable glands in distribution board. | Feb 28 2017 | On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Not corrected. At most panels it is done except PFI panel. On 06-Jan-2020: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 28 | Wiring among different floors using flexible/rigid PVC pipe- this arrangement does not have any support for cables | A cable ladder must be used; if it is routed through outside wall, either the cable ladder must be covered or a cable duct must be used | We have provided cable tray to support the power cable | Mar 30 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 29 | Generator output cables (laid on floor) are not protected and supported | Service cables from generator must be supported at its own breaker's terminal and with cable tray. | Corrected We have provided cable tray to support the power cable | Jan 30 2017 | On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 1 MONTH | Corrected
Initial Inspection |  | 30 | Maintenance people are using substation room as their working station. | Substation room shouldn’t be used as a working station. But a separate enclosure can be used for working station. | Corrected We have removed office from substation area | Feb 28 2017 | ACCORD accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline On 11/06/2017:Not Corrected. On 27/09/2017:Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 2 MONTHS | Corrected
Follow Up Inspection |  | 31 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. |  | Jul 15 2017 | On 27/09/2017: Not Corrected. No progress observed. On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 32 | New Finding: Exhaust fan's metal enclosure and manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Exhaust fan and manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Corrected We have provided earthing connection to exhaust fan | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: work's been started, but not finished yet. Not Corrected. On 22/09/2019: Corrected | 1 MONTH | Corrected
Follow Up Inspection |  | 33 | New Finding: Light fixture are not fixed properly. | All electrical fittings and outlet must fixed and protected. | Corrected Loose lighting fixture is being fixed tight | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. That light fixtures has been removed. | 1 MONTH | Corrected
Follow Up Inspection |  | 34 | New Finding: Generator room is filled with debris (or used as temporary storage). | Generator room must be kept neat and clean. | Corrected Generator room inside storage has been removed and cleaned | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 35 | New Finding: Power sockets are hanging without proper support. | Power socket has to be installed on rigid support/base securely and at minimum 200mm above floor level. | Corrected Power socket is no more hanging over | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. That sockets had been removed. | 1 MONTH | Corrected
Follow Up Inspection |  | 36 | New Finding: Change Over Switch contacts smeared with bearing grease. | Instead of bearing grease, thin layer of contact grease must be used for lubrication of Changeover-Switch contacts. | Corrected Changeover switch gear provided with bearing grease | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Not Corrected. On 04/02/2019: Not Corrected. On 22/09/2019: Corrected | 1 MONTH | Corrected
Follow Up Inspection |  | 37 | New Finding: Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | Corrected We have provided Phase separator in MCCBs | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 38 | New Finding: Flexible PVC pipe is used to cover power and signal cable for boiler. | Power and signal cable for boilers shall be distributed using proper type insulator to avoid damage of cables. | Corrected We have provided metallic conduit for power cable in boiler | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 39 | New Finding: Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables must be removed as soon as possible. | Corrected We have removed unprotected live wire from the panel or distribution board | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 40 | New Finding: Circuit breakers inside panel board are not fixed at base. | Circuit breakers and other electrical installation must be fixed on base properly. | Corrected Those type of panel board have been repaired | Nov 10 2017 | On 13/02/2018: Not Corrected. On 09/10/2018: Corrected. All breakers had been removed. | 1 MONTH | Corrected
Follow Up Inspection |  | 41 | New Finding: Electrical distribution box/panels are full of fluffs (lint/dirt) and combustible material stack near distribution box. | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured and periodic maintenance must be done in the facility. | Corrected We have maintained routine maintenance program for cleaning | Mar 20 2018 | On 09/10/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Indicator lights are mounted without disconnecting device. | Indicator lights should be connected by control device such as rated fuse or MCB. | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Mar 20 2018 | On 09/10/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Distribution panel/board is installed without proper grout. | Distribution panel/board must be installed with proper grout. | Corrected We have installed the distribution board accordingly and maintain the Checklist for Cleaning | Mar 20 2018 | On 09/10/2018: Not Corrected. On 04/02/2019: Not Corrected. On 22/09/2019: Not corrected. Fix the panel with base. On 06-Jan-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: HT Cable dropping from 11kV OH line wire is used instead of DO Fuse (Typical). | Replace the wire with standard DO fuse. | Corrected We have replace the wire with standard DO fuse. | Mar 20 2018 | On 09/10/2018: Not Corrected. On 04/02/2019: Not Corrected. On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Distribution boards have no clear identification markings. No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. Panel room has inadequate illumination. ( Accord Standard Part 10 Section 10.15.3) | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. Adequate illumination must be ensured in the sub station room thus any maintenance can be done comfortably (150 lux should be maintained). | Corrected We have properly marking the distribution board and providing rubber mat | Mar 20 2018 | On 09/10/2018: Not Corrected On 04/02/2019: Not Corrected.. On 22/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. | Corrected in 4rth follow-up inspection of accord on 9th October 2018 | Mar 20 2018 | On 09/10/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s) | Cables passing through permanent wall/floor slab must be protected. Floor to floor openings shall be sealed by proper type materials (consult with fire expert). | Corrected in 5th follow-up inspection of accord on 4th February 2019 | Mar 20 2018 | On 09/10/2018: Not Corrected. On 04/02/2019: Found Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Flexible PVC pipe has been used inside the panel covering cables. | Flexible PVC pipe shall not be used covering power cables. | Corrected in 4th follow-up inspection of accord on 9th October 2018 | Mar 20 2018 | On 09/10/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Corrected in 4th follow-up inspection of accord on 9th October 2018 | Mar 20 2018 | On 09/10/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive) | Corrected We have made a routine maintenance program as per RSC standards. | Mar 20 2018 | On 09/10/2018: Not Corrected. On 04/02/2019: Not Corrected. On 22/09/2019: Not corrected. Factory is working on the issue. On 06-Jan-2020: Not Corrected. On 04/03/2020 (Special Inspection): Not Verified. On 26/08/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Maintenance movement is obstacle due to uneven height of cable trench in utility area (generator room). | Work place around transformer/generator (or other electrical installation) must be on same height. | Corrected We have properly completed the generator room.. | Nov 20 2018 | On 04/02/2019: Not Corrected. On 22/09/2019: Corrected | 1 MONTH | Corrected
Follow Up Inspection |  | 52 | New Finding: Earth Pit resistance record is manipulated | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Corrected We have completed all earth pit resistance. | Mar 20 2019 | Factory asked for time extension till 10/08/2019. Not Accepted. On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Corrected We have installed the non-hazardous lights in these areas. | Mar 20 2019 | On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Panel has unwanted openings. | Openings shall be sealed properly | Corrected We have sealed panel opening properly. | Mar 20 2019 | On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Power socket is kept on floor | Power socket shall be install at minimum 200mm above the floor with a rigid support. | Corrected We have properly install the power socket and rigid support | Mar 20 2019 | On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Cable termination at the motor terminal box is directly connected to terminals without proper gland. | All equipment termination must be done with proper termination including cable glands to avoid ingression of moisture and dust entering the terminals. | Corrected We have use proper cable glands. | Mar 20 2019 | On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected We have properly cleaned cable channels fluffs. | Mar 20 2019 | On 22/09/2019: Not corrected On 06-Jan-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Large exhaust fans are controlled directly by MCB | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | Corrected We have properly used Direct-on-line (DOL) type control switch. | Mar 20 2019 | On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Wiring using flexible/rigid PVC pipe- this arrangement does not have any support for cables | A cable ladder must be used; if it is routed through outside wall, either the cable ladder must be covered or a cable duct must be used | Corrected We have provide cable tray & tie up with specific route | Mar 20 2019 | On 22/09/2019: Not corrected On 06-Jan-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct) | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected We have provide adequate insulator in steam line. | Mar 20 2019 | On 22/09/2019: Not corrected. Factory is working on the issue. On 06-Jan-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. Panel doors are not connected with earth. | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Corrected We have installation proper size cable and earthing connection. | Mar 20 2019 | On 22/09/2019: Not corrected as door earthing is missing at several places. On 06-Jan-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Poor interlocking capabilities among existed the sources/ changeover switches. | All sources/changeover switches shall have interlocking capabilities used to feed same busbar or load. | Corrected We have provide interlocking capabilities used to feed same busbar or load. | Mar 20 2019 | On 22/09/2019: Not corrected. Factory is working on the issue. On 06-Jan-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Loop connection has been used powering multiple circuits through MCB/MCCBs. Multiple cables connected/terminated at the bus bar using single cable lug. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity) Each power cable must be terminated at any point using single cable lug. | Corrected We have provided loop connection with using single cable lug. | Mar 20 2019 | On 22/09/2019: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: No mechanical guards are provided for electrical equipment where necessary. | Provide mechanical guards for electrical equipment where necessary. | Corrected We have provide the mechanical guards when it necessary. | Mar 20 2019 | On 22/09/2019: Not corrected On 06-Jan-2020: Not Corrected. On 04/03/2020(Special Inspection): Not Corrected. Still found some area. On 26/08/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | Corrected Now all electrical distribution board are easily accessible. | Mar 20 2019 | On 22/09/2019: Not corrected On 06-Jan-2020: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Electric boiler along with feed pump has inadequate/no earthing connection | Each electrical installation must have proper earth connection. | Corrected We have installed proper earth connection. | Mar 20 2019 | On 22/09/2019: Corrected as not found this time. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Connection is taken from receptacle without plug. Power socket is hanging with out any support | In case of taking any connection from receptacle, appropriate plug should be used. Power socket shall be installed with a rigid support. | Corrected We have used appropriate plug and Power socket installed with rigid support. | Mar 20 2019 | On 22/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Inadequate sized earth cable connected to generator frame. | Two separate earth connection & one separate and distinct Neutral connection must be provided over generator. Generator body must have earth connection with half of phase conductor. | Corrected We have provide two separate earth connection. | Mar 20 2019 | On 22/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Generator room is filled with debris (or used as temporary storage) | Generator room must be kept neat and clean. | Corrected We have kept net and clean (Generator room) | Mar 20 2019 | On 22/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: Power cables inside cable trench are buried by sand/soil/concrete | Power cables should not be buried directly in any case. If it is not designed through sand/concrete/soil, removal of sand/concrete/soil must be done. | Corrected We have remove all sand / soil / concrete. | Mar 20 2019 | On 22/09/2019: Not corrected. Generator output cable buried in concrete. On 06-Jan-2020: Not Corrected. On 04/03/2020(Special Inspection): Not Corrected. On 26/08/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Corrected We provide electrical circuit terminated as single MCB / MCCB terminals. | Feb 7 2020 | On 04/03/2020 (Special Inspection): Not Verified. On 26/08/2021: Not Corrected. Found in very few places. On 24/01/2022 (Special Inspection): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Motor terminal box is not found with body. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | We have provided cable tray to support the power cable | Feb 7 2020 | On 04/03/2020 (Special Inspection): Not Verified. On 26/08/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 73 | New Finding: Inadequate working space around transformer for performing maintenance work. No working separation between LT ( Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT switchgear) | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07m) and ventilation must be ensured. |  | Oct 30 2021 | On 24/01/2022 (Special Inspection): Not Verified. On 30-May-2022: Not Corrected. Work has not started yet. On 19/10/2022: Not Corrected. Factory prepared a substation layout but need modification due to inadequate clearance. On 29/05/2023: Not Corrected.Factory got a approved layout plan from RSC but the plan is not matched with the field condition yet. On 07/09/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 74 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected We remove all Hot Sports from entier electrical systems. | Jul 1 2022 | On 29/05/2023: Not Corrected. Burning sign found in ground floor but temparature was not measured due to malfunction of the thermal scanner. On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Uncovered/Perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected We removed all PVC wairing from storage area. We already installed Metal conduit wairing. | Nov 28 2022 | On 29/05/2023: Not Corrected. Specially in the packaging storage area on 1st floor. Feedback received from factory after inspection which seems fine but needs on site veirfication. On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 76 | New Finding: Cumulative breaker size is greater than cable ampacity. Non rated and non-certified comb bar used for powering multiple MCB. | Cable rating shall not be less than ahead of its circuit breaker or Cumulative breaker rating. Multiple connections shall be avoided at the circuit terminal unless it is designed for so. For connecting multiple MCB use rated and listed comb bar. | Corrected We already used certified comb bar as per RSC Instractions. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: PPE & LOTO (Lock-Out-Tag-Out) devices are inadequate for maintenance work. Uninsulated electrical tools are used by maintenance personnel in the factory Electrical safety training program module is not enriched/inadequate | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. Electrical safety training and awareness program for all electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. Training module shall be enriched according to acknowledged standard. | Corrected All maintenance used insulated electrical tools and also used PPE & LOTO. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 78 | New Finding: LPS Earth lead cable/Earth Continuity Conductor size is undersized Metal bonding missing | Modification work shall be done according to acknowledged standard | Corrected We checked the LPS cable diameter. It is correct according to the standard. We already using metal bonding. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: Power socket has no ECC connection Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | ECC connection shall be provided to each power socket Each manually operated machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Corrected, We removed the power socket and also provide ECC connection to all manually operated machines. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected We cleared all fluffs from cable channel and also closed all the opening in the cable channels. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Cable directly connected with motor coil without terminal box/ proper gland. | Cable must be connected through motor terminal box as manufacturer guideline. | Corrected We connected the cable through the motor terminal box as per guideline in manufacture. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 82 | New Finding: Equipment earth cable (for generator) size is inadequate.(only one pit is connected) | Provide earthing connection for generator. At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. | Corrected. We provide 3 pcs separate earth pits connectionfor Generator. One for neutral and Two for body earthing. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 83 | New Finding: Poor interlocking capabilities among existing sources. | All sources/changeover switches shall have interlocking capabilities used to feed same busbar or load. | Corrected We removed poor interlocking system and also provide fixed interlocking systems. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 84 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected We have joined the cable with proper guidance. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 85 | New Finding: Thermography survey record is not prepared properly(re-check scanner settings). | Thermography survey must be done and recorded at least twice in a year. Hot spots must be removed. | Corrected We are storing Thermography reports properly. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 86 | New Finding: Distribution boards have no clear & permanent identification markings. Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | All distribution boards, switchboards, sub main boards and switches shall be marked clear & permanently for proper identification. CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | Corrected We already marking all LT, HT , PFI panel, DB, SDB bords and also installing CPR instruction and also using rubber mat. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 87 | New Finding: Transformer Breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil mark on the cup. | Corrected We already filled the Transformer breather oil cup. | Aug 10 2023 | On 07/09/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 88 | New Finding: Transformer Oil Test (dielectric strength test) report is unavailable. | Testing of transformer oil, specifically the dielectric strength test needs to be conducted at least once in a year from government-authorized entities such as BPDB, BREB, PGCB, EGCB, DESCO, DPDC, or any other designated govt. authority. This ensures adherence to an unaltered, verifiable, standardized format, thereby maintaining the integrity and reliability of the transformer's insulation system. |  | Mar 3 2026 |  | 1 Month | In Progress

## Boiler
Date
10-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A Plus Sweater Ltd., Sorifpur Road Malekerbari, National University Gazipur, Gazipur
Date of Inspection |  | 2022-08-04
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 8340 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We Already arrange manufacturing drawing and calculations. | Jan 13 2025 | Comments on 1-Jan-2025: Factory only provided the manufacturing drawing of boiler. Other relevant documents are not provided. The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 2 | BB 8340 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We have installed an Emergency stop push switches. | Jan 13 2025 | Comments on 1-Jan-2025: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 8340 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. | We will solve the problem by 30 March 2025. | Mar 30 2025 | Comments on 1-Jan-2025: Factory given timeline is accepted. The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 8340 | Fuel line is not constructed with appropriate materials and is not properly supported and protected against corrosion. | Fuel line shall be constructed with appropriate materials as specified by the manufacturer/standard. Support and protection against corrosion shall be as per the requirements of the gas supply company and NFPA 54. | We will solve the problem by 30 April 2025. | Jan 31 2025 | Comments on 1-Jan-2025: Factory given timeline is not accepted. The new timeline is 31-Jan-25. The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 5 | BB 8340 | Fuel gas line safety valve(s) /pressure relief valve(s) blowoff is not directed to the outside of the boiler room. | Any fuel gas line safety valve or pressure relief valve blowoff shall be diverted to the outside of the boiler room (open to atmosphere condition) to prevent gas accumulation in the boiler room. | We will solve the problem by 30 April 2025. | Jan 31 2025 | Comments on 1-Jan-2025: Factory given timeline is not accepted. The new timeline is 31-Jan-25. The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 6 | BB 8340 | The feed pump was not accessible for inspection. | Proper accessibility shall be ensured around the boiler and equipment for operation, maintenance and inspection procedures. | We will solve the problem by 30 March 2025. | Mar 30 2025 | Comments on 1-Jan-2025: Factory given timeline is accepted. The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 7 | BB 8340 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have installed new Gauge glass. | Jan 13 2025 | Comments on 1-Jan-2025: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 8340 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We will solve the problem by 30 March 2025. | Jan 31 2025 | Comments on 1-Jan-2025: Factory given timeline is not accepted. The new timeline is 31-Jan-25. The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 9 | BB 8340 | Steam line connection is not terminated properly. | Any unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We will solve the problem by 30 March 2025. | Jan 31 2025 | Comments on 1-Jan-2025: Factory given timeline is not accepted. The new timeline is 31-Jan-25. The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 8340 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | We have already installed a ladder in Boiler room. | Jan 13 2025 | Comments on 1-Jan-2025: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 11 | BB 8340 | Salt and scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | The boiler Operator operate the boiler with proper blowdown. | Dec 13 2025 | Comments on 1-Jan-2025: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 12 | BB 8340 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have already installed a Steam Pressure Limiter. | Dec 13 2025 | Comments on 1-Jan-2025: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 13 | BB 8340 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | We have already installed an Air Pressure Limiter. | Dec 13 2025 | Comments on 1-Jan-2025: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification