## Structural
Date
03-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB APPARELS LTD, 225, SINGAIR ROAD, HEMAYETPUR, SAVAR, Area: Mouchak, Dhaka
Date of Inspection |  | 2016-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | High Stressed Columns in Building. | Verify in-situ concrete strength (using min. 4 nos. 100mm dia. Cores and/or assessment of available concrete strength data) and as constructed reinforcement for all columns from 1st phase of construction (Preferably from Ground Floor) . | Corrected | Mar 31 2017 | On 12/06/2017: During inspection, core cutting location was found. Factory has been recommended to submit DEA to ACCORD as early as possible. On 30/01/2018: During inspection, 14 nos. cores locations were observed out of 16nos. Factory management showed core test report which has been incorporated in Detail Engineering Assessment (DEA). Building engineer to identify all the core locations and update the core layout accordingly. DEA has been submitted to ACCORD on 31st December 2017which is under review. On 27/06/2018: During inspection, 20 cores were found. Among them, 8 cores were collected from columns, 8 cores from beams and 4 cores from slabs. Core locations were found as per core layout plan provided in the accepted DEA report. Original core test reports were found on site. On 27/09/2018: Corrected from previous inspection. During inspection, original core test report found on site and core location found according to core layout. On 02-Jan-2023: ​Corrected previously. Cores were taken from columns of the main production building to verify in-situ concrete strength and incorporated in DEA. On 26-Nov-2023: Corrected from previous inspection. Factory verified in-situ concrete strength for Main Production Building based on core test result which has been incorporated in accepted DEA. On 29-Feb-2024: Corrected previously. | Immediately | Corrected
Initial Inspection |  | 2 | High Stressed Columns in Building. | Factory Engineer to review design, loads and column stresses for all columns. Detail Engineering Assessment of as built structure to be commenced as per attached scope. | Corrected | Mar 31 2017 | On 12/06/2017: No DEA has been conducted yet. Factory is recommended to submit DEA to ACCORD as early as possible. On 30/01/2018: This issue is required to be covered in DEA which is under review. On 27/06/2018: This issue has been covered under DEA. DEA of the factory was accepted from ACCORD on 13/05/2018. On 27/09/2018: Corrected from previous inspection. This issue has been covered under DEA which was accepted from ACCORD on 13/05/2018. On 02-Jan-2023: ​Corrected previously. This issue was covered in the DEA of the main production building which was accepted by ACCORD on 13-May-2018. On 26-Nov-2023: Corrected from previous inspection. This was covered in DEA which was accepted from ACCORD on 13-May-2018. On 29-Feb-2024: Corrected previously. | 6-weeks | Corrected
Initial Inspection |  | 3 | High Stressed Columns in Building. | Produce and actively manage a loading plan for all floors within the building giving consideration to floor capacity and column capacity. | Corrected | Mar 31 2017 | On 12/06/2017: A load plan considering 3kpa was found posted at one floor. Factory management have to produce load plan as part of DEA. On 30/01/2018: Floor load plan has been produced but not accepted yet. However, loading was found within safe load plan. Factory is required to maintain safe loading 42psf until acceptance of final load plan along with DEA. On 27/06/2018: Load plan has been prepared as part of DEA. DEA of the factory was accepted from ACCORD on 13/05/2018. However, load was found below 2 kPa on each floor. On 27/06/2018: This issue has been covered under DEA. DEA of the factory was accepted from ACCORD on 13/05/2018. On 27/09/2018: Corrected from previous inspection. Factory has produced load plan as part of DEA which was accepted from ACCORD on 13/05/2018. On 02-Jan-2023: Corrected previously. Factory has produced a set of load plans as a part of DEA of the main production building which was accepted by ACCORD on 13-May-2018. During inspection, load plan was found posted on each floor and loading was observed within the allowable limit (42 psf for all floor plates and 63 psf for dining room). On 26-Nov-2023: Corrected from previous inspection. Factory has produced load plan for Main Production Building as a part of DEA which was accepted by ACCORD on 13-May-2018. During inspection load plan was found posted in each floor and loading was observed below accepted loading limit (42 psf for all floor and 63 psf for 5th floor dining & roof canteen). On 29-Feb-2024: Corrected previously. Load plan was produced as a part of DEA. During inspection, load plan was found posted and loading was found below allowable limit (42 psf for typical floor and 63 psf for dining). | 6-weeks | Corrected
Initial Inspection |  | 4 | High Stressed Columns in Building. | Continue to implement load plan. | Corrected | Jun 30 2017 | On 12/06/2017: Factory management is recommended to follow safe load plan till acceptance from ACCOD. On 30/01/2018: Final floor loading plan need to be implemented after getting acceptance from ACCORD. Till that factory is required to maintain safe loading below 2 kPa on all suspended floors. However, floor loading was found within allowable limit. On 27/06/2018: Load plan has been prepared as part of DEA. DEA of the factory was accepted from ACCORD on 13/05/2018. As per recommendation of accepted DEA, factory building required remediation in one footing. Factory has completed remediation works but test reports of retrofitting materials and completion certificate were not found on site. Factory shall maintain final load plan after completion of remediation process. However, load was found below 2 kPa on each floor. Load plan was found posted on all floors. On 27/09/2018: Factory has produced load plan as part of DEA which was accepted from ACCORD on 13/05/2018. Factory has completed remediation works and original test reports of retrofitting materials and completion certificate were found on site. Final load plan was found posted on all floors. Loading was found within allowable limit. On 02-Jan-2023: Corrected previously. Factory has produced a set of load plans as a part of DEA of the main production building which was accepted by ACCORD on 13-May-2018. During inspection, load plan was found posted on each floor and loading was observed within the allowable limit (42 psf for all floor plates and 63 psf for dining room). On 26-Nov-2023: Corrected from previous inspection. During inspection, load plan was found posted on each floor and loading was observed within the allowable limit (42 psf for all floor plates and 63 psf for dining room). On 29-Feb-2024: Corrected previously. During inspection, load plan was found posted and loading was found below allowable limit (42 psf for typical floor and 63 psf for dining). | 6-months | Corrected
Initial Inspection |  | 5 | High Stressed Columns in Building. | Implement strengthening measures where required by the DEA. | Corrected | Jun 30 2017 | On 12/06/2017: No DEA has been conducted yet. Factory is recommended to submit DEA to ACCORD as early as possible. On 30/01/2018: Remedial works suggested in DEA report to be implemented after getting acceptance from ACCORD. On 27/06/2018: This issue has been covered under DEA. DEA of the factory was accepted from ACCORD on 13/05/2018. As per recommendation of accepted DEA, factory building required remediation in one footing. Factory has completed remediation works but test reports of retrofitting materials and completion certificate were not found on site. On 27/09/2018: This issue has been covered under DEA which was accepted from ACCORD on 13/05/2018. Factory has completed remediation works according to DEA recommendation .Original test reports of retrofitting materials and retrofitting completion certificate were found on site. On 02-Jan-2023: ​Corrected previously. Factory has completed the strengthening work of the pile cap of the main production building as per the accepted retrofitting drawing. On 26-Nov-2023: Corrected from previous inspection. Factory has completed remediation works as per recommendation of accepted DEA. On 29-Feb-2024: Corrected previously. | 6-months | Corrected
Initial Inspection |  | 6 | Localized area of high loading | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Corrected | Mar 31 2017 | On 12/06/2017: No DEA has been conducted yet. Factory is recommended to submit DEA to ACCORD as early as possible. On 30/01/2018: Floor load plan has been produced but not accepted yet. However, loading was found within safe load plan. Factory is required to maintain safe loading 42psf until acceptance of final load plan along with DEA. On 27/06/2018: Load plan has been prepared as part of DEA. DEA of the factory was accepted from ACCORD on 13/05/2018. However, load was found below 2 kPa on each floor. On 27/09/2018: Corrected from previous inspection. Factory has produced load plan as part of DEA which was accepted from ACCORD on 13/05/2018. Final load plan was found posted on all floors. Loading was found within allowable limit. On 02-Jan-2023: Corrected previously. Factory has produced a set of load plans as a part of DEA of the main production building which was accepted by ACCORD on 13-May-2018. During inspection, load plan was found posted on each floor and loading was observed within the allowable limit (42 psf for all floor plates and 63 psf for dining room). On 26-Nov-2023: Corrected from previous inspection. Factory has produced load plan for Main Production Building as a part of DEA which was accepted by ACCORD on 13-May-2018. During inspection load plan was found posted in each floor and loading was observed below accepted loading limit (42 psf for all floor and 63 psf for 5th floor dining & roof canteen). On 29-Feb-2024: Corrected previously. During inspection, load plan was found posted and loading was found below allowable limit (42 psf for typical floor and 63 psf for dining). | 6-weeks | Corrected
Initial Inspection |  | 7 | Localized area of high loading | Continue to implement load plan. | Corrected | Jun 30 2017 | On 12/06/2017: Factory management is recommended to follow safe load plan till acceptance from ACCOD. On 30/01/2018: Final floor loading plan need to be implemented after getting acceptance from ACCORD. Till that factory is required to maintain safe loading below 2 kPa on all suspended floors. However, floor loading was found within allowable limit. On 27/06/2018: Load plan has been prepared as part of DEA. DEA of the factory was accepted from ACCORD on 13/05/2018. As per recommendation of accepted DEA, factory building required remediation in one footing. Factory has completed remediation works but test reports of retrofitting materials and completion certificate were not found on site. Factory shall maintain final load plan after completion of remediation process. However, load was found below 2 kPa on each floor. Load plan was found posted on all floors. On 27/09/2018: Factory has produced load plan as part of DEA which was accepted from ACCORD on 13/05/2018. Factory has completed remediation works and original test reports of retrofitting materials and completion certificate were found on site. Final load plan was found posted on all floors. Loading was found within allowable limit. On 02-Jan-2023: Corrected previously. Factory has produced a set of load plans as a part of DEA of the main production building which was accepted by ACCORD on 13-May-2018. During inspection, load plan was found posted on each floor and loading was observed within the allowable limit (42 psf for all floor plates and 63 psf for dining room). On 26-Nov-2023: Corrected from previous inspection. During inspection, load plan was found posted on each floor and loading was observed within the allowable limit (42 psf for all floor plates and 63 psf for dining room). On 29-Feb-2024: Corrected previously. During inspection, load plan was found posted and loading was found below allowable limit (42 psf for typical floor and 63 psf for dining). | 6-months | Corrected
Initial Inspection |  | 8 | Inconsistencies between permit drawings and as-built structures | As part of the DEA comprehensive As-Built drawings are to be produced. | Corrected | Mar 31 2017 | On 12/06/2017: As built drawing have to produce as part of DEA and submit to ACCORD as early as possible. On 30/01/2018: As-built drawings have been prepared as a part of DEA which is under review. On 27/06/2018: As-built drawings have been prepared as part of DEA which was accepted from ACCORD on 13/05/2018. No inconsistency was found with the accepted as-built drawings and on site condition. On 27/09/2018: Corrected from previous inspection. Factory has prepared as built drawings as part of DEA which was accepted from ACCORD on 13/05/2018. On 02-Jan-2023: ​Corrected previously. A set of as-built drawings of the main production building was produced as a part of DEA which was accepted by ACCORD on 13-May-2018. On 26-Nov-2023: Corrected from previous inspection. Factory has produced a set of as-built drawings of the Main Production Building as a part of DEA which was accepted by ACCORD on 13-May-2018. On 29-Feb-2024: Corrected previously. | 6-weeks | Corrected
Initial Inspection |  | 9 | Hairline cracks on beam | Sections of plaster finish to beams and slab to be removed to investigate if cracks penetrate the building structure. | Corrected | Mar 31 2017 | On 12/06/2017: During inspection, hairline cracks on beam were found repaired. Factory is required to submit the investigate report regarding these cracks and incorporate it with DEA. On 30/01/2018: Cracks have not been investigated yet and some cracks are repaired, but some cracks in beam soffits are observed during inspection. Factory engineer is required to investigate the reason & extent of cracks and prepare an investigation report with proper remedial measures. On 27/06/2018: Crack investigation report has been prepared and found on site. Factory engineer has removed sections of plaster finish to investigate the nature of cracks and declared that the cracks are non-structural. On 27/09/2018: Corrected from previous inspection. Crack investigation report was found on site and all cracks found repaired. On 02-Jan-2023: ​Corrected previously. Factory has prepared an investigation report regarding the crack of the beam of the main production building. According to the investigation report, the cracks were non-structural. During inspection, no further crack was observed on the beam. On 26-Nov-2023:Corrected from previous inspection. As per crack investigation report, the crack was non-structural. During inspection, no further crack was found. On 29-Feb-2024: Corrected previously. During inspection, no further crack was observed. | 6-weeks | Corrected
Initial Inspection |  | 10 | Hairline cracks on beam | As part of the Detail Engineering Assessment (see Item 1), Building Engineer to carry out design check on beams and slab taking into account the effect of the cracks on the structure | Corrected | Mar 31 2017 | On 12/06/2017: During inspection, hairline cracks on beam were found repaired. Factory is required to submit the investigate report regarding these cracks and incorporate it with DEA. On 30/01/2018: Cracks have not been investigated yet and some cracks are repaired, but some cracks in beam soffits are observed during inspection. Factory engineer is required to investigate the reason & extent of cracks and prepare an investigation report with proper remedial measures. On 27/06/2018: Crack investigation report has been prepared and found on site. Factory engineer has removed sections of plaster finish to investigate the nature of cracks and declared that the cracks are non-structural. On 27/09/2018: Corrected from previous inspection. Crack investigation report was found on site and all cracks found repaired. On 02-Jan-2023: ​Corrected previously. Factory has prepared an investigation report regarding the crack of the beam of the main production building. According to the investigation report, the cracks were non-structural. During inspection, no further crack was observed on the beam. On 26-Nov-2023: Corrected from previous inspection. As per crack investigation report, the crack was non-structural. During inspection, no further crack was found. On 29-Feb-2024: Corrected previously. During inspection, no further crack was observed. | 6-weeks | Corrected
Initial Inspection |  | 11 | Hairline cracks on beam | Carry out any structural remedial works to cracks as required following assessment. | Corrected | Jun 30 2017 | On 12/06/2017: During inspection, hairline cracks on beam were found repaired. Factory is required to submit the investigate report regarding these cracks and incorporate it with DEA. On 30/01/2018: Remediation is required to be implemented as per investigation report. On 27/06/2018: Crack investigation report has been prepared and found on site. Factory engineer has removed sections of plaster finish to investigate the nature of cracks and declared that the cracks are non-structural. Factory has repaired those hairline cracks. On 27/09/2018: Corrected from previous inspection. Crack investigation report was found on site and all cracks found repaired. On 02-Jan-2023: ​Corrected previously. Factory has prepared an investigation report regarding the crack of the beam of the main production building. According to the investigation report, the cracks were non-structural. During inspection, no further crack was observed on the beam. On 26-Nov-2023: Corrected from previous inspection. As per crack investigation report, the crack was non-structural. During inspection, no further crack was found. On 29-Feb-2024: Corrected previously. During inspection, no further crack was observed. | 6-months | Corrected
Initial Inspection |  | 12 | Exposed Bar on roof | provide proper rust proof material. | Corrected | Feb 28 2017 | On 12/06/2017: Exposed rebar were found protected at utility building. On 30/01/2018: Corrected in previous follow up inspection. No exposed rebar is observed. On 27/06/2018: This issue has been corrected as per 1st follow up inspection. Exposed rebars were covered by concrete. On 27/09/2018: Corrected from previous inspection. Exposed rebars were covered by concrete. On 02-Jan-2023: ​Corrected previously. Factory has covered the exposed rebar of the utility building by concrete. On 26-Nov-2023: Corrected from previous inspection. Factory has covered the exposed rebar of the Utility Building by concreting. On 29-Feb-2024: Corrected previously. During inspection, no exposed rebar was found. | 6-weeks | Corrected
Initial Inspection |  | 13 | No Edge protection system | Provide proper edge protection on roof. | Corrected | Mar 31 2017 | On 12/06/2017: Edge protection has been provided at utility building. On 30/01/2018: Corrected in previous follow up inspection. Edge protection is observed surrounding the roof. On 27/06/2018: This issue has been corrected as per 1st follow up inspection. Edge protection was found surrounding the roof. On 27/09/2018: This issue has been corrected from 1st follow up inspection. Edge protection was found provided on roof. On 02-Jan-2023: ​Corrected previously. During inspection, edge protection was observed on the roof of the utility building. On 26-Nov-2023:Corrected from previous inspection. During inspection, edge protection was observed on the roof of the Utility Building. On 29-Feb-2024: Corrected previously. | 6-weeks | Corrected
Follow Up Inspection |  | 14 | New Finding: 1 Damaged steel column and cantilever beam observed due to vehicular movement. | Factory engineer is required to repair the damaged steel columns and beams properly and to provide barrier surrounding the steel columns and cantilever beams to protect it from vehicle impact. | Corrected | Feb 19 2023 | On 02-Jan-2023: During inspection, some steel columns of the steel shed of loading unloading bay and 1st floor cantilever beams of the main production building were found damaged due to vehicle impact. Factory engineer is required to repair the damaged beams and steel columns properly and provide barrier surrounding the steel columns and cantilever beams to protect it from vehicle impact. On 26-Nov-2023: Factory has repaired the damage steel column and 1st floor cantilever beam west side of the Main Production Building and provided barrier to protect further vehicle impact. On 29-Feb-2024: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 15 | New Findings-2: Non-structural elements (racks) at several locations not adequately anchored and braced (Main building – Basement, 1st & 2nd floor) | Factory is required to anchor and brace all non-structural elements (racks) to resist earthquake force | Corrected | Apr 29 2024 | RPO Comments: On 25/02/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 29-Feb-2024: During inspection, non-structural elements (racks) at several locations (Main building – Basement, 1st & 2nd floor) were found unanchored/unbraced. Factory is required to anchor/brace all the non-structural elements. | (within 6 weeks) | Pending Verification

## Fire
Date
03-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB APPARELS LTD, 225, SINGAIR ROAD, HEMAYETPUR, SAVAR, Area: Mouchak, Dhaka
Date of Inspection |  | 2016-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stairs are not separated from [work areas, other spaces] on each floor by fire-rated construction properly. In few floors, exit stairs are not enclosed by fire rated construction from production areas or both rated & non-rated doors have been installed. In many cases fire doors were kept open by external objects. | Stair shall be enclosed with a minimum 2-hr fire-rated construction. Seal all unprotected openings and provide minimum 1.5-hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. Ensure the listing of fire rated doors by providing required documents If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Already we have repaired fire door which was found nonfunctional during visit. | Dec 8 2017 | On 02/12/2020 T&CVI documents submitted. On 19/July/2018: Clear gap in between fire door leaf & finished floor level was more than 19 mm. for some of the fire doors. Installed door closer for many fire doors found non-functional. Existing window at the printing section creates unprotected opening between production floor & Exit stair. Finally, exit stairs shall have to be separated from other occupancies (Utility, storage). On 27/05/2019: During follow up inspection it was observed that water basin & toilet is located South-East (stair-3) and toilet is located North-West (stair-2) exit stair enclosure throughout the building. Installed fire door with necessary accessories (door coordinator in double leaf, door closer, panic bar etc.) were not working properly on several floors. However, Stair-1 (west-middle) & 4 (south-west) directly discharge on ground floor loading & unloading shed. On 09/11/2020: As per factory concern the rafter portion is no longer used as loading unloading area. But some fire doors had functional problems. On 26/01/2021: Corrected. All fire doors were found functional during inspection. On 28-Apr-2024: Refer to Issue # 14. On 26-Nov-24: Refer to Issue # 14. | Within 03 Months | Corrected
Initial Inspection |  | 2 | Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas/exit stair. Location: 2nd & 4th Floor | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. **If store rooms is directly connected to exit stair by fire rated doors, in that case fire doors shall be interfaced with fire alarm system | Corrected | Mar 31 2017 | On 21/09/2017: Corrected as per last follow-up inspection. On 26/02/2018: Corrected as per last follow-up inspection. Fire doors need repairing in some places. On 19/July/2018: Corrected as per Previous Follow-up inspection. Note: Unprotected window opening was present between Basement Store room & 1st Floor Inspection section, Store room (Fabrics Store room) & Compressor room. On 27/05/2019: Issue re-opened. Please see issue no. 12. On 09/11/2020: Refer to issue no. 12. On 26/01/2021: Corrected. On 28-Apr-2024: Refer to issue no. 12. On 26-Nov-24: Corrected. | Within 03 Months | Corrected
Initial Inspection |  | 3 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Jul 2 2017 | On 12-06-17: Corrected. On 21/09/2017: Corrected as per last follow-up inspection. On 26/02/2018: Corrected as per last follow-up inspection. On 19/July/2018: Corrected On 27/05/2019: Corrected as per previous follow up. Refer issue no. 12. On 09/11/2020: Refer to issue no. 12. On 26/01/2021: Corrected. On 28-Apr-2024: Refer to issue no. 12. On 26-Nov-24: Refer to issue no. 12. | Within 03 Months | Corrected
Initial Inspection |  | 4 | Transformer is not properly separated by fire rated construction with other Occupancies/Areas Location: Ground Floor, Beside of South stair | Oil filled transformer shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Switch gears and transformer bays shall be separately housed with a 2-hr rated wll in between. Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Corrected | Jul 2 2017 | On 12-06-17: Corrected. On 21/09/2017: Corrected as per last follow-up inspection. On 26/02/2018: Corrected as per last follow-up inspection. On 19/July/2018: Corrected On 27/05/2019: Corrected. On 09/11/2020: Corrected. On 26/01/2021: Corrected. On 28-Apr-2024: Corrected. On 26-Nov-24: Corrected. | Within 03 Months | Corrected
Initial Inspection |  | 5 | The assembly occupancy (Dining room/Training, E4) is not properly separated with adjacent production floor by fire rated construction. Location: 5th Floor | Separate the assembly area (Dining /Training) from production floor by minimum 2-hr fire rated construction & having direct access atleast with two (02) exit stair. | Corrected | Mar 31 2017 | On 26-01-17: Timeline has been accepted. Work should be completed as per Accord recommendation within requested timeline. On 12-06-17: Corrected. On 21/09/2017: Corrected as per last follow-up inspection. On 26/02/2018: Corrected. On 19/July/2018: Corrected On 27/05/2019: Corrected as per previous follow up. On 09/11/2020: Corrected. On 26/01/2021: Corrected. On 28-Apr-2024: Corrected. On 26-Nov-24: Corrected. | Within 03 Months | Corrected
Initial Inspection |  | 6 | Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | Corrected | Mar 31 2017 | On 26-01-17: Timeline has been accepted. Work should be completed as per Accord recommendation within requested timeline. On 12-06-17: Corrected. For hydrant work few penetration has been found. Factory shall close those penetration after the hydrant work. On 21/09/2017: Corrected as per last follow-up inspection. On 26/02/2018: Corrected . On 19/July/2018: Corrected On 27/05/2019: Corrected. On 09/11/2020: Corrected. On 26/01/2021: Corrected. On 28-Apr-2024: Corrected on previous follow up. Factory shall ensure that all penetration on stairs has been sealed properly. On 26-Nov-24: Corrected. | Within 03 Months | Corrected
Initial Inspection |  | 7 | The existing fire alarm system is not a listed system and does not provide automatic alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Our Installation work has been completed before. Some documentation work needs to be update according to visitor guideline .However we are working on documentation & it will be completed end of the November-2020. | Jul 2 2017 | On 02/12/2020 T&CVI documents submitted. On 26/02/2018: Progress done . Installation work almost completed. On 19/July/2018: T&C comment (not limited to) on installed Fire Alarm & Detection System is incorporated below: Existing FACP is not fire separated from the fire pump unit (Excessive temperature & Humid condition was encountered in the FACP room). Installed FACP is not protected from the external exposure due to unprotected opening. Fire alarm control panel shall show the supervision & other applicable signal when fire pump unit is operated. All the NAC's shall have to be properly supervised as per NFPA-72 (Additional NAC's shall provide individual trouble signal & be provided with listed power supply as per NFPA-72). Control modules for exhaust fan & fire doors shall be functional. On 27/05/2019: During follow up inspection it was observed that still modification work is in progress. Still high temperature & humid condition was encountered in FACP room. On 09/11/2020: Pre T&C VI found that factory is not ready for full T&C VI. On 26/01/2021: Corrected. See full T&C VI report for details. On 28-Apr-2024: Corrected on last T&CVI. FADS has been found active and functional. During the inspection, Magnetic Door Holder and Exhaust fan has been found interfaced with FACP, MCP has been found functional. Alarm is not consistent on 6th Floor, Provide backbox for Sounder with flasher, relocate the appliances which are installed on ceiling. On 26-Nov-24: Corrected. FACP was found active & normal condition during inspection. | Within 02 Months (Design submission) & 09 Months (Installation) | Corrected
Initial Inspection |  | 8 | Activation of the fire alarm system by a manual fire alarm station provides automatic occupant notification only on the floor of alarm and not throughout the building. | Configure the fire alarm system to initiate automatic occupant notification on all floor levels to facilitate whole-building evacuation upon any manual fire alarm station activation. | Corrected | Jul 2 2017 | On 12-06-17: Corrected. On 21/09/2017: Corrected as per last follow-up inspection. On 26/02/2018: Corrected as per last follow-up inspection. On 19/July/2018: Corrected On 27/05/2019: Corrected as per previous follow up. On 09/11/2020: Corrected. On 26/01/2021: Corrected. On 28-Apr-2024: Corrected. On 26-Nov-24: Corrected. | Within 06 Month | Corrected
Initial Inspection |  | 9 | Inspection, testing, and maintenance for the fire alarm system is not in accordance with NFPA 72 or as per Accord standard | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72 or as per Accord standard. | Corrected | Apr 30 2017 | On 12-06-17: Corrected. On 21/09/2017: Corrected as per last follow-up inspection. On 26/02/2018: Corrected as per last follow-up inspection. On 19/July/2018: Corrected On 27/05/2019: Corrected as per previous follow up. On 09/11/2020: Corrected. On 26/01/2021: Corrected. On 28-Apr-2024: Corrected. On 26-Nov-24: Corrected. | Within 03 Months | Corrected
Initial Inspection |  | 10 | The existing high-rise building with an occupiable floor greater than 23 m (75 ft) above the finished grade is not protected with an approved automatic sprinkler system. The large occupant loads, heavy fuel loading, and anticipated extended egress times warrant sprinkler protection. | Provide an automatic sprinkler protection throughout the building in accordance with NFPA 1 | We have installed everything related to T & C . Now Some documentation work needs to be update according to visitor guideline .However we are working on documentation & it will be completed end of the November-2020. | Apr 30 2017 | On 02/12/2020 T&CVI documents submitted. On 26/02/2018: Progress done. Almost completed. Testing and commissioning is need to verify the system On 19/July/2018: T&C comment (not limited to) on installed Fire Alarm & Detection System is incorporated below: Fire pump room is not properly ventilated. Excessive water dripping was observed when electrical engine pump was operated. Installed PRV & NRV within the diesel pump unit shall be as per NFPA-20. Non-Return Valve (NRV) shall be provided at the Combined Hydrant riser. Store room shall have to be provided with (K=8.00) sprinkler heads. Existing sprinkler heads at the printing section are pendant type whereas no false ceiling was installed at those location. On 27/05/2019: Installation was almost completed (reportedly). Awaiting for re-T&C. On 09/11/2020: Pre T&C VI found that factory is not ready for full T&C VI. On 26/01/2021: Corrected. See full T&C VI report for details. On 28-Apr-2024: Corrected on last T&CVI. SUPS has been found in functional condition. ZCV has been found interfaced with FACP and trigger Alarm during test condition. System has been approved on 26-Jan-2021. Factory shall ensure that riser of STP has been separated from other occupancy. Also ensure that 65 mm landing valve has been installed on stair enclosure [Ground Floor]. On 26-Nov-24: Corrected. | Within 02 Months (Design submission) & 12 Months (Installation) | Corrected
Initial Inspection |  | 11 | Manual on-off switch is provided for [emergency lighting / exit signage] units | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Corrected | Jul 2 2017 | On 12-06-17: Corrected. On 21/09/2017: Corrected. On 26/02/2018: Corrected . On 19/July/2018: Corrected On 27/05/2019: Corrected. Removed. On 09/11/2020: Corrected. On 26/01/2021: Corrected. On 28-Apr-2024: Corrected. On 26-Nov-24: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 12 | New Finding (On 27/05/2019): Storage rooms ( (Finished goods, Maintenance & stationary) and process areas used for combustible storage are not separated by fire rated construction on 7th, 2nd & ground floors. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) and maximum area of 23m2 (250 ft2) – If sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (1,000 ft2) Separate areas of unenclosed combustible storage by a minimum clear distance of 3m (10ft.). | Already Done | Jan 31 2020 | On 27/05/2019: New Finding On 09/11/2020: Corrected. Note: In process storage shall be maintained as per standard. On 26/01/2021: Corrected. In process storage was found within limit. On 28-Apr-2024: Issue re opened. Room used for storage has been found not separated from production floor on 7th Floor due to penetration and 1st floor due to opening. Moreover, area used for combustible has not been separated from other occupancy on 3rd Floor. On 26-Nov-24: Corrected. Store room has been separated and in process storage area was found within limit. | Within 1 month | Corrected
Follow Up Inspection |  | 13 | New Finding (On 27/05/2019): Unsealed penetrations and openings are located in south-west exit stair (stair-4) enclosure throughout the building. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation as per Accord standard 6.3.1.3. | Already Done | Jun 27 2019 | On 27/05/2019: On 09/11/2020: Corrected. Penetrations in exit stair (stair-4) enclosure has been sealed. On 26/01/2021: Corrected. On 28-Apr-2024: Corrected. On 26-Nov-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 14 | New Finding (On 8th FUI): Fire Rated door has been found under unauthorized maintenance (Welding) so that the integrity of the fire rated doos has not been ensured. Location: Stair-1,2,3 and 4. | Factory shall ensure that the maintenance work shall be done for the door hardware and accessories on a regular basis as per NFPA 80 and manufacturer's published guideline. Repair/ replace the hardware and accessories which are not functional or under unauthorized maintenance. | Corrected | Jul 28 2024 | RPO Comments: On 25/02/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 28-Apr-2024: New Findings. On 26-Nov-24: Factory has changed some of the fire doors. 2/3 doors were found under unauthorized maintenance (welding). | Within 3 months | Pending Verification
Follow Up Inspection |  | 15 | New Finding (On 9th FUI): Penetrations through floor/ceiling assemblies (floor to floor opening by glass partition in exterior wall and pvc toilet pipe) are found unsealed. | Seal/protect all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's guideline &certified design by listing authority. Openings in the exterior wall in two consecutive floors lying within 1.5 m laterally shall be separated with a flame barrier as similar as sunshades or cornices or projected wall at least 75 cm from the external face of the exterior wall. The flame barrier shall have a fire resistance rating of not less than three-fourths hour. For Interim Building, BNBC 2006 Part III chapter 3 clause 3.1.7.2 and for new building, BNBC 2020 Part III chapter 3 clause 3.1.9.2 | We are working in this issue. | Feb 26 2025 | RPO Comments: On 25/02/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 26-Nov-24: New Finding | Within 3 months | In Progress
Follow Up Inspection |  | 16 | New Finding (On 9th FUI): The egress court serving as a portion of the exit discharge path is not separated from the building interior (cable riser, openings, office). Also some portion of the egress court is neither open to sky and nor provided with a fire resistance rated enclosure. Location: stair-1 & 4 egress court. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. | We are working in this issue. | Feb 26 2025 | RPO Comments: On 25/02/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 26-Nov-24: New Finding | Within 3 months | In Progress

## Electrical
Date
03-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB APPARELS LTD, 225, SINGAIR ROAD, HEMAYETPUR, SAVAR, Area: Mouchak, Dhaka
Date of Inspection |  | 2016-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Electrical SLD shall be amended properly; all the required information must be mentioned there; and it shall be updated when you do significant amount of changes of your electrical system. | Corrected | Jul 30 2017 | On 12/06/2017: Not Corrected. New committed time line is given till 30/07/2017 to close this issue. On 21/09/2017: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) drawing is unavailable | Factory should design Lightning Protection System (LPS) for the whole factory (where the Risk index is more than 40). Once a LPS is designed properly, installation must be done accordingly. | Corrected | Jul 30 2017 | On 12/06/2017: Not Corrected. New committed time line is given till 30/07/2017 to close this issue. On 21/09/2017: Corrected. | 4 MONTHS | Corrected
Initial Inspection |  | 3 | Hot Spots were observed at few points | Hot spots shall be eliminated from entire electrical system and shall be always carried forward. | Corrected | Mar 3 2019 | On 12/06/2017: Corrected. | IMMEDIATE | Corrected
Initial Inspection |  | 4 | No working separation between LT panel/s and HT unit/s (Transformer, HT switchgear. | A working separation between LT and HT is needed be ensured. A brick wall will do it; and adequate working clearance (1.07m) and ventilation must be ensured. | Corrected | Mar 3 2020 | On 12/06/2017: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 5 | Transformer Silica gel is discolored and breather oil cup is empty (filled with other stuffs). | Silica gel shall be changed; or reuse can be done, if color regains after sundry. Transformer breather oil cup shall be filled not more than 70% of its capacity. | Corrected | Mar 3 2021 | On 12/06/2017: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 6 | Cables running along the ladder are not covered and it makes obstacle in the working area around the transformer. | Cables along the cable tray/s shall be covered and the cover shall be capable enough to use as working platform. | Corrected | Oct 11 2017 | On 12/06/2017: Not Corrected. New committed time line is given till 30/07/2017 to close this issue. On 21/09/2017: Not Corrected. On 26/02/2018: Not Corrected. On 19/07/2018: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 7 | Cables (laid on floor) are not protected and supported. | Power cables shall be supported by cable tray (ladder- where needed. | Corrected | Mar 3 2023 | On 12/06/2017: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 8 | Wooden board is used for supporting motor base. Again, power socket laid on floor. | All electrical installation shall be installed rigidly using permanent means and avoiding wood and other combustible material. Install power socket at least 200mm above the floor. | Corrected | Mar 3 2024 | On 12/06/2017: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 9 | MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | Corrected | Mar 3 2025 | On 12/06/2017: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 10 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | Corrected | Mar 3 2026 | On 12/06/2017: Corrected. | 2 MONTHS | Corrected
Follow Up Inspection |  | 11 | New Finding: Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must be operated directly using MCB; Pushed ON/OFF circuit can be used. | Corrected | Jul 20 2017 | On 21/09/2017: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 12 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must kept at least 0.9 meter apart from any electrical installation. In unavoidable case heat source shall be covered by proper and adequate insulator. | Corrected | Aug 20 2017 | On 21/09/2017: Corrected. | 2 MONTHS | Corrected
Follow Up Inspection |  | 13 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Corrected | Nov 15 2017 | On 26/02/2018: Not Corrected. On 19/07/2018: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 14 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | Corrected | Nov 15 2017 | On 26/02/2018: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 15 | New Finding: Wiring or extensions to connect equipment/ devices are laid on floors unprotected in flexible PVC. | The cable connection to machines/equipment may be run under the checkered plates (existing) and in trenches or steel conduits. Other options may be to use cable trays and supports to protect from external damages. | Corrected | May 4 2018 | On 19/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 16 | New Finding: Electrical power cables and circuit breakers are not identified properly. | Proper identification shall be done on power cables and circuit breakers used in the system according to SLD. | Corrected | Aug 19 2018 | On 27/05/2019: Not corrected. On 09/11/2020: Not Corrected. They are working on this issue. On 26/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 17 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Corrected | Jul 10 2019 | On 09/11/2020: Not Corrected. They are working on this issue. On 26/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding: Field information has less reflection(transformer impedance, VCB fault clearing set point, pit marking, inadequate ECC, busbar calculation, load marking, individual protection) in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | Corrected. SLD approved by RSC by mail, dated on 22.02.2025. | Feb 4 2024 | RPO Comments: On 25/02/2026 - The design documents (SLD) has been accepted by the RSC. On 30/09/2024: Not Corrected. The factory re submitted SLD to RSC to review. The current status of SLD i s "Need minor Modification". | 2 Months | Pending Verification
Follow Up Inspection |  | 19 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Corrected | Jan 4 2024 | RPO Comments: On 25/08/2024 - The design documents (Proposed layout of Substation room) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. On 30/09/2024: Corrected. The maintenance and operation area shall be obstacle free, and free from all kinds of fall hazard. The floor shall be even and all trench cover shall be aligned with the floor level such that none can get injured for the uneven heights. | 1 Month | Corrected