## Structural
Date
09-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB Mart Fashion Wear Ltd., Plot No 786, Kakil Sataish Borodawra, 13/3, Purbopara Mudafa, Tongi, Gazipur, Gazipur
Date of Inspection |  | 2015-04-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The factory has not obtained the Occupancy Certificate from the concerned authority. | Apply for issuance of Occupancy Certificate from concerned authority. | N/A | Jul 15 2015 | On 21th July 2019: Not applicable. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. | Jul 15 2015 | Corrected
Initial Inspection |  | 2 | After conducting ferro-scanning, it has been found that, rebar number in central column (8#20 mm dia) is not matching with column schedule given in structural documents (10#20 mm dia). Also, column schedule of the extended portions are not available. | In conjunction with preparing credible as-built documents as per the requirements of Alliance Standard section 8.20, conduct ferro-scanning to validate the in-situ reinforcing configuration within structural elements. | Completed | Jan 11 2017 | On 21th July 2019: As-built drawing has been produced and accepted as a part of DEA. The DEA of Building-A (5 storied building has been accepted from Alliance on 24th Aug 2016 and DEA of Building-B (6 storied Building), single story Embroidery shed, as-built drawing of some ancillary structures have been accepted from Alliance on 23rd Oct 2018. During inspection as-built drawing was matched with the as-built condition. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. DEA was accepted by Alliance. On 20-Nov-2024: Corrected previously. The as-built drawing was found satisfactory with the on-site condition. | Jul 15 2015 | Corrected
Initial Inspection |  | 3 | A soil test report dated March'05 is available for review and kept on-site. After reviewing the report it has been noted that, geotechnical investigation was performed by "Geotechnical Engineers and Consultants". Engr. W. Zaman (Sohel) is the Engineer of | Provide the MIEB No. of the Engineer of Record. | Completed | Jan 11 2017 | On 21th July 2019: MIEB No was found in soil test report. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. | Jul 15 2015 | Corrected
Initial Inspection |  | 4 | The available documents do not indicate general conformance with 2006 BNBC or other comparable applicable international model building code. | Engage a qualified structural engineer to develop the required documents (i.e.design report) to confirm the structural integrity of the buildings. Documents must comply with Alliance Standard Part 8 Section 8.19 and 8.20. | Completed | Jan 11 2017 | On 21th July 2019: As-built drawing has been produced and accepted as a part of DEA. The DEA of Building-A (5 storied building has been accepted from Alliance on 24th Aug 2016 and DEA of Building-B (6 storied Building), single story Embroidery shed, as-built drawing of some ancillary structures have been accepted from Alliance on 23rd Oct 2018. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. The DEA of Building-A (5 storied building has been accepted from Alliance on 24th Aug 2016 and DEA of Building-B (6 storied Building), single story Embroidery shed, as-built drawing of some ancillary structures have been accepted from Alliance on 23rd Oct 2018. | Jul 15 2015 | Corrected
Initial Inspection |  | 5 | Following extensions have been done beyond original construction: 1) Cantilever and toilets at north direction of the building, 2) Horizontally extended portion at south direction, 3) Vertically extended portion (4th floor) situated at east di | Have a qualified structural engineer complete an analytical evaluation of the structural impact of the additions. | Completed | Jan 11 2017 | On 21th July 2019: As-built drawing has been produced and accepted as a part of DEA. The DEA of Building-A (5 storied building has been accepted from Alliance on 24th Aug 2016 and DEA of Building-B (6 storied Building), single story Embroidery shed, as-built drawing of some ancillary structures have been accepted from Alliance on 23rd Oct 2018. During inspection as-built drawing was matched with the as-built condition. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. No further extension was observed during inspection. On 20-Nov-2024: Corrected previously. During inspection, Building-A was found 5 storied and Building-B was found 6 storied. No horizontal & vertical extension was found. | Jul 15 2015 | Corrected
Initial Inspection |  | 6 | Two plastic water tanks (each having a capacity of 2000L) are placed on roof surface of 4th floor. No provisions have been made for these concentrated loads. | Engage a qualified structural engineer to confirm and document that provisions have been made to accommodate concentrated loads. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Completed | Jan 11 2017 | On 21th July 2019: Factory has completed retrofitting works in Building-A and Embroidery shed as per accepted retrofitting drawing. Retrofitting completion certificate has also been provided by the factory consultant. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. Three nos 2000L plastic water tanks were observed as per accepted drawing. On 20-Nov-2024: Corrected previously. This issue has been covered under the DEA. The water tank was found as per the accepted floor load plan. | Jul 15 2015 | Corrected
Initial Inspection |  | 7 | As stated by factory authority, the building was constructed in four phases and all the phases were constructed after 2006. There is no indication in the design documents available to understand the consideration of wind and seismic loading during the des | Have a qualified structural engineer document compliance with the seismic and wind requirements stated in the 2006 BNBC. | Completed | Jan 11 2017 | On 21th July 2019: As-built drawing has been produced and accepted as a part of DEA. The DEA of Building-A (5 storied building has been accepted from Alliance on 24th Aug 2016 and DEA of Building-B (6 storied Building), single story Embroidery shed, as-built drawing of some ancillary structures have been accepted from Alliance on 23rd Oct 2018. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. This issue has been covered under DEA. | Jul 15 2015 | Corrected
Initial Inspection |  | 8 | There is no indication in the design documents available to understand the consideration of wind and seismic loading during the design of the building. | Engage a qualified structural engineer to confirm satisfactory structural performance of the buildings under wind loading. | Completed | Jan 11 2017 | On 21th July 2019: As-built drawing has been produced and accepted as a part of DEA. The DEA of Building-A (5 storied building has been accepted from Alliance on 24th Aug 2016 and DEA of Building-B (6 storied Building), single story Embroidery shed, as-built drawing of some ancillary structures have been accepted from Alliance on 23rd Oct 2018. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. This issue has been covered under DEA. | Jul 15 2015 | Corrected
Initial Inspection |  | 9 | Masonry crack has been observed on ceiling and beam of 3rd floor (bonded warehouse). Also, crack has been observed on ceiling of printing room at fourth floor. | Engage a qualified structural engineer to provide additional investigation into the areas of cracking and provide a remediation plan if required. | Completed | Jan 11 2017 | On 21th July 2019: Factory has repaired the crack in some areas but crack was still visible in in some areas of roof slab. Factory is required to repair all cracks as per recommendation in DEA report. On 07-Dec-2021: Factory repaired the cracked areas. During inspection, no further crack was observed. On 20-Nov-2024: Corrected previously. During inspection, no crack was found. | Jul 15 2015 | Corrected
Initial Inspection |  | 10 | Masonry crack has been observed on brick wall of third floor. | Have a qualified structural engineer provide further testing and analysis of cracking in walls and provide a remediation plan to correct noted issues. | Completed | Jan 11 2017 | On 21th July 2019: Factory has repaired the crack in wall as per recommendation in DEA report. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. No crack was observed during inspection. On 20-Nov-2024: Corrected previously. During inspection, no crack was found. | Jul 15 2015 | Corrected
Initial Inspection |  | 11 | - Storage racks at store room of fourth floor, - Storage racks at bonded warehouse of third floor, - Storage racks at ground floor, - Two plastic water tanks on roof level of fourth floor. Indicated non-structural elements need to be braced an | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Completed | Jan 11 2017 | On 21th July 2019: During inspection, all non structural elements were found anchored and braced. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. Racks were anchored. On 20-Nov-2024: Corrected previously. During inspection, storage racks were found anchored. | Jul 15 2015 | Corrected
Initial Inspection |  | 12 | Cracks have been observed on exterior facade of 4th floor (store room) and bathroom on roof top. | Have a qualified structural engineer provide further analysis of the identified cracks to determine the appropriate course of corrective action. | Completed | Jan 11 2017 | On 21th July 2019: Factory has repaired the crack as per DEA recommendation in façade of 4th floor and brick wall of bathroom at roof level has re-constructed. During inspection no crack was visible in any brick wall. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. During inspection, no crack was found on exterior facade. | Jul 15 2015 | Corrected
Initial Inspection |  | 13 | Dampness has been observed on exterior facade of 4th floor. | Repair the exterior façade system to prevent water intrusion. | Completed | Jan 11 2017 | On 21th July 2019: Exterior façade was found repaired. During inspection no dampness was found in any wall. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. No dampness was found. On 20-Nov-2024: Corrected previously. During inspection, no dampness was found. | Jul 15 2015 | Corrected
Initial Inspection |  | 14 | No such program is available to ensure that the live loads for which a floor or roof is or has been designed will not be exceeded. | Develop a program to ensure that all live loads for which a floor or roof has been designed for will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Completed | Jan 11 2017 | On 21th July 2019: Load plan has been produced and accepted as part of DEA. During inspection accepted load was found posted at every floor and load was found below the allowable limit (63 psf). On 07-Dec-2021: This issue was corrected in previous follow-up inspection. Accepted load plan(63 psf) was posted. Load was found below 63 psf. On 20-Nov-2024: Corrected previously. During inspection, load plan was found posted & loading was found within allowable limit of 63 psf. | Jul 15 2015 | Corrected
Initial Inspection |  | 15 | No Load Manager is appointed yet. | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to RMG vendors and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | Completed | Jan 11 2017 | On 21th July 2019: Load manager has been appointed and he was present during inspection. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. Load manager was present during inspection. On 20-Nov-2024: Corrected previously. During inspection, Load manager was present. | Jul 15 2015 | Corrected
Initial Inspection |  | 16 | As set of Floor Load Plan is available but not prepared as per Alliance Standard. Also, base (i.e design report) is not available to justify the consideration of load at different zone of the building. | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3. | Completed | Jan 11 2017 | On 21th July 2019: Load plan has been produced and accepted as part of DEA. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. During inspection, load plan was found posted & loading was found within allowable limit of 63 psf. | Jul 15 2015 | Corrected
Initial Inspection |  | 17 | As set of Floor Load Plan is available but not prepared as per Alliance Standard. Also, base (i.e design report) is not available to justify the consideration of load at different zone of the building. No Floor Load Plan is posted. | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. Once prepared post the load plans on each floor of the building as required. | Completed | Jan 11 2017 | On 21th July 2019: Load plan has been produced and accepted as part of DEA. During inspection accepted load was found posted at every floor and load was found below the allowable limit (63 psf). On 07-Dec-2021: This issue was corrected in previous follow-up inspection. Load plan was posted. Loading was found within 63 psf. On 20-Nov-2024: Corrected previously. During inspection, load plan was found posted & loading was found within allowable limit of 63 psf. | Jul 15 2015 | Corrected
Initial Inspection |  | 18 | Standard Load Plans are not available and areas of storage are not marked also. | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Completed | Jan 11 2017 | On 21th July 2019: During inspection load marking was visible in all storage areas and load was found below the allowable limit (63 psf). On 07-Dec-2021: This issue was corrected in previous follow-up inspection. Load plan was posted. Loading was found within 63 psf. On 20-Nov-2024: Corrected previously. During inspection, load plan was found posted & loading was found within allowable limit of 63 psf. Also, load height mark was found posted. | Jul 15 2015 | Corrected
Initial Inspection |  | 19 | Structural drawing is available along with the approval plan (approved by local authority). But, the structural drawing as well have certain lack of information and mismatch with present condition of the building such as: 1) Detail of cantilever at north | Have a qualified structural engineer prepare credible as-built documents based on the requirements of Part 8 Section 8.19 of the Alliance Standard. | Completed | Jan 11 2017 | On 21th July 2019: As-built drawing has been produced and accepted as a part of DEA. During inspection no discrepancy was found. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. The as-built drawing was prepared as a part of the DEA. The as-built drawing was found satisfactory with the on-site condition. | Jul 15 2015 | Corrected
Initial Inspection |  | 20 | During inspection, the following areas are found to be affected by dampness: 1) Ceiling of printing room (4th floor), 2) Masonry wall of store room (4th floor), 3) Wall of bathroom on roof top, 4) Masonry wall of generator room (ground floor), | Under guidance of a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Completed | Jan 11 2017 | On 21th July 2019: Factory has repaired all damp areas and during inspection no dampness was found. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. No dampness was found during inspection. On 20-Nov-2024: Corrected previously. During inspection, no dampness was found. | Jul 15 2015 | Corrected
Initial Inspection |  | 21 | Slabs were constructed with MCAC and roof slab is exposed to rainfall. No protective sealing was available on roof. | Provide a protective coating at the structural elements constructed with MCAC exposed to rainfall or other sources of water. Have protective coating approved by the Alliance or a qualified structural engineer. | Completed | Jan 11 2017 | On 21th July 2019: Factory has provided water proofing and drainage slope on roof slab to prevent water ponding. On 07-Dec-2021: This issue was corrected in previous follow-up inspection. On 20-Nov-2024: Corrected previously. | Jul 15 2015 | Corrected

## Fire
Date
09-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB Mart Fashion Wear Ltd., Plot No 786, Kakil Sataish Borodawra, 13/3, Purbopara Mudafa, Tongi, Gazipur, Gazipur
Date of Inspection |  | 2015-04-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Occupancy certificate for the building was not found. | Apply to FSCD for issuance of occupancy certificate and expedite the matter. | N/A | Jul 3 2015 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jul 3 2015 | Corrected
Initial Inspection |  | 2 | Extinguishers are inspected monthly by factory personnel, but no documents were found in support of i) annual maintenance of extinguishers by a servicing agent nor ii) annual testing of nozzle of CO2 extinguisher. | Establish an inspection, testing, and maintenance program for all fire extinguishers and prepare proper documentation. Program must comply with NFPA 10. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 3 | Fire alarm control panel was not installed. | Install an automatic fire alarm and detection system for the facility. System shall comply with the Alliance Standard and NFPA 72. Consult a qualified fire protection engineer and/or authorized fire alarm company to design and install the system. | Completed and Waiting for Pre T&CVI | Oct 18 2018 | On 18/06/2019: Factory will submit necessary documents and drawings to ACCORD. On 10/03/2020: Factory has installed fire alarm system. But the factory is not ready for Accord T&C according to documents assessment (Pre T&C). On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Factory has already submitted the documents to RSC. On desk review is going on. Awaiting for T&C. On 22/Jun/2022: Factory still is not ready for T&C according to previous onsite and desk review. On 16/11/2022: The factory has applied for T&CVI. On 15-Oct-2024: Pre T&CV has been conducted and found the system requires closer verification inspection. See details on the full Pre T&CV report. On 26-Dec-24: FADS found active and free of any abnormal condition during the inspection. As per last conducted Pre-T&CVI on 15th Oct 2024, FADS requires a Pre-T&CVI Closure Verification. Reportedly, the factory has completed all the modification works as per Pre-T&CVI report and informed the concern RPO as well. On 01-Jun-2025: Pre-T&C Closure verification has been conducted and found the system the FADS is ready for T&CVI. See details on the Pre-T&C Closure verification report. On 10-Sep-25: The T&CVI found that the FADS is required Final Verification Inspection (FVI) after completing the remediation work as per the T&CVI report. For details see the T&CVI report. On 03-Mar-26: Corrected. The FVI found that the FADS is approved. FADS was in normal condition and fully functional. For more details see the FVI report. | Aug 14 2015 | Corrected
Initial Inspection |  | 4 | Aisles are obstructed on 3rd floor by building column, printing table and fabrics. | Remove all impediments, obstructions, and stored materials from the means of egress. Keep all elements of the means of egress (exit path, aisles, stairs, corridors, etc.) continuously free and clear of all obstructions in accordance with Alliance Standard Section 6.3.9. | Ground Floor all Exit Staircase are free from Storage. Fire Door are free from brick & rope. Aisle are free from any Obstructed. | Jan 11 2017 | On 18/06/2019: In progress. On 10/03/2020: Not corrected yet. On 03/03/2021: (Special Inspection): It has been found that maximum aisles are block by storage. In 3rd floor aisles block by printing table. In ground floor all Exit staircase are blocked by storage. Fire door tightened by brick & rope. On 07/12/2021: Same as before. Maximum aisles were found obstructed by storage and building column. On 22/Jun/2022: Corrected. Aisles at 3rd floor has been rearranged and reportedly spaces beside wall is not using for work and found vacant. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | May 22 2015 | Corrected
Initial Inspection |  | 5 | Change in elevation of walking surfaces exceeds 6.35 mm at exit locations on 3rd floor and ground floor. | Provide a uniform slope/ramp for the walking surface. Slope should not exceed 1 in 20 in the direction of travel. Any changes in elevation (protrusions or lips) must not exceed 1/4 in. | Completed | Jan 11 2017 | On 18/06/2019: Removed and not found. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 6 | Occupant loads are not posted anywhere in the factory premises. | Post the occupant load for all assembly and production floor areas in a conspicuous space near the main exit or exit access doorway for the space in accordance with Alliance Standard Section 6.4.4. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 7 | On 3rd floor, aisles width was found to be less than 0.9 m (36 in) and was obstructed with column, printing table and fabrics. | Provide proper aisles marking (clear width minimum 36 in.) and keep aisles free of storage. Relocate the machines accordingly if necessary to provide proper width. The path of egress travel along a means of egress shall not be interrupted by any obstruction. The capacity of the means of egress shall not be reduced along the path of travel. | We provide proper Aisles Mark ( Clear width minimum 36 inch ). We Relocate the machine. We also ensure the path of egress travel are not interrupted by any obstruction. We also ensure the capacity of the means of egress not reduce along the path of travel. | Jan 11 2017 | On 18/06/2019: In progress. On 10/03/2020: Not corrected yet. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Not corrected yet. On 22/Jun/2022: Corrected. Aisles at 3rd floor has been rearranged and reportedly spaces beside wall is not using for work and found vacant. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 8 | The path of egress along the means of egress was sufficient for the occupant load. But on 3rd floor aisles were blocked by building column and printing table. | Provide proper aisles marking (clear width minimum 36 in.) and keep aisles free of storage. Relocate the machines accordingly if necessary to provide proper width. The path of egress travel along a means of egress shall not be interrupted by any obstruction. The capacity of the means of egress shall not be reduced along the path of travel. | We provide proper Aisles Mark ( Clear width minimum 36 inch ). We Relocate the machine. We also ensure the path of egress travel are not interrupted by any obstruction. We also ensure the capacity of the means of egress not reduce along the path of travel. | Jan 11 2017 | On 18/06/2019: In progress. On 10/03/2020: Not corrected yet. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Not corrected yet. On 22/Jun/2022: Corrected. Aisles at 3rd floor has been rearranged and reportedly spaces beside wall is not using for work and found vacant. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 9 | All door widths were greater than 0.8 m, but fire doors with proper rating were not provided. Exits doors are collapsible type and steel swing door. | Replace non-compliant doors and frames in the means of egress with side-swinging doors. Replacement doors shall be a minimum width of 0.8 m (32 in), and are listed, approved, self-closing, fire rated door assemblies (door and frame) with latching panic hardware. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 10 | All paths of egress are not provided with compliant means of illumination. Ordinary CFL bulbs are used as emergency lights in some area, which do not provide sufficient illumination as required in accordance with Alliance Standard. | Install emergency lighting for all paths of egress in accordance with Alliance Standard Section 6.7. Illumination needs to be a minimum of 10 lux for all corridors, exit doors and stairways. Illumination for aisles needs to be a minimum of 2.5 lux. Egress lighting shall be provided with emergency power or supplemented with battery powered lights that provide a minimum of 10 lux for not less than 30 mins in the event of failure of normal lighting. | Completed | Jan 11 2017 | On 18/06/2019: Emergency lights are inadequate. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 11 | Record of verifying emergency power for means of egress illumination was not found. | Develop a testing and maintenance program that ensures the emergency power for all egress lighting is verified at least once per year. If battery-operated lights are used, these lights shall be tested on a monthly basis. Functional testing of battery powered lights shall be provided for a minimum 90 min once per year. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 12 | Door installed in the means of egress are not side-hinged swinging type. Collapsible exit doors are installed from ground to 3rd floor. | Replace non-compliant doors and frames in the means of egress with side-swinging doors. Replacement doors shall be a minimum width of 0.8 m (32 in), and are listed, approved, self-closing, fire rated door assemblies (door and frame) with latching panic hardware. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 13 | There are collapsible doors and steel swing doors in exits with locking arrangements. | Remove all locking devices from all egress doors and means of egress components in accordance with Alliance Standard Section 6.8. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 5 2015 | Corrected
Initial Inspection |  | 14 | Landing width of stair-2 on 2nd floor was less than the width of the stair. Considering landing width (30") as stair width, total stair width becomes 2.03 m; which can serve more than 250 persons. | In Accordance with Alliance Standard Section 6.9.2.2, increase the landing widths to make it equal to the width of the stairs or reduce the overall available capacity of the stairs as calculated in Section 6.5 (this may also effect the maximum occupant load of any floor or story of the building). | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 15 | For both the stairs, handrails are provided only on one side. | Provide handrails on both sides of each stairway. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.). Mount new handrail at a height consistent with existing height (between 30 in. and 44 in). | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 16 | Floor level was mentioned for every floor but stair designation sign was not provided at any floor entrance from the stair to the floor. | Install signage adjacent to each stair door indicating the stair name and the floor level in both English and Bengali. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 17 | Stair-1 terminates at ground floor passageway, where non-rated openings are available from storage room, finishing & storage area and embroidery room. Stair-2 terminates at ground floor, where compressor is installed without fire resistive construct | Remove the compressor from the exit enclosure and relocate in a safe location. Route exits directly to the exterior or provide an exit passageway in accordance with Alliance Standard Section 6.15 or an Egress Court in accordance with Alliance Standard Section 6.17.2 for non-compliant arrangements. Consult a qualified fire protection engineer to design and/or approve the required exit passageway or egress court. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Refer to the issue No# 55. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 18 | Exit signs are placed at entrances to exits, but most of the exit signs were not of the illuminated type. | Provide continuously illuminated exit signs per Alliance Standard Section 6.11. Signs shall be placed at all required exits and along egress paths, especially where there is a change in direction for the path of travel. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 19 | Exit signs are provided with IPS backup but most of the exit signs are not illuminating continuously and not illuminated type. | Provide an emergency power source (battery back-up or connection to emergency power system) for illuminated exit signs. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 20 | No record of testing existing IPS backup power for exit signs was found. | Develop a testing and maintenance program that ensures the emergency power for exit signs is verified at least once per year. If battery-operated signs are used, these signs shall be tested on a monthly basis. Functional testing of battery powered signs shall be provided for a minimum 90 min once per year. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 21 | All exit signs do not have appropriate illumination level and contrasting graphics. | Provide continuously illuminated exit signs at all required exits and along egress paths, especially where path has a change of direction. Exit signs may be illuminated either by lamps exterior to the sign or contained within the sign. The source of illumination shall provide not less than 50 lux at the illuminated surface with a contrast of not less than 0.5. Approved self-luminous signs which provide evenly illuminated letters having a minimum luminance of 0.2 cd/m2 may also be used. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 22 | Roof of the building is unoccupied. However on 4th floor, which is partially occupied, parapet height was found 30 inch. | Provide parapets or guards with a minimum height of 1067 mm (42 in.) for all occupiable roof areas in accordance with Alliance Standard Section 6.12. | Completed | Jan 11 2017 | On 18/06/2019: In progress. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Refer to the issue No# 56. On 03-Mar-26: Refer to the issue No-56. | Nov 6 2015 | Corrected
Initial Inspection |  | 23 | Stair-1 terminates at a non rated passageway and discharges through main exit to outside of the building. Stair-2 discharges through an egress court having 3.5 ft width and non rated window openings to the production floors are found on one side of that e | Route exits directly to the exterior or provide an exit passageway in accordance with Alliance Standard Section 6.15 or an Egress Court in accordance with Alliance Standard Section 6.17.2 for non-compliant arrangements. Consult a qualified fire protection engineer to design and/or approve the required exit passageway or egress court. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Refer to the issue No# 55. On 03-Mar-26: Refer to the issue No# 55. | Aug 14 2015 | Corrected
Initial Inspection |  | 24 | No viable documentation or physical presence of Fire Safety Director were noted. | Create a Fire Safety Director position and fill the position with an individual that has sufficient training to be able to carry out the required duties in accordance with Alliance Standard Section 13.1. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 25 | Through the interview it was noted that the workers are aware of the evacuation procedure upon commencement of the alarm. However, no procedure defining evacuation process was available. Only designated fire fighting, first aid, and rescue team were available. | Develop an emergency evacuation plan in accordance with the Alliance Standard and communicate the plan to all employees. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 26 | Emergency egress maps are not posted on all floors at the entrance to exit of Stair-2 (North Stair). Emergency egress maps are posted for Stair-1 (South Stair). | Create and post emergency evacuation maps at the entrance to each stair or main point of egress. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 27 | Fire department pre-planning was not found. | Complete Fire Department pre-planning activities with the local Fire Service and Civil Defense in accordance with Alliance Standard Section 13.1.1(2). | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 28 | Hot work permit program is not established by the factory authority. | Develop a hot work permit program. The program must comply with the requirements of NFPA 51B. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 29 | Alliance Safety Training was not completed and no documentation of any training program in accordance with the Alliance Safety Training Curriculum was found. | Implement training programs and document in accordance with the Alliance Safety Training Curriculum. | Completed | Jan 11 2017 | On 18/06/2019: N/A On 10/03/2020: N/A On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: N/A On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 30 | Smoking is prohibited in the factory premises as per verbal information from the factory personnel. However no sign is posted in the factory premises. | Smoking is prohibited in garment factory buildings or similar uses. Post "No Smoking" signs in English and Bengali at all building entrances. If the Owner designates a smoking area outside the building, information on the location of these areas shall be posted on the "No Smoking" signs. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 5 2015 | Corrected
Initial Inspection |  | 31 | 1) Fire license, Boiler license, Trade license, Factory license, Boiler license, Boiler operator license are valid and up to date. 2) Electrician license not available. 3) BERC waiver certificate for 132 KW diesel generator is not available. F | Apply to the proper authority and keep all the licenses and permits up to date. | Completed | Jan 11 2017 | On 18/06/2019: N/A On 10/03/2020: N/A On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: N/A On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 32 | Document or certificate from appropriate authority for training on fire fighting, first aid, and rescue was not available. | Need to provide training and certification for the required number of people in fire fighting, first aid, and rescue training by an appropriate authority in accordance with the Alliance Safety Training Curriculum. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 33 | A written housekeeping policy is established and enforced by the factory authority but it is not per Alliance Standard. | Establish written corporate and plant policies on housekeeping to ensure scheduled cleaning for floor, wall, ceiling, supply and return air ventilation systems. Promptly reschedule skipped cleanings. Provide a documented line of authority for authorizing a cleaning delay and rescheduling. As a general rule the maximum tolerable deposit thickness for loose fluffy lint is 13 mm (½ in.) over a maximum of 46.5 m2 (500 ft2). Limit dense deposits to 6 mm (¼ in.) and oil saturated deposits to 3.2 mm (1/8 in.). Establish written corporate and plant policies on housekeeping to ensure scheduled cleaning for floor, wall, ceiling, supply and return air ventilation systems. Promptly reschedule skipped cleanings. Provide a documented line of authority for authorizing a cleaning delay and rescheduling. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jan 29 2016 | Corrected
Initial Inspection |  | 34 | 1) Non rated door opening (steel door) was found at the generator room, which is located in front of main exit discharge on the ground floor of the building. 2) Boiler room has unprotected opening (steel door) with finishing section on ground floor. | Install fire rated doors and windows or fill in unprotected openings with fire resistive rated assemblies. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. They have replaced the position of the room. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 35 | Height of the highest occupied floor is 13.11 m (43 ft) which is above 10 m (33 ft). Class-III standpipe system shall be installed in the building at required locations as per Alliance Standard. One class-II hose connection with attached hose (40 mm | Install standpipe system at required locations. Standpipe system must comply with NFPA 14. The hydraulic calculations should be submitted and reviewed by Alliance prior to start of work. All standpipe system installation activities shall be submitted for reviewed by the Alliance prior to commencement of installation in accordance with Section 5.4.3.2. | Completed and Waiting for Pre T&CVI | Jan 11 2017 | On 18/06/2019: Factory will submit necessary documents and drawings to ACCORD. On 10/03/2020: Factory has installed standpipe system. But factory is not ready for full functional T&C VI according to documents assessment (Pre T&C). On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Factory has already submitted the documents to RSC. On desk review is going on. Awaiting for T&C. On 22/Jun/2022: Factory still is not ready for T&C according to previous onsite and desk review. On 16/11/2022: During follow up inspection it was observed that still the factory has not started modification work after last pre-T&CVI such as all standpipe risers are located inside the floor though factory has applied & submitted design and documents for again T&CVI. On 15-Oct-2024: Pre T&CV has been conducted and found the system requires closer verification inspection. See details on the full Pre T&CV report. On 26-Dec-24: SUPS found active and the fire pump controllers were normal in condition during the inspection. As per last conducted Pre-T&CVI on 15th Oct 2024, SUPS requires a Pre-T&CVI Closure Verification. Reportedly, the factory has completed all the modification works as per Pre-T&CVI report and informed the concern RPO as well. On 01-Jun-2025: Pre-T&C Closure verification has been conducted and found the system (SUPS) is ready for T&CVI. See details on the Pre-T&C Closure verification report. On 10-Sep-25: The T&CVI found that the SUPS is required for Final Verification Inspection (FVI) after completing the remediation work as per the T&CVI report. For details see the T&CVI report. On 03-Mar-26: The FVI found that the SUPS is approved. For details see the FVI report. | Aug 14 2015 | Corrected
Initial Inspection |  | 36 | On the ground floor, the fabric storage area is not properly separated from the finishing area with appropriate fire separation. Compressor is installed under the waist slab of the staircase (stair-2) without any fire resistive construction barrier on ground | Provide fire-resistive rated construction barriers between hazard types in accordance with Alliance Standard Sections 3.4 and 4.5. Consult a qualified fire protection engineer to design the required rated construction barrier. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 37 | Both exit enclosures are not provided with fire separations from the production floor. Collapsible gate and steel swing doors are installed in the exits. | Provide fire-resistive rated construction barriers and associated opening protection for exit enclosures in accordance with Alliance Standard Sections 4.5 and 4.6. Consult a qualified fire protection engineer to design the required rated construction barrier. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 38 | Fire department inlet (Siamese) and outlet connections are not installed. | Provide Fire Department (Siamese) connections in accordance with Alliance Standard Section 5.5.4. Connections shall match the Fire Service and Civil Defense hose thread standard. |  | Jan 11 2017 | On 18/06/2019: Integrated part of hydrant system. Related with issue no. 35 On 10/03/2020: Integrated part of hydrant system. Related with issue no. 35 On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Integrated part of hydrant system. Related with issue no. 35. On 22/Jun/2022: Integrated part of standpipe system. Related with issue no. 35. On 16/11/2022: It is an integrated part of standpipe system. On 15-Oct-2024: Pre T&CV has been conducted and found the system requires closer verification inspection. See details on the full Pre T&CV report. On 26-Dec-24: SUPS found active and the fire pump controllers were normal in condition during the inspection. As per last conducted Pre-T&CVI on 15th Oct 2024, SUPS requires a Pre-T&CVI Closure Verification. Reportedly, the factory has completed all the modification works as per Pre-T&CVI report and informed the concern RPO as well. On 01-Jun-2025: Corrected as per as built system condition. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 39 | Inspection, maintenance, and testing procedures of the existing class-II hose system is not documented per NFPA 25. | Establish an inspection, testing, and maintenance program for the standpipe system. Program must comply with NFPA 25. Any newly installed standpipe system needs to be evaluated for compliance with the design pressure and flow demands of NFPA 14 or BNBC Section 5.4.3. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected as per previous follow up. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Nov 6 2015 | Corrected
Initial Inspection |  | 40 | Fire pump is not provided. Standpipe system is currently fed by overhead reservoir. At 2nd floor, hose pressure was around 2 bar. Overhead water tank capacity is 4000 liter. | Install a dedicated fire pump for the facility in accordance with NFPA 20 to supply the demands of the connected fire protection systems along with a stored source of water sufficient to meet the demands in accordance with NFPA 22. Fire pump installation is to be tested for final acceptance in presence of Alliance and a final inspection of the installation shall be conducted by the Alliance prior to final acceptance of the installation by the Alliance as per clause 5.5.5. Acceptance testing of the installation shall be in accordance with NFPA 20, 22, and 25 testing requirements. Documentation of all testing shall be submitted to the Alliance for review prior to final acceptance by the Alliance. The pump is to be connected to an alternative power source such as a generator. The generator is to be configured with an ATS (auto starter). | Completed and Waiting for Pre T&CVI | Jan 11 2017 | On 18/06/2019: Integrated part of hydrant system. Related with issue no. 35 On 10/03/2020: Integrated part of hydrant system. Related with issue no. 35 On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Integrated part of hydrant system. Related with issue no. 35. On 22/Jun/2022: Integrated part of standpipe system. Related with issue no. 35. On 16/11/2022: It is an integrated part of standpipe system. On 15-Oct-2024: Pre T&CV has been conducted and found the system requires closer verification inspection. See details on the full Pre T&CV report. On 26-Dec-24: SUPS found active and the fire pump controllers were normal in condition during the inspection. As per last conducted Pre-T&CVI on 15th Oct 2024, SUPS requires a Pre-T&CVI Closure Verification. Reportedly, the factory has completed all the modification works as per Pre-T&CVI report and informed the concern RPO as well. On 01-Jun-2025: Pre-T&C Closure verification has been conducted and found the system the system (SUPS) is ready for T&CVI. See details on the Pre-T&C Closure verification report. On 10-Sep-25: The T&CVI found that the SUPS is required Final Verification Inspection (FVI) after completing the remediation work as per the T&CVI report. For details see the T&CVI report. On 03-Mar-26: The FVI found that the SUPS is approved. For details see the FVI report. | Aug 14 2015 | Corrected
Initial Inspection |  | 41 | Call points are provided only at one egress point on each floor. Stand alone smoke detectors are inadequate on all floors. Other visible and audible devices are placed where required but approved shop drawing for the installed system were not found. | Install initiating devices and notification appliances as required by the Alliance Standard and NFPA 72. This includes electrical supervision of all valves controlling fire protection systems (sprinklers, fire pumps, water supplies, etc.). Connect devices to an automatic fire alarm and detection system for the facility. All fire alarm installations shall be submitted for review by the Alliance prior to commencement of installation. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. However it is an integrated part of fire alarm system. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Aug 14 2015 | Corrected
Initial Inspection |  | 42 | Centralized alarm and detection system was not found. | Install a new automatic fire alarm and detection system. Once installed, arrange for direct connection of the fire alarm and detection system to a central station monitoring service or the Fire Service and Civil Defense as per Alliance Standard Section 5.7.5. Until that time, a person trained to contact the Fire Service and Civil Defense in the event of fire alarm activation shall be provided. An annunciator shall be located in a constantly attended location (such as a fire control room) to alert this person. | We already submitted Documents to RSC. On desk review is going on. Awaiting for T & C. | Jan 11 2017 | On 18/06/2019: Factory will submit necessary documents and drawings to ACCORD. On 10/03/2020: Factory has installed fire alarm system. But the factory is not ready for Accord T&C according to documents assessment (Pre T&C). On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Factory has already submitted the documents to RSC. On desk review is going on. Awaiting for T&C. On 22/Jun/2022: Not applicable as FSCD has no centralized alarm and detection system. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 19 2015 | Corrected
Initial Inspection |  | 43 | Fabrics are stored underneath the cutting tables of cutting section on 3rd floor of the building. | Remove all combustibles stored underneath the cutting tables in accordance with Alliance Standard Section 13.7.2. | Completed | Jan 11 2017 | On 18/06/2019: Corrected. On 10/03/2020: Corrected. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Corrected. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. Removed. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Jun 5 2015 | Corrected
Follow Up Inspection |  | 44 | New Finding(1st FUI):The egress path along means of egress has interrupted by obstruction/storage. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Ground Floor all Exit Staircase are free from Storage. Fire Door are free from brick & rope. Aisle are free from any Obstructed. Egress path are free from storage at ground floor. | Jun 21 2019 | On 18/06/2019: New finding. On 10/03/2020: Not corrected. Aisles were found obstructed by column and printing tables. On 03/03/2021: (Special Inspection): It has been found that maximum aisles are block by storage. In 3rd floor aisles block by printing table. In ground floor all Exit staircase are blocked by storage. Fire door tightened by brick & rope. On 07/12/2021: Not corrected. Aisles were found obstructed by column and storage. Egress path was blocked by storage at ground floor. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 45 | New Finding(1st FUI):Liquefied or compressed gas cylinders were located within the factory under the east exit stair. | The storage or use of liquefied or compressed flammable gas cylinders shall be prohibited within the factory building. | Management totally stop uses of Gas Cylinder in Factory Premises. | Jul 18 2019 | On 18/06/2019: New finding. On 10/03/2020: Corrected. No gas cylinder was found during inspection. On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Issue re-opened. Factory still using gas cylinders without proper separation. On 22/Jun/2022: Corrected. No gas cylinder was found during inspection. Factory stated that they are not using gas cylinders. On 16/11/2022: Corrected. Not found during follow up inspection. On 26-Dec-24: Corrected. Not found. On 10-Sep-25: Corrected. Not found during the inspection. On 03-Mar-26: Corrected. Not found during the inspection. | within 1 month | Corrected
Follow Up Inspection |  | 46 | New Finding (2nd FUI): Exit stair door/egress door at 4th floor roof does not swing in the direction of egress travel. | Modify the egress door to swing in the direction of egress travel. | We already modify the egress door to swing in the direction of egress travel. | Apr 10 2020 | On 10/03/2020: New finding On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Not corrected yet. On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 47 | New Finding (2nd FUI): Expose room used as a storage in 3rd floor and areas used for combustible storage in ground floor are not separated by fire rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected. | Apr 10 2020 | On 10/03/2020: New finding On 03/03/2021: (Special Inspection): Not checked during special inspection. On 07/12/2021: Same as before. On 22/Jun/2022: Same as before. On 16/11/2022: Corrected. During follow up inspection process goods storage areas were found as per standard. On 26-Dec-24: Corrected. On 10-Sep-25: Issue re-opened. In-process storage in the production areas was not maintained as per the recommendation in the ground floor finishing section and the 4th floor cutting section. The factory requires to maintain maximum storage height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and storage area do not exceed 10 percent of the floor area of the story in which they occur. On 03-Mar-26: Corrected. In-process storage in the production areas was maintained as per the recommendation during inspection. | Within 1 month | Corrected
Follow Up Inspection |  | 48 | New Finding (3rd FUI): Storage was located underneath the exit stair. | Remove all storage from exit stairs and egress paths. | Already remove all storage from exit stairs and egress paths. | Dec 10 2021 | On 07/12/2021: New finding On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. Removed. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 49 | New Finding (3rd FUI): Storage was found in the dining room. | Remove all storage from dining area. | Dining room are free from all storage. | Dec 10 2021 | On 07/12/2021: New finding On 22/Jun/2022: Corrected. On 16/11/2022: Corrected. Removed. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 50 | New Finding: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | We already increase emergency lighting system for providing adequate illumination for all floor and means of egress as per requirement. | Jul 22 2022 | On 22/Jun/2022: New Finding On 16/11/2022: Corrected. During follow up inspection illumination level was found satisfactory. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | within 1 month | Corrected
Follow Up Inspection |  | 51 | New Finding: No stair landing is provided at roof top floor. | Provide stair landing and modify the egress door to swing in the direction of egress travel in a way that it does not sewing over stair landing and does not reduce the exit width/interrupt the egress path. | Completed and Waiting for Verification. | Jul 22 2022 | On 22/Jun/2022: New Finding On 16/11/2022: Not corrected. During follow up inspection landing space not observed at stair on top floor. On 26-Dec-24: Corrected. The factory has provided Stair landing at roof top floor. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | within 1 month | Corrected
Follow Up Inspection |  | 52 | New Finding: Width of aisles is less than 0.9m (36-in.). (ground floor aisles) | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). | We already take necessary steps for width of Aisles as per instruction in ground floor. | Aug 22 2022 | On 22/Jun/2022: New Finding On 16/11/2022: Corrected. Provided. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | within 2 month | Corrected
Follow Up Inspection |  | 53 | New Finding: The length of dead end distance exceeds 50 ft at ground floor storage and circular knitting section. Length: 82 ft | The maximum length of dead end distance/aisles/corridor shall 50 ft. | Completed and Waiting for Verification. | Aug 22 2022 | On 22/Jun/2022: New Finding On 16/11/2022: The factory has taken initiative to open an exit from knitting section (will be used as a finished goods store instead of knitting section as per factory personnel) on the ground floor. On 26-Dec-24: Corrected. The factory has provided additional exit at North side to omit the dead end at Storage, Ground floor. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | within 2 month | Corrected
Follow Up Inspection |  | 54 | New Finding: Lift machine room is not separated from exit stair. | Separate the lift machine room by a minimum 1.5 hr. fire rated door to separate from stair. Stair shall be enclosed with a minimum 2-hr fire-rated construction. Seal all unprotected openings and provide minimum 1.5-hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | As per requirement of RSC we have already separated the lift machine room by a fire rated door to separate from stair. | Sep 22 2022 | On 22/Jun/2022: New Finding On 16/11/2022: Corrected. The factory has installed fire door in lift machine room on rooftop to separate exit stair enclosure. On 26-Dec-24: Corrected. On 10-Sep-25: Corrected. On 03-Mar-26: Corrected. | within 3 month | Corrected
Follow Up Inspection |  | 55 | New Finding (7FUIN): The exit stair enclosures are not separated from the work area and other spaces due to, - (a) Unprotected opening from medical and childcare room on the ground floor of Stair enclosure-1. (b) Plastic pipes passing through Stair-2 enclosure on every floor. | (a) The exit stair enclosure shall be provided with a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. (b) No other penetration into and through the exit enclosure except for fire alarm equipment electrical raceway, required exit doors, sprinkler piping, standpipes, and electrical conduit serving the exit enclosure is permitted in accordance with section 6.14.4 of RSC Technical Guidelines (Standard)¹ V1.0. So, relocate the utility line to somewhere else avoiding the exit enclosure, and seal the created unprotected openings with a minimum of 1.5 hours listed/certified fire-rated materials. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating. Or, seal the penetration by 2-hr masonry construction. | a) Work in Progress. (Unprotected opening from medical and childcare room on the ground floor of Stair enclosure-1.) b) Corrected. (Plastic pipes passing through Stair-2 enclosure on every floor.) | Dec 10 2025 | On 10-Sep-25: New Finding. On 03-Mar-26: Still the exit stair enclouser-1 is not separated due to unprotected openings of doctor’s room and child-care room on ground floor. The plastic pipe has been removed from the stair-2. | within 3 months | In Progress
Follow Up Inspection |  | 56 | New Finding (7FUIN): Roof of the building on 4th floor is partially occupied, where parapet heights were found to be less than 42 inches. (measured height 37 inches) | Provide parapets or guards with a minimum height of 1067mm (42 inch.) in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.12. | Work in Progress. We are working to ensure minimum 42'' inch parapet height. Hope it be completed soon. | Dec 10 2025 | On 10-Sep-25: New Finding. On 03-Mar-26: Corrected. The factory has increased the parapet wall height to 42 inch. | within 3 months | Corrected

## Electrical
Date
09-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB Mart Fashion Wear Ltd., Plot No 786, Kakil Sataish Borodawra, 13/3, Purbopara Mudafa, Tongi, Gazipur, Gazipur
Date of Inspection |  | 2015-04-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Though electrical drawing is available at site, it is not as built or up to date. | Have a qualified electrical engineer develop an as-built single line diagram detailing key components and the capacity of the electrical system. | Completed | Jan 11 2017 | On 18/06/19: Not Corrected. SLD was almost corrected. Only BBT Breaker marking was not completed. On 10/02/20: Not Corrected. Field information has no/less reflection in existing SLD & also SLD has inadequate information. On 07/12/2021: Not corrected. Submit the SLD at RSC. On 22/06/2022: Not Corrected. SLD is under review process. On 16-Nov-2022: Not Corrected. SLD is not updated properly and is not matching with field. They need to work at field and SLD as well. Comments from CH on 24/07/2023: SLD submitted and waiting for the review from RSC. 17/08/2023: Corrected. The SLD was accepted. During inspection, it was observed that there are few modifications in certain existing panels as well as newly added some panels(SDB-8,7,9,10,11, Maintenance) which are done as per standards. | Jun 21 2015 | Corrected
Initial Inspection |  | 2 | No periodical Insulation Resistance Measurement Program established and recorded. | Develop an Insulation Resistance Measurement Program that ensures deterioration of insulation resistance will be identified quickly. Testing should be in compliance with International Electrical Testing Association (NETA). All transformers, switchgears etc. shall be subject to an insulation resistance measurement test to ground after installation but before any wiring is connected. Insulation tests shall be made between open contacts of circuit breakers, switches etc. and between each phase and earth. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 3 | Thermographic scans of electrical equipment are not completed. | Complete thermographic scans at least on a three year cycle. Thermographic scans should be completed in accordance with the Standard for Infrared Inspection of Electrical Systems & Rotating Equipment and NFPA70B or a comparable standard. | Completed | Jan 11 2017 | On 18/06/19: Not Corrected. Report was outdated. On 10/02/20: Not Corrected. Previous report wasn't found. On 07/12/2021: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 4 | Transformer oil analysis has not been completed on the main service transformer. | Complete an oil analysis on applicable transformers at appropriate intervals based on voltage and power. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 5 | No document found to verify that the transformer does not contain harmful substances such as PCBs. | Consult with manufacturer to determine if transformer contains harmful substances. If harmful substances are found, consider replacing transformers to reduce health hazards. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 6 | Workers that operate and maintain the electrical system have not received electrical safety training. | Develop and implement an electrical safety program. Include key topics such as lock-out/tag-out procedures, personal protective equipment requirements, etc. Keep records of completed electrical training available on site. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 7 | No periodic safety inspections of the electrical system components have been completed and documented. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Maintain records concerning inspections and follow up actions. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 8 | Distribution boards are not provided with adequate clearance. Location: SDB/GF. | Provide clearance of at least 1 m (39 in) in front of switchboards and/or distribution boards. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 9 | Distribution boards are not metal enclosed with dead front construction. Location: All distribution boards. | Ensure distribution boards are metal enclosed with a dead front construction. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 10 | Internal components of distribution boards are not properly concealed. Location: MDB/GF, SDB/1st Floor, SDB/2nd Floor, SDB/3rd Floor. | Provide covers or blanks to conceal all live internal components of switchboards and/or distribution boards. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 17 2015 | Corrected
Initial Inspection |  | 11 | Distribution boards are not properly grounded (earthed). Location: All distribution boards. | Provide grounding (earthing) for switchboards and/or distribution boards as per BNBC section 2.8.1. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 12 | Distribution boards do not have clear identification markings. Location: All distribution boards. | Ensure clear and permanent identification marks are painted in all distribution boards, switchboards, sub main boards and switches. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 13 | Distribution boards do not have capacity information labels. Location: All Distribution boards. | Provide capacity information labels (Maximum current rating, no of circuit breakers etc.) for switchboards and/or distribution boards. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 7 2015 | Corrected
Initial Inspection |  | 14 | Switchboards and/or distribution boards are not provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Ensure switchboards and/or distribution boards provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed following NFPA 70 section 408.54. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 15 | Circuits are drawn for loads without the incorporation of an overcurrent protection device (circuit breaker). Location: SDB/1st Floor. | Ensure overcurrent protection device (circuit breaker) for each and every load. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 16 | Electrical wiring/cables are not properly identified. Location: All Distribution Boards. | Ensure the means of identification is obtained by separate color coding, marking tape, tagging, or other approved means. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 17 | Electrical wiring/cables are not sized according to capacity of circuit breakers. Location: SDB/2nd Floor. | Consult with a qualified Electrical Engineer and ensure electrical wiring/cables are sized according to capacity of circuit breakers. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 18 | Multi looping of wiring/cables observed at circuit breakers within distribution boards. Location: MDB/GF, SDB/GF, SDB/1st Floor, SDB/2nd Floor. | Remove multi looping of wiring/cables at circuit breakers within distribution boards. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 19 | Phase separators are not provided between terminals on circuit breakers. Location: All Distribution Boards. | Install phase separators between terminal connections. Verify phase separators are installed at all remaining locations. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 20 | Electrical wiring/cable is not properly terminated. Location: SDB/1st floor, SDB/3rd Floor. | Ensure all electrical wiring/cable properly terminated at its point of termination. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 21 | Indications of overheating were observed at some locations and the detailed observations were uploaded in thermographic scan report. | Find out the cause of overheating, overloading, or signs of burning and take proper action. Consider replacement of equipment immediately if necessary. | Completed | Jan 11 2017 | On 18/06/19: Corrected. Not got this type of issue during inspection time. | May 17 2015 | Corrected
Initial Inspection |  | 22 | Distribution boards are not clean. Location: MDB/GF, SDB/GF, SDB/1st Floor. | Disconnect the panel from the electrical service and clean interior components of all dust and debris. Seal all openings within the enclosure to prevent dust and debris from entering. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 23 | Electrical insulation mats are not provided in front of substation and distribution boards. | Provide electrical insulation mats in front of distribution boards and substation. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 24 | Each circuit is not provided with a dedicated neutral. Location: SDB/3rd Floor. | Provide dedicated neutral for each circuit. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 25 | Lighting fixtures are not supported from the structure and seismic bracing is not installed as required. Location: 2nd and 3rd floor. | Ensure Lighting fixtures are supported from the structure and seismic bracing is installed as required. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 26 | All metal in the building is not connected to the building earthing/grounding system such as metal rebar in concrete, metal frame of building, or metal water pipe. Location: Throughout the building. | Connect all metal in the building to the building earthing system such as metal rebar in concrete, metal frame of building, or metal water pipe. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 27 | Junction boxes and other electrical devices are not provided with covers. Location: Generator Room. | Provide adequate covers for junction boxes and other electrical devices. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 28 | Cable sockets are not provided for stranded conductors. Location: MDB/GF, SDB/GF, SDB/1st Floor, SDB/3rd Floor. | Provide cable sockets for stranded conductors having a nominal cross-sectional area 6mm2 or greater. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 7 2015 | Corrected
Initial Inspection |  | 29 | Cable joints are not through porcelain/PVC connectors with PIB tape wound around joint. Location: SBD/3rd Floor. | Ensure cable joints are through porcelain/PVC connectors with PIB tape wound around joint. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 30 | Mechanical guards are not provided for electrical equipment and wiring where necessary. Location: SS Room. | Provide mechanical guards for electrical equipment and wiring where necessary. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 31 | Electrical wiring and conduit is not properly supported. Location: COS/Generator Room. | Provide adequate supports for electrical wiring and conduit. | Completed | Jan 11 2017 | On 18/06/19: Not Corrected. On 10/03/2020: Cable should be supported properly. On 07/12/2021: Corrected. | Jun 7 2015 | Corrected
Initial Inspection |  | 32 | Substation room is not clean and free from dirt, lint, oil and debris. Location: SS Room, GF. | Remove all dirt, debris, lint, water, oil, and improperly stored materials from the substation room. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Apr 26 2015 | Corrected
Initial Inspection |  | 33 | The substation room does not have the required fire rating (Fire rated door has not been used) protection and is not physically separated from the remainder of the building. | Consult with an expert fire engineer and provide adequate fire rating/protection for substation room. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 34 | Combustible materials are stored within the substation room. | Remove all combustible materials within the substation room. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Apr 26 2015 | Corrected
Initial Inspection |  | 35 | No signage indicating the prohibition of light fixtures without protective covers is installed at required locations. Location: Bonded warehouse. | Light fixtures without protective covers (otherwise known as naked lights) shall not be allowed in storage areas or in any area where the Inspector of the Factories Rules (1.6.3.7) Part 53 disallows these fixtures. Install signs posted in Bengali and English, indicating this prohibition at all entrances to these areas. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Initial Inspection |  | 36 | Light fixtures without protective covers are installed in storage areas. Location: Finishing section, GF. | Ensure light fixtures without protective covers are not installed in storage areas or in any area where the Inspector of the Factories Rules (1.5.3.5) Part 53 disallows these fixtures. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Apr 26 2015 | Corrected
Initial Inspection |  | 37 | Inspection, maintenance, and testing procedures of the emergency generator are not being completed and documented. | Establish a routine maintenance and testing program for the emergency generator. The program shall be based on all of the following: (1) Manufacturer's recommendations (2) Manufacturer's Instruction manuals (3) Requirements of NFPA 110 Chapter 8. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 21 2015 | Corrected
Initial Inspection |  | 38 | Generator room is not properly rated (Door is not fire rated) and is not physically separated from the remainder of the building. | Ensure the generator room is properly rated and physically separated from the remainder of the building. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 7 2015 | Corrected
Initial Inspection |  | 39 | Generator frame earthing (grounding) is not provided at two separate points. | Provide two separate points earthing (grounding) provided for generator. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 7 2015 | Corrected
Initial Inspection |  | 40 | Emergency power switchboards, distribution boards and circuits are not identified. | All boxes and enclosures (including transfer switches, generators, and power panels) for emergency circuits shall be permanently marked so they will be readily identified as a component of an emergency circuit or system. The required marking can be by color code, the words “emergency system,” or any other method that identifies the box or enclosure as a component of the emergency system. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 18 2015 | Corrected
Initial Inspection |  | 41 | Inspection, maintenance, and testing procedures of the UPS/IPS are not completed and documented. | Establish an inspection testing, and maintenance program for the Uninterruptable Power Supply (UPS) and associated components. The program must based on the following: (1) Manufacturer's recommendations (2) Manufacturer's instruction manuals (3) Minimum Requirements of NFPA 111 Chapter 8 (4) Minimum Requirements of NFPA 70B Chapter 28. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jun 18 2015 | Corrected
Initial Inspection |  | 42 | No lightning protection system is installed on the building. As per BNBC risk assessment calculation, risk index is 44, i.e. greater than 40. So, a lightning protection system is required for the building. | Have a qualified electrical engineer design a lightning protection system according to the BNBC requirements. Have a licensed electrician install the designed system. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | Jul 29 2015 | Corrected
Initial Inspection |  | 43 | Required equipment and safety signage is not posted within the room. | Indoor electrical installations that are accessible to unqualified persons shall be made with metal-enclosed equipment. Switchgear, unit substations, transformers, pull boxes, connection boxes, and other similar associated equipment shall be marked with appropriate caution signs. Entrances to rooms and other guarded locations that contain exposed live parts shall be marked with conspicuous warning signs forbidding unqualified persons to enter. Caution, warning, danger signs or labels should meet the following requirements: (1) The marking shall adequately warn of the hazard using effective words and/or colors and/or symbols. American National Standards Institute ANSI Z535.4-2011, Product Safety Signs and Labels, provides guidelines for suitable font sizes, words, colors, symbols, and location requirements for labels. (2) Shall be permanently affixed to the equipment or wiring method and shall not be hand written. Exception, portions of labels or markings that are variable, or that could be subject to changes, shall be permitted to be hand written and shall be legible. (3) The label shall be of sufficient durability to withstand the environment involved. ANSI Z535.4-2011, Product Safety Signs and Labels, provides guidelines for the design and durability of safety signs and labels for application to electrical equipment. | Completed | Jan 11 2017 | On 18/06/19: Corrected. | May 24 2015 | Corrected
Follow Up Inspection |  | 44 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained with proper separation and adequate ventilation. | Completed | Sep 10 2019 | On 10/02/20: Not Corrected. No Progress observed. On 07/12/2021: Not corrected. Prepare a layout and then do the renovation work. Additionally, HT and LT switchgear are needed to be separated. On 22/06/2022: Not Corrected. No progress found. 17/08/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 45 | New Finding: Inadequate working clearance around the generator. | Working clearance around each generator (and related electrical installations) shall be 1.07m & must be maintained with proper separation and adequate ventilation. | Completed | Sep 10 2019 | On 10/02/20: Not Corrected. No Progress observed. On 07/12/2021: Not corrected. Prepare a layout and then do the renovation work. On 22/06/2022: Not Corrected. No progress found. On 16-Nov-2022: Not Corrected. No progress has been observed. 17/08/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 46 | New Finding: Transformer Oil Test report isn't available in the factory. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | We already test Transformer Oil. | Apr 12 2020 | On 07/12/2021: Not corrected. The report is outdated. On 22/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | We already hang CPR near all electrical equipment. | Apr 12 2020 | On 07/12/2021: Not corrected. On 22/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: No policies for PPE & LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. | We already introduce and implement PPE & LOTO device. | Apr 12 2020 | On 07/12/2021: Not corrected. On 22/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | Completed | Apr 12 2020 | On 07/12/2021: Not corrected. On 22/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Panel body & doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Completed | Apr 12 2020 | On 07/12/2021: Not corrected. On 22/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Circuit breaker rating is not identifiable. | Replace the old breaker with a new one so that anyone can know the ampacity of the breaker. | Completed | Apr 12 2020 | On 07/12/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Power socket is kept on floor. | Power socket shall be install at minimum 200mm above the floor with a rigid support. | Completed | Apr 12 2020 | On 07/12/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: LPS drawing isn’t as built & 150/50 mesh isn't maintained in the roof of 3rd floor. | Design LPS as built with exact measurement & install LPS as per standard. | Completed | May 12 2020 | On 07/12/2021: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 54 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Completed | Apr 12 2020 | On 07/12/2021: Corrected. | 1 Month | Corrected

## Boiler
Date
09-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB Mart Fashion Wear Ltd., Plot No 786, Kakil Sataish Borodawra, 13/3, Purbopara Mudafa, Tongi, Gazipur, Gazipur
Date of Inspection |  | 2022-04-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 9100 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Emergency stop push switches have been arranged near the entrance outside of the boiler room and on the boiler control panel. | Feb 12 2025 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 9100 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Low Low Water Level (LLWL) has been marked properly on water level gauge glass system. | Feb 12 2025 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9100 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Necessary technical documents have been ensured to verify boiler design and operation parameters. | Feb 12 2025 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 9100 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Boiler Safety Valve outlet line rearranged, directed outside of the boiler room. | Dec 12 2024 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 9100 | Direct groundwater is used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. | We are using softner for feed water treatment. | Feb 12 2025 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 9100 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | The boiler manufacturer's nameplate is available on the boiler. | Dec 12 2024 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 14102 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door | Emergency stop push switches have been arranged near the entrance outside of the boiler room and on the boiler control panel. | Feb 12 2025 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 14102 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Low Low Water Level (LLWL) has been marked properly on water level gauge glass system. | Feb 12 2025 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 14102 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Boiler Safety Valve outlet line rearranged, directed outside of the boiler room. | Dec 12 2024 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 14102 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Necessary technical documents have been ensured to verify boiler design and operation parameters. | Feb 12 2025 | Comments on 20-Feb-25: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 14102 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Completed | Dec 12 2024 | Comments on 20-Feb-25: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments On 24-Feb-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 14102 | Fuel gas line pressure relief valve(s) blowoff is not directed to the outside of the boiler room. | Any fuel gas line safety valve or pressure relief valve blowoff shall be diverted to the outside of the boiler room (open to atmosphere condition) to prevent gas accumulation in the boiler room. | Completed | Dec 26 2024 | Comments on 20-Feb-25: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments On 24-Feb-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 13 | BB 14102 | The boiler air vent line was not directed to the outside of the boiler room. | The boiler vent line should be directed outside of the boiler room with proper support. | Completed | Dec 12 2024 | Comments on 20-Feb-25: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments On 24-Feb-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 14 | BB 14102 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Completed | Dec 12 2024 | Comments on 20-Feb-25: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments On 24-Feb-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 15 | BB 14102 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | Completed | Dec 12 2024 | Comments on 20-Feb-25: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments On 24-Feb-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 16 | BB 14102 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | Completed | Nov 19 2024 | Comments on 20-Feb-25: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments On 24-Feb-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 WEEKS | Pending Verification