## Structural
Date
24-Jan-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4 Stitch Knit composite Ltd., West Shaildubi, Ward: 05 , Post office & P.S: Kashimpure, Gazipur-1346, Gazipur
Date of Inspection |  | 2019-07-21
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Discrepancies between provided drawing and on site condition (Main Building) | Building engineer to survey the building and update as built drawings reflecting the as constructed condition. | Done | Oct 16 2019 | On 16-Feb-2020: The factory prepared updated as-built structural and architectural drawings for main building. During inspection, the updated drawing was found on-site. However, factory submitted the corrected updated drawings to ACCORD on 26-Feb-2020 which is under review. On 07-Sep-2021: EA has been reviewed and accepted from RSC on 18th July 2021. However, during inspection some discrepancies were found between as-built drawing and as-built condition (location of water tank, indication of false slab in toilet zone). After that factory has updated the as-built drawing as per site condition and submitted to RSC which have been reviewed and found acceptable. On 03-Jan-2022: Corrected in the previous follow-up inspection. EA of the factory has been accepted by RSC. On 11-Oct-2023: This issue was corrected from previous inspection. On 14-May-2024: Corrected previously. As-built drawings have been prepared as part of EA which was accepted by RSC dated 18-July-2021. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Initial Inspection |  | 2 | Implement floor load management program(Main Building) | Factory is required to implement load management program (signage, load restriction height marking) as per floor load plan. | Done | Oct 16 2019 | On 16-Feb-2020: During inspection, load plan was not posted and load height marking was not provided. The factory is required to post and maintain the load plans. Provide load restriction height marking in storage area. On 07-Sep-2021: Load plan has been prepared as a part of the EA and it has been reviewed and accepted by RSC on 18 July 2021. During inspection, accepted load plan was found posted at every floor and load was found below allowable limit (100 psf). However, location of water tank and load plan for roof floor was missing. After that factory has updated the load plan which have been reviewed and found acceptable. On 03-Jan-2022: Corrected in the previous follow-up inspection. EA of the factory has been accepted by RSC. The factory is maintaining accepted load plan of 100 psf. On 11-Oct-2023: This issue was corrected from previous inspection. Load plan has been prepared as a part of the EA which was accepted by RSC on 18 July 2021. During inspection, accepted load plan was found posted at every floor and loading was found below allowable limit (100 psf). On 14-May-2024: Corrected previously. During the inspection, load plan was found posted on the floors and loading was found within allowable limit (5 kPa) of the accepted load plan. On 31-Dec-2024: Corrected previously. During inspection, floor loading was found within the allowable limit (100 psf) of accepted load plan. | (within 6 weeks) | Corrected
Initial Inspection |  | 3 | Implement floor load management program(Main Building) | Continue to implement load plan. | Done | Mar 5 2020 | On 16-Feb-2020: During inspection, load plan was not posted and load height marking was not provided. The factory is required to post and maintain the load plans. Provide load restriction height marking in storage area. On 07-Sep-2021: Load plan has been prepared as a part of the EA and it has been reviewed and accepted by RSC on 18 July 2021. During inspection, accepted load plan was found posted at every floor and load was found below allowable limit (100 psf). However, location of water tank and load plan for roof floor was missing. After that factory has updated the load plan which have been reviewed and found acceptable. On 03-Jan-2022: Corrected in the previous follow-up inspection. EA of the factory has been accepted by RSC. The factory is maintaining accepted load plan of 100 psf. On 11-Oct-2023: This issue was corrected from previous inspection. Load plan has been prepared as a part of the EA which was accepted by RSC on 18 July 2021. During inspection, accepted load plan was found posted at every floor and loading was found below allowable limit (100 psf). On 14-May-2024: Corrected previously. During the inspection, load plan was found posted on the floors and loading was found within allowable limit (5 kPa) of the accepted load plan. On 31-Dec-2024: Corrected previously. Corrected previously. During inspection, floor loading was found within the allowable limit (100 psf) of accepted load plan. | (within 6 MONTHS) | Corrected
Initial Inspection |  | 4 | Possible vertical extension. (Main Building) | In case of extension, detailed engineering assessment to be carried out following BNBC requirement. | Done | Oct 16 2019 | On 16-Feb-2020: During inspection, the factory building was found 3 storied. Possible future vertical extension was found. Factory is required to submit DEA if extension is done. The factory has submitted the corrected as built architectural and structural drawings to ACCORD on 26-Feb-2020 which is under review. On 07-Sep-2021: Factory has submitted a declaration letter regarding no more further vertical extension. During inspection, the factory building was found 3 storied as per accepted as-built drawing. On 03-Jan-2022: Corrected in the previous follow-up inspection. EA of the factory has been accepted by RSC. As per the declaration letter, the factory does not have any intention of vertical extension. On 11-Oct-2023: This issue was corrected from previous inspection. During inspection, Main Building was found 3 storied. On 14-May-2024: Corrected previously. During the inspection, the building was found 3 storied as per the initial report and accepted EA. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Initial Inspection |  | 5 | Slab adequacy check of underground water reservoir.(Main Building) | Building Engineer to check the adequacy of top slab of underground water reservoir for the applied load. | Done | Oct 16 2019 | On 16-Feb-2020: The factory has prepared the documents and submitted to ACCORD on 26-Feb-2020 which is under review. On 07-Sep-2021: This issue has been covered in the EA which has been accepted from RSC on 18 July 2021. As per accepted EA no remediation is required. On 03-Jan-2022: Corrected in the previous follow-up inspection. EA of the factory has been accepted by RSC. As per accepted EA remediation works are not required. On 11-Oct-2023: This issue was corrected from previous inspection. On 14-May-2024: Corrected previously. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Initial Inspection |  | 6 | Slab adequacy check of underground water reservoir.(Main Building) | Implement remediation work if required. | Done | Mar 5 2020 | On 16-Feb-2020: The factory has prepared the document and submitted to ACCORD on 26-Feb-2020 which is under review. On 07-Sep-2021: This issue has been covered in the EA which has been accepted from RSC on 18 July 2021. As per accepted EA no remediation is required. On 03-Jan-2022: Corrected in the previous follow-up inspection. EA of the factory has been accepted by RSC. As per accepted EA remediation works are not required. On 11-Oct-2023: This issue was corrected from previous inspection. EA of the Main Building has been accepted by RSC. As per accepted EA remediation works were not required. On 14-May-2024: Corrected previously. No remediation is required as per the accepted EA. On 31-Dec-2024: Corrected previously. | (within 6 MONTHS) | Corrected
Initial Inspection |  | 7 | Discrepancies between provided drawing and on site condition . (Utility Building) | Building engineer to survey the building and update as built drawings reflecting the as constructed condition. | Done | Oct 16 2019 | On 16-Feb-2020: The factory has updated the as-built structural drawing for utility building and submitted the updated documents to ACCORD on 26-Feb-2020. On 07-Sep-2021: EA has been reviewed and accepted from RSC on 18th July 2021. However, during inspection some discrepancies were found between as-built drawing and as-built condition (size of the floor beam). After that factory has updated the as-built drawing as per site condition and submitted to RSC which have been reviewed and found acceptable. On 03-Jan-2022: Corrected in the previous follow-up inspection. EA of the factory has been accepted by RSC. On 11-Oct-2023: This issue was corrected from previous inspection. On 14-May-2024: Corrected previously. As-built drawings have been prepared as part of EA which was accepted by RSC dated 18-July-2021. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Initial Inspection |  | 8 | Apparently non engineered shed ..(Dining Shed) | Prepare an “as constructed” drawings which reflect the actual site dimensions with complete structural information. | Done | Oct 16 2019 | On 14/11/2021: No timeline extension has been accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 05/10/2021: Factory was required to complete the demolition within 30 September 2021 which is still in progress. No timeline extension has been accepted. Corrective action plan should be completed as per the given recommendation with immediate concern. On 16-Feb-2020: The factory has not prepared the as-built drawings of dinning shed. However, later the factory has decided to demolish the non-engineered shed and on 26-Feb-2020 the factory has submitted the consent letter to ACCORD. On 07-Sep-2021: The factory had submitted a demolition consent letter along with the EA documents which has been accepted from RSC on 18 July 2021. During the inspection it was found that the dinning shed has not demolished yet. Factory is required to complete the demolition within 30 September 2021. On 03-Jan-2022: EA of the factory has been accepted by RSC. As per accepted EA the factory is required to demolish the shed within 30 September 2021. The factory has not started the demolition works. On 11-Oct-2023: Factory has demolished the Dinning shed. On 14-May-2024: Corrected previously. During the inspection, Dining Shed was found demolished. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Initial Inspection |  | 9 | Apparently non engineered shed ..(Dining Shed) | Building engineer to check the capacity of the lightweight steel roof against lateral loading. | Done | Oct 16 2019 | On 14/11/2021: No timeline extension has been accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 05/10/2021: Factory was required to complete the demolition within 30 September 2021 which is still in progress. No timeline extension has been accepted. Corrective action plan should be completed as per the given recommendation with immediate concern. On 16-Feb-2020: The factory has not prepared the documents for capacity check of dinning shed. However, later the factory has decided to demolish the non-engineered shed and on 26-Feb-2020 the factory has submitted the consent letter to ACCORD. On 07-Sep-2021: The factory had submitted a demolition consent letter along with the EA documents which has been accepted from RSC on 18 July 2021. During the inspection it was found that the dinning shed has not demolished yet. Factory is required to complete the demolition within 30 September 2021. On 03-Jan-2022: EA of the factory has been accepted by RSC. As per accepted EA the factory is required to demolish the shed within 30 September 2021. The factory has not started the demolition works. On 11-Oct-2023: Factory has demolished the Dinning shed. On 14-May-2024: Corrected previously. During the inspection, Dining Shed was found demolished. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Initial Inspection |  | 10 | Apparently non engineered shed ..(Dining Shed) | Carry out remedial works resulting from engineering assessment if necessary. | Done | Mar 5 2020 | On 14/11/2021: No timeline extension has been accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 05/10/2021: Factory was required to complete the demolition within 30 September 2021 which is still in progress. No timeline extension has been accepted. Corrective action plan should be completed as per the given recommendation with immediate concern. On 16-Feb-2020: The factory has not prepared the documents for capacity check of dinning shed. However, later the factory has decided to demolish the non-engineered shed and on 26-Feb-2020 the factory has submitted the consent letter to ACCORD. On 07-Sep-2021: The factory had submitted a demolition consent letter along with the EA documents which has been accepted from RSC on 18 July 2021. During the inspection it was found that the dinning shed has not demolished yet. Factory is required to complete the demolition within 30 September 2021. On 03-Jan-2022: EA of the factory has been accepted by RSC. As per accepted EA the factory is required to demolish the shed within 30 September 2021. The factory has not started the demolition works. On 11-Oct-2023: Factory has demolished the Dinning shed. On 14-May-2024: Corrected previously. During the inspection, Dining Shed was found demolished. On 31-Dec-2024: Corrected previously. | (within 6 Months ) | Corrected
Follow Up Inspection |  | 11 | New Finding 1: Dampness observed on beams, stair slabs and different walls throughout the structure. | Factory is required to investigate the extent of dampness and carry out remedial works accordingly. | In progress 27/12/21 | Oct 19 2021 | On 14/11/2021: No timeline extension has been accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 05/10/2021: Factory is required to complete the remediation within 19 September 2021. On 07-Sep-2021: Dampness were found on beams, stair slabs and different walls throughout the structure. Factory is required to investigate the extent of dampness & water penetration and carry out remedial works accordingly. On 03-Jan-2022: The factory has repaired the damp areas. No additional dampness observed. On 11-Oct-2023: This issue was corrected from previous inspection. On 14-May-2024: Corrected previously. During the inspection, dampness was not observed on the beams, stair slabs and walls. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 12 | New Finding 2: Exposed reinforcement | Area identified to be structurally repaired to ensure further corrosion of reinforcement does not occur. | In progress 27/12/21 | Oct 19 2021 | On 14/11/2021: No timeline extension has been accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 05/10/2021: Factory is required to complete the remediation within 19 September 2021. On 07-Sep-2021: During inspection exposed rebar was observed at different location on the roof floor. The factory is required to protect exposed reinforcement to avoid corrosion. On 03-Jan-2022: Exposed rebars are protected by anti corrosive paint. On 11-Oct-2023: This issue was corrected from previous inspection. On 14-May-2024: Corrected previously. On 31-Dec-2024: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 13 | New Finding-3: Undocumented structure (Security Room; area- 175 sft ). Lack of as-built drawing. | Building engineer is required to prepare accurate as-built drawing for the structure and keep at site office which will be verified during the next inspection. | Done. Waiting for the RSC to verify. | Feb 25 2025 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 31-Dec-2024: During the inspection, an undocumented structure (Security Room; area- 175 sft ) was found at factory premises. As-built drawing was found unavailable for the security room. Building engineer is required to prepare accurate as-built drawing for the structure and keep at site office which will be verified during the next inspection. | (within 6 weeks) | Pending Verification

## Fire
Date
24-Jan-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4 Stitch Knit composite Ltd., West Shaildubi, Ward: 05 , Post office & P.S: Kashimpure, Gazipur-1346, Gazipur
Date of Inspection |  | 2019-07-21
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Exit stairs are not separated from work areas & other spaces on each floor by fire-rated construction due to unprotected openings and penetrations. | Separate the exit stairs from work areas and other levels by minimum 2- hr If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. fire-rated construction. Provide minimum 1.5- hr fire rated doors and seal all unprotected openings and penetrations to maintain the fire separation. Ensure that all fire doors are self-closing and positive latching, and are provided with fire exit (panic) hardware where serving production floors or assembly occupancies. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | In Progress. Remediation is not completed yet. | Dec 5 2019 | RPO Comments: On 21/01/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/10/2022: N-W exit stair enclosure is not separated from cutting section at ground floor. Factory shall provide proper documents for listed fire door. Observed some offices and few penetrations at S-E exit stair enclosure. On 11-Oct-2023: Not corrected yet. N-W exit stair enclosure has been separated by fire rated door with cutting section. Factory shall provide proper documents for listed fire door. Moreover the door coordinators at double leaf doors are not functioning properly violating the requirement of self closure of fire doors which may compromise the required rating of exit enclosure separation. Additionally, the office located at the S-E exit stair is still lacking the necessary fire separation. On 10-Nov-24: Exit stairs have not been separated yet. Fire Doors are not functional properly due to Fire Door accessories' non-functionality including door coordinator, door closer, and missing door accessories (i.e. panic hardware, push bar, etc) on several doors. On 23-Jul-25: Same as before. Fire rated doors and it's components were found non functional on several floors. Additionally, doors were held by external objects such as rope, brick etc. | 3 months | In Progress
Initial Inspection |  | 2 | Egress gates on the all floor with locking features are provided at all exits & exit discharge. | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking features complying with ACCORD standard 6.8.2. | Done | Sep 12 2019 | On 03/10/2022: Observed locking features at N-W exit door, finished goods storage and roof top doors. On 11-Oct-2023: Corrected. No locking features were found during the inspection. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | Immediately | Corrected
Initial Inspection |  | 3 | Room on the ground floor used for combustible storage is not separated by a minimum 1-hr fire-rated construction and door has no certification tag. | Provide dedicated storage rooms separated by minimum months 1-hr fire-rated construction and 0.45-min listed door. | Done. Waiting for the RSC to verify. | Dec 5 2019 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: Bonded warehouse at ground floor has been separated but proper documents shall be provided for listed fire door. Storage rooms at 2nd floor are not separated yet. On 11-Oct-2023: Not Corrected yet. Fire door at ground floor bonded warehouse found inoperable. Proper documents for listed fire doors were not provided. Storage rooms at 2nd floor are not separated yet. On 10-Nov-24: No certification tag or listing information has been found on installed fire doors. Required documents for installed fire doors were not found on site. On 23-Jul-25: Listed fire rated door was installed at Ground floor's storage room. However, the door was held by external objects such as rope. | 3 months | Pending Verification
Initial Inspection |  | 4 | Unsealed electrical shaft is located in the fire-rated floor/ceiling assemblies. | Provide a minimum 2-hr fire-rated shaft to separate the months utility risers from each floor level and seal all penetrations in floor/ceiling assemblies to maintain the fire separation. | In Progress. Remediation is not completed yet. | Dec 5 2019 | RPO Comments: On 21/01/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/10/2022: Observed floor to floor penetrations for electrical shaft and toilet. On 11-Oct-2023: Not corrected yet. Unsealed floor/ceiling penetration observed for toilet pipes during inspection. On 10-Nov-24: Unsealed vertical penetrations were found due to electrical cables passing through PVC pipes above the false ceiling areas. Also, plumbing pipes were observed on the west side of the building inside toilet blocks. On 23-Jul-25: Factory re-route the electrical cable riser outside of the building. However, Penetration at Floor to Floor/Ceiling assemblies due to Plastic plumbing pipe was observed at the west side of the building. | 3 months | In Progress
Initial Inspection |  | 5 | The generator room and substation is not separated by fire-rated construction | Separate the generator room by a minimum 2-hr months fire-rated construction. Seal and/or protect all openings to maintain the required fire separations. Provide proper ventilation and consult a qualified engineer. | Done | Dec 5 2019 | On 03/10/2022: Not separated yet. On 11-Oct-2023: Corrected. Separated. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 3 months | Corrected
Initial Inspection |  | 6 | Areas on the 2nd floor used for combustible storage open to the factory is not properly defined and/or not within limits. | Provide defined storage areas and limit the storage months arrangement as follows: Maximum height of 2.45m (8 ft) and maximum area of 23 m2 (250 ft2). If sprinkler protected: maximum height of 3.66m (12 ft) and maximum area of 93m2 (1000 ft2). Separate the areas of unenclosed combustible storage by a minimum clear distance of 3 m (10 ft). | Done. Waiting for the RSC to verify. | Dec 5 2019 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: Observed huge in process storage at 2nd, Mezzanine and Ground floor. On 11-Oct-2023: Not Corrected yet. In-process storage exceeds allowable limit at 2nd floor and ground floor cutting area. On 10-Nov-24: Not corrected. Still, undesignated in-process storage areas have been found exceeding the maximum allowable limit on the 2nd floor. On 23-Jul-25: No progress observed. Remediation has not started yet. Area used for combustible storage were found not separated from production area on all floors. | 3 months | Pending Verification
Initial Inspection |  | 7 | The mezzanine floor exceed allowable limit from ground floor by fire rated months and not separated from ground floor. | Separate the mezzanine floor from ground floor by fire rated construction barrier. ground floor. Seal or/and protected all non openings and penetrations to maintain the required rating. | Done | Dec 5 2019 | On 03/10/2022: Corrected. Separated. On 11-Oct-2023: Corrected. Separated. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 3 months | Corrected
Initial Inspection |  | 8 | Exterior exit stair is not properly separated the building interior. | Exterior exit stairs shall be separated from the building with a rating requirement of 2-hr fire rating for 4 or more stories. The rating of the exterior wall shall extend 3.05 m(10 ft) beyond the ends of the stair structure. | Done | Dec 5 2019 | On 03/10/2022: Corrected. Sealed On 11-Oct-2023: Corrected. Sealed. On 10-Nov-24: Corrected. On 23-Jul-25: Corrected | 3 months | Corrected
Initial Inspection |  | 9 | Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the required fire separation. Penetrations into and through an exit enclosure shall be prohibited with the exception as per Accord 6.14.4. | Done | Dec 5 2019 | On 03/10/2022 Observed few penetrations and some openings at exit stair enclosure On 11-Oct-2023: Corrected. No Penetration were observed during the inspection. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 3 months | Corrected
Initial Inspection |  | 10 | Outward swinging type doors are not provided at the building exits, exit stairs, along egress routes and exit discharge. | Replace all gates, sliding doors and rolling shutters along the means of egress with side-hinged, swinging egress doors, swinging in the direction of egress travel. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Oct 5 2019 | On 03/10/2022: Corrected. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 1 months | Corrected
Initial Inspection |  | 11 | The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed automatic fire alarm systemin accordance with NFPA 72and ACCORD standards | Fire alarm system panel has been activated, tested, and found operational. Alarm functions are working properly.We will apply for the T&C withing 16-02-26 | Apr 5 2020 | RPO Comments: On 21/01/2026 - The Pre-T&C documents have not been submitted yet for Pre-T&C. On 03/10/2022: The proposed drawing has been reviewed by Accord. Installation is almost completed. Some fire door, exhaust fan interfacing work is still pending. On 11-Oct-2023: During the inspection Installation of FADS found completed. Factory shall apply to RSC for Pre T&C immediately. On 10-Nov-24: FACP was found in abnormal (68 troubles, including 29 fire alarms) condition. Reportedly, installation work has been completedn & troubleshooting is going on. Initial design has been reviewed on 27.01.2020. Reportedly, factory shall submit the design and necessary documents for Pre-T&C within Dec-2024. On 23-Jul-25: Reviewed design found on site and installation work is completed. Fire alarm control panel was found in abnormal condition. Factory person mentioned that, After troubleshooting the fire control panel, they will submit the design and documents for pre T&C. | Design within 3 months Install with in 6 months | In Progress
Initial Inspection |  | 12 | Inspection, testing and maintenance of the automatic fire alarm system is not in accordance withNFPA 72. | Inspect, test and maintain the automatic fire alarm system and keep written records on-site, in accordance withNFPA 72. | Done | Jul 5 2020 | On 03/10/2022: Maintaining but not in accordance with NFPA 72. On 11-Oct-2023: Corrected. Documents were provided. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 10 Months | Corrected
Initial Inspection |  | 13 | The factory building has an occupied floor greater than 10m (33ft)and is not provided with standpipe system as per NFPA 14 and fire pumpas per NFPA 20. | Provide standpipe system protection and fire pump in accordance with NFPA 14 and NFPA 20 standards respectively. | Design Drawing form RSC is already approved We have applied for the LC. Due to some financial constraints, it will take a little time. Standpipe sytem protection and fire pump we wil complete the work within 29-06-2026. | Apr 5 2020 | RPO Comments: On 21/01/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/10/2022: The proposed drawing has been reviewed by Accord. But installation work has not been started yet. Pump LC is not opened yet. On 11-Oct-2023: Progress has been observed. Factory already start the remediation process through confirming the vendor and start process to open LC for import all foreign equipment. On 10-Nov-24: No progress found. Installation has not been started yet. LC process has been started but LC has not yet been opened for the fire pumps and standpipe system equipments purchase & installation. On 23-Jul-25: Same as before. Remediation has not started yet. Reviewed design was found onsite. Installation work is not started. | Design within 3 months Install with in 6 months | In Progress
Initial Inspection |  | 14 | Inspection, testing and maintenance of the standpipe system is not in accordance withNFPA 14. | Inspect, test and maintain the automatic sprinkler system and keep written records on-site, in accordance with NFPA 14. | In Progress. Design Drawing form RSC is already approved We have applied for the LC. Due to some financial constraints, it will take a little time. Standpipe sytem protection and fire pump we wil complete the work within 29-06-2026. | Jul 5 2020 | RPO Comments: On 21/01/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/10/2022: Not maintaining yet. LC has not been opened yet. On 11-Oct-2023: Integrated part of standpipe system. On 10-Nov-24: It is an integrated part of the fire protection system. On 23-Jul-25: It is an integrated part of the fire protection system. | 10 Months | In Progress
Initial Inspection |  | 15 | Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 20. | Inspect, test and maintain the fire pump system and keep written records on- site, in accordance with NFPA 20. | In Progress. Design Drawing form RSC is already approved We have applied for the LC. Due to some financial constraints, it will take a little time. Standpipe sytem protection and fire pump we wil complete the work within 29-06-2026. | Jul 5 2020 | RPO Comments: On 21/01/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 03/10/2022: Not maintaining yet. LC has not been opened yet. On 11-Oct-2023: Integrated part of standpipe system. On 10-Nov-24: It is an integrated part of the fire protection system. On 23-Jul-25: It is an integrated part of the fire protection system. | 10 Months | In Progress
Initial Inspection |  | 16 | Fire evacuation maps is not posted at the entrance of the exits at most of the floors. | Fire evacuation maps shall be posted at the entrance to each exits and exit stairs. | Done | Oct 5 2019 | On 03/10/2022: Not found at 2nd floor. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 1 months | Corrected
Initial Inspection |  | 17 | Exit signage not illuminated (burned out, broken, etc. | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs. The source of illumination shall provide not less than 50 lux at the illuminated surface with a contrast of not less than 0.5. Approved self-luminous signs which provide evenly illuminated letters having a minimum luminance of 0.2 cd/m2 may also be used. | Done | Oct 5 2019 | On 03/10/2022: Observed not illuminated exit signage at several places. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 1 months | Corrected
Initial Inspection |  | 18 | Manual on-off switch is provided for emergency lighting and exit signage units. | Remove manual on/off switches from emergency Lighting & exit signage units to prevent them from being switched off. | Done | Oct 5 2019 | On 03/10/2022: Observed manual on off switch at every floor. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected. On 23-Jul-25: Corrected | 1 months | Corrected
Initial Inspection |  | 19 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. | Done | Dec 5 2019 | On 03/10/2022: No action has been taken yet. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected. On 23-Jul-25: Corrected | 3 months | Corrected
Initial Inspection |  | 20 | Building did not have stair designation sign, occupant load sign & floor level signs at required locations. | Provide occupant load sign, stair & floor designation signs at required locations in both. Bengali and English. | Done | Oct 5 2019 | On 03/10/2022: Stair designation sign, occupant load sign & floor level signs have not been found at required locations. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected. On 23-Jul-25: Corrected | 1 Month | Corrected
Initial Inspection |  | 21 | The exit discharge path serving the [N-W exit] is less than 10 ft wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the months building along the discharge path, up to a height of 10 ft, to provide a minimum 1-hr Fire separation. Alternatively, provide a second remote discharge path to the public way (only Include this if feasible). | Done | Dec 5 2019 | On 03/10/2022: Not separated from the building interior. On 11-Oct-2023: Corrected. Separated. On 10-Nov-24: Corrected. On 23-Jul-25: Corrected | 3 months | Corrected
Initial Inspection |  | 22 | Inspection, testing and maintenance of portable fire extinguishers is not accordance with NFPA 10 | Inspect, test and maintain the portable fire extinguishers and keep written records - on site, in accordance with NFPA 10. | Done | Oct 5 2019 | On 03/10/2022: Maintaing but not accordance with NFPA 10. On 11-Oct-2023: Corrected. Documents were provided. On 10-Nov-24: Corrected On 23-Jul-25: Corrected. Maintained. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding (1st FUI): Exit light is not provided at the required places. | Lighted exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated. | Done | Nov 3 2022 | On 03/10/2022: New Finding. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected On 23-Jul-25: Corrected | 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding (1st FUI): Handrail is not provided on both side of the stairs. | Provide handrails on both side of exit stair having a minimum height 34 in. | Done. Waiting for the RSC to verify. | Nov 3 2022 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: New Finding. On 11-Oct-2023: Not Corrected yet. On 10-Nov-24: Not Corrected. Still, handrails have not been provided on both sides of the exit stairs from the 2nd floor to the rooftop. On 23-Jul-25: No progress observed. Remediation has not started yet. | 1 month | Pending Verification
Follow Up Inspection |  | 25 | New Finding (1st FUI): The egress path along means of egress has interrupted by obstruction/storage. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Done | Oct 6 2022 | On 03/10/2022: New Finding. On 11-Oct-2023: Corrected. On 10-Nov-24: Corrected. On 23-Jul-25: Corrected | Immediately | Corrected
Follow Up Inspection |  | 26 | New Finding (2nd FUI): Sliding door was found at Day care. | Remove sliding doors from the means of egress. | Done | Nov 11 2023 | On 11-Oct-2023: New finding. On 10-Nov-24: Corrected. Sliding door has been removed. On 23-Jul-25: Corrected | Within 1 month. | Corrected
Follow Up Inspection |  | 27 | New Finding (2nd FUI): Inspection, testing, and maintenance for the emergency lighting system was not in accordance with the RSC standard. | Inspect, test and maintain the emergency lighting system in the accordance with the RSC standard. Keep written records on-site. | Done | Jan 11 2024 | On 11-Oct-2023: New finding. On 10-Nov-24: Corrected. Maintained as per standard. On 23-Jul-25: Corrected. Maintained. | Within 3 months. | Corrected
Follow Up Inspection |  | 28 | New Finding (2nd FUI): Flammable liquid storage area is not separated by fire-rated construction (openings, non-rated doors, penetrations). Location: Ground floor General store. | Separate the flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Done | Jan 11 2024 | On 11-Oct-2023: New finding. On 10-Nov-24: Corrected. Flammable liquid storage has been removed. On 23-Jul-25: Corrected. Flammable liquid storage was not observed. | Within 3 months. | Corrected
Follow Up Inspection |  | 29 | New Finding (3rd FUI): Floor to floor unsealed penetration was observed between the exterior glass wall and the floor slab connecting all floor levels. Location: East side of the main production building. | Seal the opening and penetrations between the glass wall and floor slab assembly with a minimum 3-hr fire rated listed/certified materials. The installation of such fire-rated materials shall be following certified design. Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. If fire stopping materials with proprietary design are used for seal, then it shall be classified for the purpose it is used for. Also the installation shall be as per the proprietary design it has been tested with. | Done. Waiting for the RSC to verify. | Feb 10 2025 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 10-Nov-24: New Finding. On 23-Jul-25: Significant progress was not observed. Factory sealed one room by brick wall at 1st floor. But other area of 1st and 2nd floor was found unsealed. | Within 3 months. | Pending Verification
Follow Up Inspection |  | 30 | New Finding (3rd FUI): Exit stair-2 is not separated due to unprotected window opening from the compressor room & medical on the ground floor. | Where nonrated walls or unprotected openings enclose the exterior of the stairway and the walls or openings are exposed by other parts of the building at an angle of less than 180 degrees (3.14 rad), the building exterior walls within 3050 mm (10 ft) horizontally of a nonrated wall or unprotected opening shall have a fire-resistance rating of not less than 1 hr. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than ¾ hr. | Done | Jan 10 2025 | On 10-Nov-24: New Finding. On 23-Jul-25: Corrected. Factory sealed the unprotected window opening from the medical room and the compressor room at exit stair-2. | Within 2 months. | Corrected
Follow Up Inspection |  | 31 | New Finding (3rd FUI): Stair designation sign has not been provided at the required locations of the main production building. | Provide stair designation signs and occupant load signs at the required locations. | Done. Waiting for the RSC to verify. | Dec 10 2024 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 10-Nov-24: New Finding. On 23-Jul-25: No progress observed. Stair designation signs has not been provided yet. | Within 1 month. | Pending Verification
Follow Up Inspection |  | 32 | New Finding (3rd FUI): Emergency evacuation map has not been provided at utility building. | Fire evacuation maps shall be posted at the entrance to each exit stair following 13.3.2 of RSC Technical Guideline (Standard) | Done. Waiting for the RSC to verify. | Dec 10 2024 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 10-Nov-24: New Finding. On 23-Jul-25: No progress observed. Remediation has not started yet. | Within 1 month. | Pending Verification
Follow Up Inspection |  | 33 | Unsealed penetrations and openings are located in exit stair enclosures. Electrical cable/ BBT raceway passing through the exit enclosure. Location(s): Stair-1 at Main Production building. | No other penetration into and through the exit enclosure except for fire alarm equipment electrical raceway, required exit doors, sprinkler piping, standpipes, and electrical conduit serving the exit enclosure is permitted in accordance with section 6.14.4 of RSC Technical Guidelines (Standard)¹ V1.0. So, relocate the electrical wires/raceways to somewhere else avoiding the exit enclosure, and seal the created unprotected openings with a minimum of 1.5 hours listed/certified fire-rated materials. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating. Or seal the penetration by 2-hr masonry construction. | Done. Waiting for the RSC to verify. | Oct 23 2025 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 23-July-2025: New Finding | Within 3 Months | Pending Verification

## Electrical
Date
24-Jan-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4 Stitch Knit composite Ltd., West Shaildubi, Ward: 05 , Post office & P.S: Kashimpure, Gazipur-1346, Gazipur
Date of Inspection |  | 2019-07-21
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by a qualified engineer and get it reviewed by Accord. Electrical SLD shall be updated properly when the electrical system is modified. | Done. Remediation is completed and waiting for the RSC to verify. | Dec 5 2019 | RPO Comments: On 21/01/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: SLD has been reviewed but the implementation work is not started yet. On 11/10/2023: Not Corrected. Significance changes were observed during the inspection. SLD needs to resubmit. On 06/03/2024: Not Corrected. SLD got accepted from RSC on July 2021. Major changes has been observed in substation and new generator has also been installed in the facility. Earthing layout also mismatch with as built condition. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will resubmit updated SLD to RSC for further review after completing the renovation work during upcoming eid holiday. On 10/11/2024: Not corrected. Modification has been observed at several areas, however the factory is working to update their SLD and plan to submit it to RSC within 10 days. On 23/07/2025: Not corrected. Significant progress (approximately 30%) has been observed. The factory got accepted SLD from RSC and rectification work needs to be done as per the accepted SLD. | 3 MONTHS | Pending Verification
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index is equal to or greater than 40 (According to BNBC). | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation shall be done accordingly. | Corrected | Jan 5 2020 | On 03/10/2022: Corrected. | 4 MONTHS | Corrected
Initial Inspection |  | 3 | Insulation resistance test of electrical power cables are not performed. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) shall be performed once in every 2 years cycle and recorded (this shall require a complete power shut off). | Corrected | Nov 5 2019 | On 03/10/2022: Insulation resistance test of electrical power cables is not performed yet. On 11/10/2023: Not Corrected. Insulation resistance test of electrical power cables is performed but mismatch found with field. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 4 | Earth Pit resistance record is not available. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. | Corrected | Nov 5 2019 | On 03/10/2022: Earth pit resistance test is not performed yet. On 11/10/2023: Not Corrected. Earth pit resistance test of electrical power cables is performed but mismatch found with field. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 5 | Electric safety training program is conducted but training module is not adequate and has no influence in the factory. | Electrical safety training and awareness programs for the electrical personnel shall be conducted by a qualified engineer. It is a periodic task that which factory shall continue to improve the overall electrical safety situation for the staff. | Corrected | Nov 5 2019 | On 03/10/2022: Electric safety training does not have any influence on the attitude of the electrical personnel. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 6 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electric al maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | Corrected | Nov 5 2019 | On 03/10/2022: Maintenance program schedule does not have any effectiveness. On 11/10/2023: Not Corrected. Maintenance program schedule is not adequate. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 7 | PPE and electrical graded tools are not available for maintenance personnel in the factory. | Factory shall provide proper PPE. For maintenance purposes, all the electrical tools shall be properly insulated, and these insulations shall be checked periodically. | Corrected | Oct 5 2019 | On 03/10/2022: Electrical graded tools are not available. On 11/10/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 8 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hung near all electrical installations (LT panel, MDB, FDB, DB, SDB) at a visible location. | Corrected | Oct 5 2019 | On 03/10/2022: CPR is not available in all places near the panel board. On 11/10/2023: Not Corrected. CPR not found in some required area. On 06/03/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 9 | Inadequate working space around the transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) shall be maintained. | Corrected | Dec 5 2019 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: No progress is observed. On 11/10/2023: Not Corrected. No progress is observed. On 06/03/2024: Not Corrected. Significant progress has been observed. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will complete the renovation work during upcoming eid holiday. On 10/11/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 10 | No working separation between LT (Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT Switchgear). | A working separation between LT and HT shall be ensured. A brick wall will do it; and adequate working clearance (1.07m) and ventilation shall be ensured. | Done | Dec 5 2019 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: No progress is observed. On 11/10/2023: Not Corrected. No progress is observed. On 06/03/2024: Not Corrected. Significant progress has been observed. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will complete the renovation work during upcoming eid holiday. On 10/11/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 11 | Transformer breather wrapped by plastic cover. The silica gel is discolored, and the breather oil cup is empty. | Plastic cover shall be removed from the breather. Silica gel shall be changed, or reuse can be done if color regains after sundry. Transformer breather oil cup shall be filled up to the oil mark on the cup. | Done | Oct 5 2019 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: Breather oil cup is found empty. On 11/10/2023: Not Corrected. Transformer breather is not wrapped by plastic cover but silica gel is discolored. On 06/03/2024: Not Corrected. Transformer breather plastic cover removed, silica gel color is proper but breather oil cup found empty. On 10/11/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 12 | Transformer earthing (body and neutral ) cable size is inadequate. | Equipment earthing cable size shall be increased. The earth cable size shall be determined according to BNBC or Adiabatic method (if possible). Number of earth pits shall be determined by the size of connected earth cable. | Done | Nov 5 2019 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: Both earthing and neutral earthing of the generator & transformer are found inadequate. On 11/10/2023: Not Corrected. Neutral earthing of the transformer are found inadequate. On 06/03/2024: Not Corrected. Significant progress has been observed. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will complete the renovation work during upcoming eid holiday. On 10/11/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 13 | 11kV power cable dropping from the overhead line is not properly supported with the pole. | 11kV distribution power cable shall be fixed with pole properly. | Corrected | Nov 5 2019 | On 03/10/2022: No progress is observed. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 14 | Maintenance movement is an obstacle due to improper cable trench cover in the utility area (Generator/Substation/Boiler/compressor). | Covered cable trench shall be equal to the working floor height. If not, the extended area shall be sloped at both sides to avoid obstacles. | Done | Dec 5 2019 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: No progress is observed. On 11/10/2023: Not Corrected. No progress is observed. On 06/03/2024: Not Corrected. Significant progress has been observed. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will complete the renovation work during upcoming eid holiday. On 10/11/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 15 | Power Cables are hanging without proper support. | Power cables shall be supported by cable tray (ladder where needed). Outdoor arrangements shall be covered. | Corrected | Dec 5 2019 | On 03/10/2022: This issue is not fully addressed yet. On 11/10/2023: Not Corrected. No progress is observed. On 06/03/2024: Corrected. Change over Switch panel has been removed from the place. | 3 MONTHS | Corrected
Initial Inspection |  | 16 | Generator output cables (laid on floor) are not protected and supported. | Service cables from the generator shall be supported at its own breaker's terminal and with a cable tray. | Corrected | Dec 5 2019 | On 03/10/2022: No progress is observed. On 11/10/2023: Not Corrected. Some Cable are not protected and supported yet and also maintenance movement is obstacle due to uneven height of cable trench. On 06/03/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 17 | Inadequate size earth cable connected to the generator frame. | At least two separate earth pits shall be ensured for generator body; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related determined by the size of connected earth factors). Number of earth pits shall be Cable. | Corrected | Nov 5 2019 | On 03/10/2022: No progress is observed. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 18 | Lead acid battery terminals are left open. | Lead acid battery terminals shall be covered/ capped, and rust shall be cleaned. | Corrected | Nov 5 2019 | On 03/10/2022: No progress is observed. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 19 | Excessive temperature is found on the generator body. | Heat shields/blankets shall be installed to shield hot surfaces to protect the component and operator from excessive heat. Proper guards shall be provided after shielding hot surfaces. Blankets on the exhaust manifold, turbocharger housing, and other engine components are not necessary. Suggested to consult with the generator supplier/service provider/expert before doing the job. | Corrected | Nov 5 2019 | On 03/10/2022: No action has been taken yet. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 20 | Distribution boards are not identified properly. | All distribution boards, switchboards, sub-main boards, and switches shall l be marked clearly for proper identification. | Corrected | Nov 5 2019 | On 03/10/2022: No progress is observed. On 11/10/2023: Not Corrected. Some Distribution boards are not identified yet. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 21 | Panel base plates are removed to allow cable entry. | Panel base plates shall be installed, at all times, and cables entering the panel shall be firmly fixed with cable gland. | Done | Nov 5 2019 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: No progress is observed. On 11/10/2023: Not Corrected. No progress is observed. On 06/03/2024: Not Corrected. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will complete the renovation work during upcoming eid holiday. On 10/11/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 22 | Electrical power cables and circuit breakers are not identified properly. | Proper identification shall be done on power cables, and circuit breakers used in the system according to SLD. | Corrected | Dec 5 2019 | On 03/10/2022: No progress is observed. On 11/10/2023: Not Corrected. Some power cables and circuit breakers are found without identification. On 06/03/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 23 | Panel doors are not connected with earth. | All metal installation of the electrical system shall be connected to earth to avoid electrical shock or electrocution. | Corrected | Nov 5 2019 | On 03/10/2022: This issue still exists in a few panel boards. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 24 | Multiple cables (came from different electrical consumers) terminated at MCCB terminals/Busbar. | Each electrical circuit shall be terminated at single MCB/MCCB /Busbar terminal. | Corrected | Nov 5 2019 | On 03/10/2022: Multiple cables terminated at the busbar via a single lug. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 25 | MCCBs /MCBs are not adjusted /selected per load demand. | All the MCCBs /MCBs shall be adjusted /selected per connected load current; if the adjustment is not possible, the replacement will be the only way. | Done. Remediation is completed and waiting for the RSC to verify. | Nov 5 2019 | RPO Comments: On 21/01/202 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: The issue still exists in a few panel boards. On 11/10/2023: Not Corrected. Some MCCBs/MCBs were found that were not adjusted or selected per load demand. On 06/03/2024: Not Corrected. Progress has been observed but till now MCCBs/MCBs adjustment mismatches found during inspection. On 10/11/2024: Not corrected. This issue is related to SLD issue. Factory is working on it. On 23/07/2025: Not corrected. This issue is related to SLD. Rectification work needs to be done as per the accepted SLD. | 2 MONTHS | Pending Verification
Initial Inspection |  | 26 | No/inadequate Earth Continuity Conductor ( for panel board, change-over switch and electrical equipment. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | Corrected | Nov 5 2019 | On 03/10/2022: The issue still exists in the changeover switch. On 11/10/2023: Not Corrected. No progress is observed since last inspection follow-up. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 27 | Cable connected to busbar/ MCCB/MCB terminal without cable lug. | Each electrical circuit shall be terminated at a single busbar/MCB/MCCB terminal using a proper sized cable lug (where applicable). | Corrected | Nov 5 2019 | On 03/10/2022: The issue still exists in the changeover switch. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 28 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing shall be made following proper guidance. | Corrected | Nov 5 2019 | On 03/10/2022: No improper splicing joint is found. | 2 MONTHS | Corrected
Initial Inspection |  | 29 | Distribution Board's top/bottom is left open (typical). | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs, but an adequate ventilation system shall also be ensured. Gland shall be used, where required. | Corrected | Nov 5 2019 | On 03/10/2022: This issue still exists in a few panel boards. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 30 | Circuit is drawn from bus bar without any protective means. | Each electrical circuit shall be drawn from the distribution board busbar using a proper type protection arrangement (MCCB/MCB). | Corrected | Oct 5 2019 | On 03/10/2022: The issue still exists in the changeover switch. On 11/10/2023: Not Corrected. No progress is observed since last inspection follow-up. On 06/03/2024: Corrected. Change over panel has been removed. | 1 MONTH | Corrected
Initial Inspection |  | 31 | Unterminated live wire is kept inside the electrical panel. | All the unterminated live power cables shall be removed as soon as possible. | Corrected | Oct 5 2019 | On 03/10/2022: No unterminated live is found. | 1 MONTH | Corrected
Initial Inspection |  | 32 | Power sockets are hung without proper support. | Power socket shall be installed on rigid support/base securely and at minimum 200mm above floor level. | Corrected | Nov 5 2019 | On 03/10/2022: This issue still exists in the cutting section. On 11/10/2023: Not Corrected. No progress is observed since last inspection follow-up. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 33 | Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Corrected | Nov 5 2019 | On 03/10/2022: The work is not completed yet. On 11/10/2023: Not Corrected. Earth pits are not identify yet. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 34 | Cable trench is uncleaned, and cables are laid on the trench floor. | A cable trench shall always be kept neat and clean; a cable tray shall be installed in the trench to ensure proper support for cables. | Done | Nov 5 2019 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/10/2022: This issue still exists in the substation room and cutting section. On 11/10/2023: Not Corrected. No progress is observed since last inspection follow-up. On 06/03/2024: Not Corrected. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will complete the renovation work during upcoming eid holiday. On 10/11/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 35 | MCCB is installed with in broken enclosure. | Each MCCB/MCB shall be enclosed by proper type material. | Corrected | Nov 5 2019 | On 03/10/2022: The work completed yet. On 11/10/2023: Corrected. | 2 MONTHS | Corrected
Follow Up Inspection |  | 36 | New Finding: Cables passing through the wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slabs shall be protected. Floor-to-floor openings shall be sealed with proper type materials (consult with a fire expert). | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. This issue still exists in some places. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Thermography scanning report is not available. | Thermography survey shall be done and recorded at least twice in a year. | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. Factory conducted thermography scanning report but periodicity not maintained. Recent test conduct on 01-Nov-2022. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Periodicity of the Transformer Oil Test (dielectric strength, moisture content, and flash point) survey is not continued. | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year. If the operation of transformer is 24/7 in the facility twice in a year is a better practice. | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. Not found during inspection. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) shall not be operated directly using MCB; Direct-On-Line (DoL) type control switch shall be used. | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. Some Large exhaust fans are still controlled directly by MCB. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Power socket is kept on the floor unsafely. | Power socket shall be install at minimum 200mm above the floor with a rigid support. | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. Some Power socket are still kept on the floor unsafely. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Phase barriers/ separators are missing in MCCBs. | Phases shall be separated by insulator (a rubber type no-flammable materials shall be used for it). | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. Phase separators are missing in some MCCBs. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs; but an adequate ventilation system shall also be ensured. | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. This issue still exists in some Electrical distribution panels. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Illumination near the panel working area is inadequate. | Adequate illumination shall be ensured in the sub station room thus any maintenance can be done comfortably (150 lux should be maintained). | Corrected | Nov 10 2022 | On 11/10/2023: Not Corrected. Observed inadequate illumination near the panel working area. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Panel/ Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | At least 1 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Done | Dec 21 2023 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 06/03/2024: Not Corrected. Proposed substation layout accepted from RSC on January 2024. Factory is working on it and will complete the renovation work during upcoming eid holiday. On 10/11/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 45 | New Finding: Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | Corrected | Nov 21 2023 | RPO Comments: On 17/01/20234 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | Corrected | Nov 21 2023 | RPO Comments: On 17/01/20234 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 06/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Heat shields/blankets missing to protect component and operator from excessive heat. | Heat shields/blankets must be installed to shield hot surface to protect component and operator from excessive heat. Proper guards shall be provided after shielding hot surface. Blankets on exhaust manifold, turbocharger housing and other engine components is not necessary. Suggested to consult with the generator supplier/service provider/expert before doing the job. | Done | Apr 16 2024 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 10/11/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Done | Apr 16 2024 | RPO Comments: On 30/05/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 10/11/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: The 11kV power cables laid on the substation room floor are creating obstacles in the working areas. | HT cables shall be rerouted avoiding obstacles in the working areas of electrical installations | Done | Jan 16 2025 | RPO Comments: On 27/05/2025 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 23/07/2025: Corrected. | 2 Months | Corrected