## Structural
Date
08-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A M Fashion, Mazu Khan Bazar,Harbaid, Gazipur-1710, Gazipur, Dhaka
Date of Inspection |  | 2021-02-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Lack of information in drawing. | Factory engineer is required to survey the whole structure Factory engineer is required to survey the whole structure and prepare “as constructed” drawings (Architectural & Structural), prepare in compliance with section 1.9.1.2 as per BNBC 2006.in compliance with section 1.9.1.2 as per BNBC 2006. | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | May 2 2021 | On 02-May-2024: This issue is required to be covered under EA. Factory has submitted EA report to RSC which is now under review for pre submission meeting. On 29-Jun-2025: Factory prepared the as-built drawing along with EA which is pending for submission. As per last meeting with RSC, the factory is required to submit the updated document to the RSC within 20 July 2025. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | within 6-weeks | In Progress
Initial Inspection |  | 2 | Lack of information in drawing. | Building engineer to prepare the design document including design report for the full structure, in compliance with section 1.9.1.1 as per BNBC 2006. | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | Apr 12 2021 | On 02-May-2024:This issue is required to be covered under EA. Factory has submitted EA report to RSC which is now under review for pre submission meeting. On 29-Jun-2025: Factory prepared the EA document which is pending for submission. As per last meeting with RSC, submit the updated document to the RSC within 20 July 2025. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | within 6-weeks | In Progress
Initial Inspection |  | 3 | Lack of lateral stability system(Part -B). | Factory engineer is required to check the lateral stability pf the structure and adequacy of the connections as part of Engineering Assessment (EA) in compliance with section 1.9.1 (Part-6, BNBC 2006) | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | Apr 12 2021 | On 02-May-2024: This issue is required to be covered under EA. Factory has submitted EA report to RSC which is now under review for pre submission meeting. On 29-Jun-2025: This issue is required to be covered in the EA, which is pending for submission. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | within 6-weeks | In Progress
Initial Inspection |  | 4 | Lack of lateral stability system(Part -B). | Complete implementation of any remedial works deemed Complete necessary by the Engineering Assessment (EA). | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | Sep 21 2021 | On 02-May-2024: This issue is required to be covered under EA. Factory has submitted EA report to RSC which is now under review for pre submission meeting. On 29-Jun-2025: Once the EA is accepted by the RSC, carryout necessary remedial works. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | within 6-months | In Progress
Initial Inspection |  | 5 | Lack Lack of as -built drawings (Dining Shed). | Building Engineer to survey the whole structure and prepare accurate as accurate as -built drawings in compliance with section 1.9.1.2 as per BNBC. | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | May 2 2021 | On 02-May-2024: No as-built drawing was found onsite. However, during inspection factory management verbally informed that they will demolish the dining shed. The factory is required to submit written declaration letter regarding demolition of dining shed or submit the design documents to RSC for review. On 29-Jun-2025: As per consent leter dining shed will be replaced by new one. Factory prepared the as-built drawing along with EA for the proposed dining shed which is pending for submission. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | within 6-weeks | In Progress
Initial Inspection |  | 6 | Lack Lack of as -built drawings (Dining Shed). | Building engineer to prepare the design document including a design report, and a set of structural drawings in compliance with section 1.9.1.1 and 1.9.1.2 as per BNBC. | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | May 2 2021 | On 02-May-2024: This issue is required to be covered under EA. No design documents were found onsite. However, during inspection factory management verbally informed that they will demolish the dining shed. The factory is required to submit written declaration letter regarding demolition of dining shed or submit the design documents to RSC for review. On 29-Jun-2025: This issue is required to be covered in the EA, which is pending for submission. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | within 6-weeks | In Progress
Initial Inspection |  | 7 | Lack Lack of as -built drawings (Dining Shed). | Complete implementation of any remedial works deemed necessary by the Design Report. | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | Sep 21 2021 | On 02-May-2024: This issue is required to be covered under EA. No design documents were found onsite. However, during inspection factory management verbally informed that they will demolish the dining shed. The factory is required to submit written declaration letter regarding demolition of dining shed or submit the design documents to RSC for review. On 29-Jun-2025: Once the EA is accepted by the RSC, carryout necessary remedial works. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | within 6-months | In Progress
Follow Up Inspection |  | 8 | New Finding 01: Newly constructed structure (Fabric Godown-single storied steel shed) Lack of lataral stability. | The building engineer is required to check the lataral stability system and suggest proper remediation accordingly. | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | Jun 27 2024 | On 02-May-2024: During inspection, a newly constructed single storied steel shed found in the premises. As built drawing and design documents were not available onsite during inspection. The structure has no lateral load transfer media (compression strut) along long direction. Building engineer is required to produce as built drawing and check the lateral stability and adequacy of all structural elements of the structure. On 29-Jun-2025: This issue is required to be covered in the EA, which is pending for submission. RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 9 | New Finding 02: New uncovered structure- single storied Fire Pump Room (160 sft), Substation Room (50 sft) & Securty Room (50 sft) | The building engineer is required to prepare as-built drawings for Substation & Security Room, and conduct an Engineering Assessment (EA) for fire pump room. Submit EA documents to the RSC for review and after finalization carry out remediation as per EA (if required). | We have already submitted all the DA reports, designs, drawings, and retrofitting drawings, reviewed them, and made some corrections. We will submit the hard copies for approval by the end of this month. | Jul 20 2025 | On 29-Jun-2025: New uncovered structure observed in the factory premises- Fire Pump Room, Substation Room & Security Room. The building engineer is required to prepare as-built drawings for Substation & Security Room, and conduct an Engineering Assessment (EA) for fire pump room. Submit EA documents to the RSC for review and after finalization carry out remediation as per EA (if required). RPO Comments On 27-Jan-2026: The design documents of revised DEA is pending to be submitted to RSC. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 10 | New Finding 03: Lack of anchorage of storage racks & water tanks | Anchor/brace all non-structural elements including water tanks and storage racks. | All non-structural elements, including the mentioned water tanks and storage racks, have been properly anchored and braced in accordance with the requirement. The corrective work has been fully completed. | Jul 20 2025 | On 29-Jun-2025: Lack of anchorage observed for storage racks in Production Shed & plastic water tanks on Fire Pump roof. Anchor/brace all non-structural elements including water tanks and storage racks. RPO Comments On 24-Aug-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification

## Fire
Date
08-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A M Fashion, Mazu Khan Bazar,Harbaid, Gazipur-1710, Gazipur, Dhaka
Date of Inspection |  | 2021-02-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Exit Enclosures are not properly fire separated due to some unprotected penetration and openings. Location : Main production building | Provide minimum 1-hr fire rated separation exit enclosure. Provide minimum 1-hr fire rated doors and seal all unprotected openings and penetration to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Completed: We have Already sealed all opening to prevent fire penetration properly . | Jun 21 2021 | On 16-May-2023: Progress has been observed but not corrected yet. All stairs of main production building are not separated on ground floor. Moreover accessories of installed fire fire rated door has been found missing and non functional. On 04-Nov-25: Progress has been observed. Factory has replaced all non-functional fire doors with new ones and separated the ground floor with fire-rated construction. Fire door datasheet & certificate was provided on-site. All the fire doors were properly functional. However, stair separation is not completed due to exposed non-rated constructions in the stair enclsoures and penetrations on the head of wall joint. RPO Comments On 27-Jan-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 2 | Boiler is not properly separated by fire rated construction with other Occupancies/Areas. Location: S-E corner first floor of production building. | Boilers shall be separated from other occupancies by a minimum 1-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location.OrRelocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | We have already separated Boiler room from other occupancies with fire rated wall and instigated Fire Door. | Jun 21 2021 | On 16-May-2023: Corrected based on site condition. Installed electric boiler capacity has been found less then 22.76 Liter. Moreover, the separation from production area has been done by fire rated door with separation wall. On 04-Nov-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas.Location: Ground floor of Production building-1 | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour fire rated construction. | Corrected.Fire rated doors hardware and accessories have been installed as per requirement , now all the fire doors are functional. | Jun 21 2021 | On 16-May-2023: Progress has been observed but not corrected yet. Fire Rated door has been installed but not functional due to missing and non functional door hardware and accessories. On 04-Nov-25: Corrected. Factory has replaced all non-functional fire doors with new ones and separated the ground floor with fire-rated construction. Fire door datasheet & certificate was provided on-site. | Within 3 months | Corrected
Initial Inspection |  | 4 | Generator was not properly separated by fire rated construction from the middle of the Substation/Transformer (Non rated doors, unsealed penetrations and openings, etc.). Location: S-E corner of ground floor production building | Generator room shall be separated from the transformer by a minimum 2-hr fire-rated construction (wall, floor, slab, etc.). Seal all penetrations and openings (door, window, etc.) shall be protected by 1.5-hr fire-rated materials to maintain the fire separation is required. All exhaust systems shall discharge to the exterior of the building in a safe location.Or, Relocate the Transformer to the exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | We have separated Generator properly with fire rated wall construction from the middle of the Substation/Transformer. | Jun 21 2021 | On 16-May-2023: Corrected based on site condition. Generator and Substation has been separated from production area and egress by fire rated door and wall. On 04-Nov-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | Compressor is not properly separated by fire rated construction with other Occupancies/Areas. Location: S-E corner first floor of production building. | Compressor shall be separated from other occupancies by a minimum 1-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location.OrRelocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | Corrected.We have already separated the Compressor by a fire-rated construction wall to close it from other Occupancies/Areas. | Jun 21 2021 | On 16-May-2023: Progress has been observed but not corrected yet. Openings are closed by brick wall but still available on the north side wall of production building. On 04-Nov-25: Corrected. Factory has sealed the penetrations with fire-rated constructions. | Within 3 months | Corrected
Initial Inspection |  | 6 | The exit discharge path is less than 10 ft wide and is not separated from the building interior. Location: W-N side of production building-1 | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. | Corrected.Now exit discharge path is 10 ft wide. | Jun 21 2021 | On 16-May-2023: Progress has been observed but not corrected yet. Some openings has been found on discharge path where 10 feet width has not been maintained. On 04-Nov-25: Corrected. Factory has sealed the window openings with fire-rated constructions as per the recommendation. | within 3 months | Corrected
Initial Inspection |  | 7 | The fire pump room is not properly separated by fire rated construction with other occupancies. Location : near to Dinning shed. | Provide fire pump room with 2 hr. rated fire separation with 1.5 -hr. fire rated door when not sprinkler building in accordance with NFPA 20 Or, Physically separate the pump room from the protected building by a minimum of 50 ft. (15.3 m) in accordance with NFPA 20. | we have alredy separated the fire pum room from the dining section by a fire rated door . | Jun 21 2021 | On 16-May-2023: Progress has been observed but not corrected yet. Opening has been closed and Fire Rated Door has been installed but to ensure the credibility, factory shall provide all required catalog and certificate of Fire Rated Door on next follow up inspection. On 04-Nov-25: Corrected. Previously installed fire door has been replaced with new one which was properly functional. Fire door datasheet & certificate was provided on-site. Openings and penetrations have been sealed with fire-rated constructions on all sides. | within 3 months | Corrected
Initial Inspection |  | 8 | Childcare & dinning are not properly fire separated due to some unprotected penetration and openings. | Seal all penetrations and openings assemblies by fire-rated materials to maintain the fire-resistance rating. | we have already seal all penetrations The child care room | Jun 21 2021 | On 16-May-2023: Progress has been observed but not corrected yet. Opening has been closed and Fire Rated Door has been installed but to ensure the credibility, factory shall provide all required catalog and certificate of Fire Rated Door on next follow up inspection. On 04-Nov-25: Corrected. Previously installed fire door has been replaced with new one which was properly functional. Fire door datasheet & certificate was provided on-site. | within 3 months | Corrected
Initial Inspection |  | 9 | The main structural element of the building is constructed by steel which is non-rated and were found in exposed condition without any fire protection. | Construction of new non-high-rise factories containing G and/or H2occupancies (factories) shall be Type 1or Type 2 construction as required in NBC Part 3 Table 3.2.4.Provide/ensure required fire rating on the structural elements by following Section 4.4 and Table 4.4.1 of the Accord Standard or Table 3.3.1 and Table 4.1.1 from BNBC. Consult a qualified fire protection engineer to design the rated construction barriers in-between two floors and in structural members. | In Progress: we have already submitted the design philosophy report . The RSC team has reviewed the report and made some correction. We will submit the corrections in the report within the timeline . | Sep 21 2021 | On 16-May-2023: No significant progress has been found. Reportedly factory is in planning stage and currently product selection process is on going. Prior to installation of passive fire protection system, factory shall share all documents, designs and drawings to RSC for review. Moreover newly occupied storage shed under this ID has been found constructed and occupied with approved design from the appropriate building approval authority after 11 February 2021 hence not fall under the requirements of interim building. The factory persons need to review the building's architectural setup to ensure the requirement of new construction if applicable. On 04-Nov-25: Factory has been waiting for DEA report from the Structural Safety Department to confirm the structural integrity, which is under review. However, as per the resolution from the "Ministry of Housing and Public Works”, based on the recommendations from the House Building Research Institute (HBRI) and the Public Works Department (PWD) to assess structural fire protection requirements of steel buildings (unprotected non-combustible construction type) according to BNBC 2020. During the inspection, it was found that the Height of the building is less than 11 m (up to peak). The aggregate of 2 x (Front Road Width + Front Open Space) equals 21 m. Based on this, as per section 1.9.2.4 and table 3.1.7 of BNBC 2020, the building is considered as Type I-E construction. Measurements on all sides: South: 5.5 ft to B. Wall, then 30 ft main road; North: 4.5 ft to B. Wall then other property; East: No space for B. Wall and other property; West: 4.5 ft to B. wall, then Average 5 ft distance to Fabric Godown; partially 16 ft away dining shed. As per the mentioned fire separation distances, the exterior wall ratings were not ensured. Mixed occupancy separation must be ensured, and the exterior walls shall have a fire resistance and opening protection as specified in BNBC 2020 Part 3 Table 3.2.2 & 3.2.3 and BNBC 2020 Part 3 Section 2.4.1.3. Additionally, factory shall ensure the 2nd floor exterior wall separation from the non-rated single-storied portion (roof) of the building on the North side as per BNBC 2020, Table 3.2.2. The newly occupied Fabric Godown (storage shed) height is less than 8 m (up to peak). Based on this, as per section 1.9.2.4 and table 3.1.7 of BNBC 2020, the building is considered as Type I-E construction. Measurements on all sides: South: 14 ft to B. Wall, then 30 ft main road; North: 5 ft to B. Wall, then other property; East: 5 ft to B. wall, then 4.5 ft distance to Main Building; West: 5 ft to B. wall and 12 ft road. As per the mentioned fire separation distances, the exterior wall ratings were not ensured. Mixed occupancy separation must be ensured, and the exterior walls shall have a fire resistance and opening protection as specified in BNBC 2020 Part 3 Table 3.2.2 & 3.2.3 and BNBC 2020 Part 3 Section 2.4.1.3. If any pending issues (i.e. Mixed occupancy separation etc.) in the fire CAP (other than unprotected steel structure) partially depend on the rating of any structural member, then other associated items shall be verified independently, and the rating of those structural members are to be taken only into consideration as a part of the remedial scheme for that issue. RPO Comments On 27-Jan-2026: The design documents of revised is pending to be submitted to RSC. | Within 6 months | In Progress
Initial Inspection |  | 10 | Headroom for the exit door (pocket gate) were not found as per standard. Location: West side exit stair of production building. | The minimum headroom shall be 2.03m (6 ft 8inch) | Corrected.We have already modified all pocket gates,now the exit door's hight is 2.03 meter. | Apr 21 2021 | On 16-May-2023: Not corrected yet. Headroom height has not been maintained on several location including storage room and stair discharge. On 04-Nov-25: Corrected. Headroom height is maintained as per the recommendation. | Within 1 month | Corrected
Initial Inspection |  | 11 | Egress gates with locking features are provided at ground floor discharge position all exit.Location: Production building-1 | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking featurescomplying with NFPA 101. | We already removed lock from all gates. | Mar 28 2021 | On 16-May-2023: Corrected. Not found. On 04-Nov-25: Corrected. Non-compliant locking features were not found with exit doors. | Immediately | Corrected
Initial Inspection |  | 12 | Electrical panel boards located on the south side exit stair of ground floor production building. | Remove and relocate electrical panel boards from exit stairs. | We have already removed and relocated the electrical panel board from the exit stair. | Apr 21 2021 | On 16-May-2023: Corrected. Removed from the stair enclosure. On 04-Nov-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 13 | The egress path along the means of egress has been interrupted by obstruction/storage. Location: East side of ground floor production building. | Means of egress shall be maintained continuously free and clear of all obstructions/storage.OrAisles shall be provided with a minimum unobstructed clear- with of 0.9m (36 in). | We already completed this. | Mar 28 2021 | On 16-May-2023: Corrected. No interruption has been found. On 04-Nov-25: Corrected. No storages were observed along the egress paths. | Immediately | Corrected
Initial Inspection |  | 14 | Obstructions (Generator) were located on the exit pass way of the dinning area . | Keep egress paths way clear of obstructions/storage. | We already cleared obstruction from the exit pass. | Apr 21 2021 | On 16-May-2023: Corrected. No obstruction has been found. On 04-Nov-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 15 | Storage were observed underneath the cutting tables. | Storage underneath the cutting tables shall be kept clear of combustibles at all time, except as provided for miscellaneous storage in accordance with Accord building standard section 3.4.2.1.6 or where automatic sprinkler protection is installed. Where an automatic sprinkler system is installed sprinklers are required to be installed beneath cutting tables greater than 4 ft in width that are used for storage of combustibles. | We have already cleared underneath the cutting tables. | Apr 21 2021 | On 16-May-2023: Corrected. Not found. In process storage arrangement has been maintained as per recommendation. On 04-Nov-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 16 | Storage located in the dining area. | Remove storage from the dining area. | We already removed storage from the dining area.. | Apr 21 2021 | On 16-May-2023: Corrected. Storage has been removed. On 04-Nov-25: Corrected. No storages were observed in the dining area. | Immediately | Corrected
Initial Inspection |  | 17 | Egress gates with locking features are provided at ground floor discharge position all exit.Location: Dinning shed | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking featurescomplying with NFPA 101. | We already removed lock from all gates with complying with NFPA101 | Apr 21 2021 | On 16-May-2023: Corrected. Non compliant locking feature has been removed. On 04-Nov-25: Corrected. Non-compliant locking feature were not found with egress gates. | Immediately | Corrected
Initial Inspection |  | 18 | Sliding gates are provided of Dining shed & store room (Main building-Ground Floor) | Replace all gates along the means of egress with side hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | We already removed lock from all gates with complying with NFPA101 | Apr 21 2021 | On 16-May-2023: Corrected. Pocket gate with outside swing has been provided. On 04-Nov-25: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 19 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Now we are routinely checked and we have record also. | Jun 21 2021 | On 16-May-2023: Corrected. On 04-Nov-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 20 | The Required Fire Alarm system is not installed in accordance with the ACCORD standard and NFPA-72. | Submit design to RSC for review and modify installation if required. Installation of Fire Alarm system should be in accordance with ACCORD standard and NFPA 72. | Already we submitted the design to RSC for review and fire alarm system installation is done according to NFPA-72 standard. | Jul 21 2021 | On 16-May-2023: During the day of FUI, Pre T&C also has been conducted and found FADS not ready for Full T&CVI and requires On Desk review. On 20/02/2024: The T&C VI of Fire Alarm & Detection System has been conducted on dated 20/02/2024. The system is required Final verification inspection. On 26/06/2024: Corrected. FADS FVI was conducted & it was found that the system was functional & approved. See details in the FVI report. On 04-Nov-25: Corrected. FACP was found functional & no trouble was observed during the inspection. | Design within 2 months, Install within 4 months (If modification required | Corrected
Initial Inspection |  | 21 | Inspection, testing, and maintenance for the fire alarm system is not in accordance with NFPA 72 or as per Accord standard. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72 or as per Accord standard | Now we are checking and keeping all records as per Accord standards. | Jun 21 2021 | On 16-May-2023: Not Corrected. Factory Shall maintain the record as per RSC Fire Safety Manual for RMG Buildings. On 20/02/2024: The T&C VI of Fire Alarm & Detection System has been conducted on dated 20/02/2024. The system is required Final verification inspection. On 26/06/2024: Corrected. FADS FVI was conducted & it was found that the system was functional & approved. Inspection, Test & maintainenance records were available on-site in accordance with the standard. See details in the FVI report. On 04-Nov-25: Corrected. | Within 3months | Corrected
Initial Inspection |  | 22 | Inspection, testing, and maintenance of the extinguisher system is not in accordance with NFPA 10 or as per Accord standard. | Inspect, test and maintain the extinguisher system, and keep written records on-site, in accordance with NFPA 10 or as per Accord standard. | Now we are checking routinely and have recorded also. | Jun 21 2021 | On 16-May-2023: Corrected. On 04-Nov-25: Corrected. | Within 3months | Corrected

## Electrical
Date
08-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A M Fashion, Mazu Khan Bazar,Harbaid, Gazipur-1710, Gazipur, Dhaka
Date of Inspection |  | 2021-02-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. |  | May 30 2021 | On 16/05/2023: Not Corrected. The factory has prepared an as-built SLD. Factory need to submit the SLD to RSC for review. On 24/03/2024: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once a LPS is designed properly, installation must be done accordingly. |  | Jun 30 2021 | On 16/05/2023: Not Corrected. The factory has designed & installed LPS for the main production building. LPS design & installation yet to be done for the godown shed. On 24/03/2024: Corrected. The factory installed LPS at godown shed as per design. | Within 3 months | Corrected
Initial Inspection |  | 3 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 4 | Thermography scanning report is unavailable. | Thermography survey must be done and recorded at least twice in a year. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 5 | Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 6 | No working separation between LT (Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT switchgear). | A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07m) and ventilation must be ensured. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 7 | Inadequate space around Generator for performing maintenance work. | Minimum working space (1.07m) around the generator (and related electrical installations) must be maintained. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 8 | Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped, and rust must be checked and cleaned. |  | Nov 29 2020 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 9 | Generator output cables (laid on floor) are not protected and supported. | Service cables from generator must be supported at its own breaker's terminal and with cable tray. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 10 | Inadequate sized earth cable connected to generator frame. | Two separate earth connection & one separate and distinct neutral connection must be provided over generator. The earth cable size shall be determined according to BNBC or Adiabatic method (if possible). Number of earth pits shall be determined by the size. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 11 | Transformer Body earthing (equipment earthing) cable size is inadequate. | Equipment earthing cable size must be increased. The earth cable size shall be determined according to BNBC or Adiabatic method (if possible). Number of earth pits shall be determined by the size of connected earth cable. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 12 | Transformer Breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil mark on the cup. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 13 | Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 14 | Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 15 | Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 16 | Electrical power cables are not identified properly. | Proper identification shall be done on power cables circuit breakers used in the system according to SLD. |  | May 30 2021 | On 16/05/2023: Not Corrected. Cable identification doesn't match with the as-built SLD. On 24/03/2024: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 17 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 18 | Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 19 | Panel/distribution board is not firmly fixed with the foundation. | Panel base must be securely fixed to the foundation with appropriate fastening devices. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 20 | No permanent identification found at the panel boards & instruction for CPR (Cardiopulmonary Resuscitation)/Electrical shock restoration is absent. | (1) All distribution boards shall be marked permanently, as the case may be, provided a unique ID number (e.g. MDB-1). (2) Hang this instruction (CPR) near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 21 | Combustible materials are attached with cable channel. | Remove all combustible materials. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 22 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 23 | Cables inside distribution board is disorganized (Typical issue). | Organize all the power cables securely and neatly inside distribution board to prevent from electrical hazards. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Initial Inspection |  | 24 | Distribution Board has unwanted opening. | Seal each distribution board's top/bottom/ back; and use cable glands holding/supporting cables. Also seal the unwanted gland holes & other openings. |  | Apr 30 2021 | On 16/05/2023: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 25 | Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. |  | May 30 2021 | On 16/05/2023: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 26 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be accurately reflected in the record. Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years and documented. This testing may require power shutdown to ensure accurate results and safety. | In Progress: Already we communicate with our electrical third party & the pawer supplier REB to do this insulation resistance test with the x-former to LT panel cable also. For your information there is no HT - VCB in our factory, for this reason we should have to keep shutdown from the pole of REB. There is continuous pressure of production & shipment, at this situation we are waiting for a vacation to keep shutdown the power to do the test. We are trying to do this earlier as possible. | Dec 16 2025 | RPO Comments: On 27-Jan-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 27 | New Finding: Hot spots have been observed at some points. | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | Completed: We have taken necessary safety precautions by replacing oversized circuit breakers and eliminating identified hot spots.” | Dec 16 2025 | RPO Comments On 27-Jan-2026: The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 28 | New Finding: Protective device is not installed/adjusted per load demand. | Protective devices must be installed or adjusted according to the connected load current. If adjustment is not feasible, replacement is necessary. Each motor load exceeding 376W requires separate protection, adhering to nameplate data for selecting the appropriate protective device. | In Progress: Some oversized breakers have been replaced, and the balance modifications are ongoing as per the plan. Cutting machine fuses have been changed and installed as per SLD requirements. | Jan 16 2026 | RPO Comments: On 27-Jan-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress

## Boiler
Date
08-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A M Fashion, Mazu Khan Bazar,Harbaid, Gazipur-1710, Gazipur, Dhaka
Date of Inspection |  | 2022-10-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | Non BBR-24040-1 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed emergency stop push switches at the required locations to ensure immediate shutdown during emergencies.” | Mar 18 2026 | Comments on 05-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | Non BBR-24040-1 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | “We have already completed the low-low water level marking as a corrective action.” | Mar 18 2026 | Comments on 05-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | Non BBR-24040-1 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Our manufacture Modern Erection Ltd., has been informed and is preparing the necessary design and operational documents. Please consider will be submitted once received." | Mar 18 2026 | Comments on 05-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | Non BBR-24040-1 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We have already completed proper insulation work on the steam header and steam pipeline to prevent heat loss and ensure safety compliance. | Feb 18 2026 | Comments on 05-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 5 | Non BBR-24040-1 | Inconsistency was observed between the nameplate data and the CIoB provided certificate copy for the boiler regarding the boiler manufacturing year. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | We have informed the boiler manufacturer, Modern Erection Ltd., regarding the inconsistency between the nameplate data and the CIoB certificate. They have started corrective actions to resolve the issue, and updated documents will be submitted shortly. | Mar 18 2026 | Comments on 05-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 6 | Non BBR-24040-1 | Salt and 1 mm thin scale formation was observed on the waterside on the top on the end plate. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Proper blowdown has been carried out regularly in accordance with the SOP. Water treatment parameters are being monitored to prevent salt and scale formation | Feb 18 2026 | Comments on 05-Mar-2026: As per the pictorial evidence, the issue is not remediated yet. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 7 | Non BBR-24040-1 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | The required interlock switch for the Low Low Water (LLWL) level trip has been installed. The LLW level tripping mechanism has been tested and verified as fully functional. | Jan 25 2026 | Comments on 05-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification