## Structural
Date
30-Oct-2025 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB APPARELS LTD (extension), 225, SINGAIR ROAD, HEMAYETPUR, SAVAR, Dhaka
Date of Inspection |  | 2021-09-12
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Prepared load plan to be revised Building-1 (Wash Building) | Produce and actively manage a set of floor live load plan following BNBC minimum live load requirement and considering foundation & column capacity of the building. | Corrected | Oct 14 2021 | On 29-Feb-2024: The load plan has been produced as a part of EA. Factory has submitted the EA to RSC which is currently under review. During the inspection, floor loading was found within 100 psf. The factory is required to post and maintain accepted load plan. On 12-Mar-2025: Load plan has been produced and accepted as part of EA considering 7 storied building (G+6) on 6 March 2024 from RSC. During inspection accepted load plan was found posted on each floor and live load was found below the allowable limit (5 kPa for typical floor and 6 kPa for storage area). | within 6-weeks | Corrected
Initial Inspection |  | 2 | Prepared load plan to be revised Building-1 (Wash Building) | Implement floor load plan. | Corrected | Jul 10 2021 | On 29-Feb-2024: The load plan has been produced as a part of EA. Factory has submitted the EA to RSC which is currently under review. During the inspection, floor loading was found within 100 psf. The factory is required to post and maintain accepted load plan. On 12-Mar-2025: During inspection accepted load plan was found posted on each floor and live load was found below the allowable limit (5 kPa for typical floor and 6 kPa for storage area). | within 6-months | Corrected
Initial Inspection |  | 3 | Inconsistency in the as-built drawing Building-1 (Wash Building) | The factory engineer is required to survey the structure and update the as-built structural drawing. | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Nov 14 2021 | On 29-Feb-2024: The as-built drawing has been produced as a part of EA. Factory has submitted the EA to RSC which is currently under review. On 12-Mar-2025: As-built drawing has been produced and accepted as part of EA considering 7 storied building (G+6) on 6 March 2024 from RSC. The building is currently 3 storied. During inspection as-built drawing was found satisfactory with on site condition. | within 6-weeks | Corrected
Initial Inspection |  | 4 | Falling hazard Building-1 (Wash Building) | Factory is required to provide parapet/railing at all locations of roof and staircase to avoid possible falling hazard | Done | Oct 14 2021 | On 29-Feb-2024: Railing has been provided at the periphery of roof. During inspection, no falling hazard was observed. On 12-Mar-2025: Corrected previously. Factory has provided railing and parapet wall. | within 6-weeks | Corrected
Initial Inspection |  | 5 | Design Report needs to be prepared Building-2 (Chemical & Boiler Building) | Factory engineer is required to prepare a Design Report in compliance with section 1.9.1.1 (part-6, BNBC). | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Nov 14 2021 | On 29-Feb-2024: Factory has submitted the EA to RSC which is currently under review. On 12-Mar-2025: This issue has been covered in EA which has been accepted on 6 March 2024 from RSC. | within 6-weeks | Corrected
Initial Inspection |  | 6 | Design Report needs to be prepared Building-2 (Chemical & Boiler Building) | Implement any remediation work if required. | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Dec 14 2021 | On 29-Feb-2024: Factory has submitted the EA to RSC which is currently under review. Factory is required to complete the remediation within the given timeline by RSC (if required). On 12-Mar-2025: As per accepted EA, no remediation work is required. | within 6-months | Corrected
Initial Inspection |  | 7 | Column appears to be slender Building-2 (Chemical & Boiler Building) | Factory engineer is required to carryout adequacy check of the highlighted column considering slenderness effect | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Nov 14 2021 | On 29-Feb-2024: Factory has submitted the EA documents to RSC which is currently under review. On 12-Mar-2025: This issue has been covered in EA which has been accepted on 6 March 2024 from RSC. | within 6-weeks | Corrected
Initial Inspection |  | 8 | Column appears to be slender Building-2 (Chemical & Boiler Building) | Implement any remediation work if required. | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Nov 14 2021 | On 29-Feb-2024: Factory has submitted the EA documents to RSC which is currently under review. Factory is required to complete the remediation within the given timeline by RSC (if required). On 12-Mar-2025: As per accepted EA, no remediation work is required. | within 6-months | Corrected
Initial Inspection |  | 9 | Falling hazard Building-2 (Chemical & Boiler Building) | Factory is required to provide parapet/railing at all locations of roof and staircase to avoid possible falling hazard. | Done | Jun 10 2021 | On 29-Feb-2024: Railing has been provided at the periphery of roof. During inspection, no falling hazard was observed. On 12-Mar-2025: Corrected previously. Factory has provided railing and parapet wall. | within 6-weeks | Corrected
Initial Inspection |  | 10 | Design Report needs to be prepared Building-3 (Compressor & Substation Building) | Factory engineer is required to prepare a Design Report in compliance with section 1.9.1.1 (part-6, BNBC). | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Nov 14 2021 | On 29-Feb-2024: Factory has submitted the EA documents to RSC which is currently under review. On 12-Mar-2025: This issue has been covered in EA which has been accepted on 6 March 2024 from RSC. | within 6-weeks | Corrected
Initial Inspection |  | 11 | Design Report needs to be prepared Building-3 (Compressor & Substation Building) | Implement any remediation work if required. | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Dec 14 2021 | On 29-Feb-2024: Factory has submitted the EA documents to RSC which is currently under review. Factory is required to complete the remediation within the given timeline by RSC (if required). On 12-Mar-2025: As per accepted EA, no remediation work is required. | within 6-months | Corrected
Initial Inspection |  | 12 | Discrepancy in as-built drawing Building-3 (Compressor & Substation Building) | The factory engineer is required to survey the structure and update the as-built structural drawing. | Corrected. Note-EA approved by RSC by mail dated on 10.03.2024. | Nov 14 2021 | On 29-Feb-2024: The as-built drawing has been produced as a part of EA. Factory has submitted the EA to RSC which is currently under review. On 12-Mar-2025: As-built drawing has been produced and accepted as part of EA on 6 March 2024 from RSC. During inspection as-built drawing was found satisfactory with on site condition. During inspection two new structures were found (Pump room-RC basement structure-area-132 sft, Desanding Area-single storied RC open structure-area-924 sft). As-built drawing was available on site and fond satisfactory. | within 6-weeks | Corrected
Follow Up Inspection |  | 13 | New finding-1: Corrosion on the exposed rebar (Building-1). | Provide rust proof paint on exposed rebar. | Corrected. | Apr 24 2025 | RPO Comments: On 27/10/2025 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 12-Mar-2025: During inspection, corrosion was found on the exposed rebar (Building-1). Provide rust proof paint on exposed rebar. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 14 | New finding-2: Non-structural storage racks found not anchored/braced. (Building-2). | Anchor/brace non-structural storage racks. | Corrected. | Sep 12 2025 | RPO Comments: On 27/10/2025 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 12-Mar-2025: During inspection, non-structural storage racks found not anchored/braced. (Building-2). Anchor/brace non-structural storage racks. | (within 6 months) | Pending Verification

## Fire
Date
30-Oct-2025 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB APPARELS LTD (extension), 225, SINGAIR ROAD, HEMAYETPUR, SAVAR, Savar
Date of Inspection |  | 2021-09-12
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Exit Enclosures are not properly fire separated from other occupancy on each floor by fire rated construction due to non-functionality of installed fire rated doors. Location: Building 1 | Provide minimum 2-hr fire rated separation in exit enclosures with minimum 1.5-hr fire rated doors and seal all unprotected openings and penetration to separate the exit stairs from work areas and other building spaces on all floor levels with similar rating of fire door. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Corrected | Oct 7 2021 | On 03/07/2022: Corrected. Fire doors with necessary accessories were found functional during inspection. Doors were found interfaced with FACP. On 26-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Unsealed electrical busbar penetration was found in fire rated floor/ceiling assemblies. Location: Building-1 | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level or Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation by at least 3-hr (Considering proposed?7 storied). | Corrected | Oct 9 2021 | On 03/07/2022: Corrected. Penetration has been sealed with fire rated materials (Abesco FP200, Fire rated expanding foam). On 26-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Wastage chemical storage was found near the exit discharge path. Location: Stair-2, Ground Floor, Building-1. | Remove the wastage chemical storage from the exit discharge path or separate the storage area from the exit discharge path with minimum 4-hr fire rated construction. | Corrected | Oct 9 2021 | On 03/07/2022: Corrected. Not found. On 26-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Areas used for combustible storage are not separated by fire-rated construction . Location: 2nd Floor of Building-1 | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m | Corrected | Oct 9 2021 | On 03/07/2022: Corrected. In process storage was found within limit during inspection. On 26-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | The elevator discharges inside the stair enclosure. Location: Stair-1 of Building -1 | For new construction, elevators shall not open into an exit enclosure as per ACCORD Standard?6.14.3. So, ensure separate enclosures for the elevator shafts with minimum 2 hr. fire rating. If elevator is not being installed then the door opening can be sealed by minimum 2-hr fire rated construction. | Corrected | Oct 11 2021 | On 03/07/2022: Corrected. Elevator shaft has been sealed. On 26-Nov-24: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Handrails are not provided at exit stair. Location: stair-3 of Building-1 | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in | Corrected | Oct 8 2021 | On 03/07/2022: Corrected. Provided. On 26-Nov-24: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 7 | Storage was located in exit stair. Location: Ground floor of Stair-1 of Building-1 | Remove storage from the exit stairs and egress path | Corrected | Oct 4 2021 | On 03/07/2022: Corrected. Not found. On 26-Nov-24: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | The stair tops at the roof is open, because of this rain water may enter the stairs and cause slipping hazard. | Cover the stair tops with appropriate construction so that rain water can not enter the stairs. | Corrected | Oct 9 2021 | On 03/07/2022: Corrected. Stair tops have been covered. On 26-Nov-24: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 9 | Evacuation map was not found. Location: 2nd Floor of Building-1 | Provide evacuation map at the entrance of exit stairs. | Corrected | Oct 5 2021 | On 03/07/2022: Corrected. Provided. On 26-Nov-24: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on?site | Corrected | Oct 5 2021 | On 03/07/2022: Corrected. On 26-Nov-24: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 11 | The factory has installed an addressable fire alarm & detection system which is required to be reviewed and verified. | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review and approval. Modification (if required) shall have to be done as per the reviewed design and NFPA-72. Upon review & modification (if required) the owner shall verify the system by RSC for final acceptance | Corrected. T&C related work was completed. We are waiting for final T &C by RSC. | Oct 13 2021 | On 03/07/2022: Drawing has been reviewed by RSC. Reportedly, installation work has been completed. FACP was found functional during inspection. On 15-Feb-2024: T&CVI has conducted & found that FADS is not corrected. See the details T&CVI report. On 28-Oct-2024: T&CVI has conducted & found that FADS is corrected. See the details T&CVI report. On 26-Nov-24: Corrected. FACP was found active & normal condition during inspection. | Design within 2 months, Install within 4 months. | Corrected
Initial Inspection |  | 12 | Inspection, testing, and maintenance for the fire detection system is not in accordance with NFPA 72 | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Oct 5 2021 | On 03/07/2022: It is an integrated part of Fire Alarm & Detection System. On 15-Feb-2024: T&CVI has conducted & found that FADS is not corrected. See the details T&CVI report. On 28-Oct-2024: T&CVI has conducted & found that FADS is corrected. See the details T&CVI report. On 26-Nov-24: Corrected. | Within 3 months | Corrected

## Electrical
Date
30-Oct-2025 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB APPARELS LTD (extension), 225, SINGAIR ROAD, HEMAYETPUR, SAVAR, Savar
Date of Inspection |  | 2021-09-12
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | Corrected | Oct 6 2021 | Comments from RCH: 22/05/2022: SLD is under review by the RSC now. On 03/07/2022: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 2 | Air terminals aren't installed at proper height. | The tip of an air terminal shall be not less than 10 in. (254 mm) above the object or area, it is to protect. | Corrected | Oct 6 2021 | RPO Comments: On 05/12/2023 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/07/2022: Not corrected. Some progress has been observed. Metal bonding is not done properly. On 14/01/2024: Corrected | 1 MONTHS | Corrected
Initial Inspection |  | 3 | Earth Pit resistance record is not available for all earth pits. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made, and the result shall be available to the Inspector when required. | Corrected | Oct 10 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 4 | Safety program is initiated but not adequate. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded according to NFPA 70E. After the training, there should be exam to evaluate the influence of the training program. | Corrected | Oct 12 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 5 | Circuit breaker is not firmly fixed to the base. | Circuit shall be fixed with its base firmly for secure operation. | Corrected | Oct 10 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 6 | Cables are hanging without (proper) support and protection. | Cable tray/ladder must be used to support cables at any where to keep cable out of tension. | Corrected | Oct 12 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 7 | Earth lead cable/Earth Continuity Conductor size is absent. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | Corrected | Oct 8 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 8 | Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Corrected | Oct 7 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 9 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected | Oct 11 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 10 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Corrected | Oct 13 2021 | RPO Comments: On 05/12/2023 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 03/07/2022: Not corrected. No progress has been observed. On 14/01/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 11 | Electrical power cables are not identified properly. (Not matched with SLD). | Proper identification shall be done on power cables, circuit breakers used in the system according to SLD. | Corrected | Oct 10 2021 | On 03/07/2022: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 12 | Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Corrected | Oct 13 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 13 | Transformer Body earthing (equipment earthing) cable size is inadequate. | Equipment earthing cable size must be increased. The earth cable size shall be determined according to BNBC or Adiabatic method (if possible). Number of earth pits shall be determined by the size of connected earth cable. | Corrected | Oct 10 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 14 | Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Corrected | Oct 7 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 15 | Distribution board/panel are filled with fluffs (lint/dust). | Keep always clean inside all the distribution boards/panels. Seal them properly and ensure adequate ventilation. | Corrected | Oct 6 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 16 | MCCB is installed without any enclosure. | Each MCCB/MCB must be enclosed by proper type material. the material must not be more than 18 SWG graded. | Corrected | Oct 13 2021 | On 03/07/2022: Corrected. | 1 MONTHS | Corrected
Follow Up Inspection |  | 17 | New Finding: Outdoor Cable are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Corrected | Sep 12 2022 | RPO Comments: On 05/12/2023 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 14/01/2024: Corrected. | 2 MONTHS | Corrected