## Structural
Date
02-Feb-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A Yarn Dyeing Ltd. (Extension buildings)., Kaichabari, West Side of DEPZ, Ashulia, Savar, Dhaka, Dhaka
Date of Inspection |  | 2021-08-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Vertical bracing missing. (Building 3) | Building engineer is required to check the lateral stability of the existing bracing system. | Corrected | Nov 14 2021 | On 09-Jan-2022: This issue is covered under the EA which is currently under review. Factory has submitted EA documents on 9-Jan-2022 to RSC for review. On 16-Aug-2022: This issue had been covered in EA report. Factory management got EA acceptance from RSC on 21-April-2022. On the other hand, a single storied childcare building was found east side of building-3, which as built drawing matched with the existing condition of childcare building. On 03-Nov-2024: Corrected Previously. | 6 weeks | Corrected
Initial Inspection |  | 2 | Vertical bracing missing. (Building 3) | Install missing bracing as per design. | Corrected | Nov 14 2021 | On 09-Jan-2022: Factory has installed the missing bracings as per design drawing. On 16-Aug-2022: Corrected from previous follow up inspection. During inspection, missing bracings were found installed as per accepted design drawing. On 03-Nov-2024: Corrected Previously. | 6 weeks | Corrected
Initial Inspection |  | 3 | Floor Load Plan need to be revised. (Building 3) | Building engineer is required to revise the prepared live load plan and review the design. | Corrected | Nov 14 2021 | On 09-Jan-2022: This issue is covered under the EA which is currently under review. Factory has submitted EA documents on 9-Jan-2022 to RSC for review. During inspection no overloading was observed and loading was found below 3 Kpa. After EA acceptance factory will continue to implement final load plan. On 16-Aug-2022: This issue had been covered in EA report. Load plans were prepared as a part of EA. Factory management got EA acceptance from RSC on 21-April-2022.As per acceptance of EA, no retrofitting work is required. On 03-Nov-2024: Corrected Previously. | 6 weeks | Corrected
Initial Inspection |  | 4 | Floor Load Plan need to be revised. (Building 3) | Implement floor load plan. | Corrected | Apr 4 2022 | On 09-Jan-2022: This issue is covered under the EA which is currently under review. Factory has submitted EA documents on 9-Jan-2022 to RSC for review. During inspection no overloading was observed and loading was found below 3 Kpa. After EA acceptance factory will continue to implement final load plan. On 16-Aug-2022: As per acceptance of EA, no retrofitting work is required in building-3. During inspection load plan was found posted to each floor and overall loading was found within the allowable accepted loading limit (126 psf). On 03-Nov-2024: Corrected Previously. Loading was found within the acceptable load limit of 6 kPa. | 6-months | Corrected
Initial Inspection |  | 5 | Possible vehicle impact loading on column. (Building 3) | Provide vehicle impact protection to the susceptible column. | Corrected | Nov 14 2021 | On 09-Jan-2022: Factory has installed MS angle on corners of columns in parking area to resist vehicle impact loading. On 16-Aug-2022: Corrected from previous follow up inspection. Factory management had provided vehicle impact protection to the susceptible column. On 03-Nov-2024: Corrected Previously. | 6 weeks | Corrected
Initial Inspection |  | 6 | Improve roof drainage system.(Building 4) | Building engineer is required to improve roof drainage system to prevent stagnant water. | Corrected | Nov 14 2021 | On 09-Jan-2022: Factory has provided water proofing on roof and drainage system has also been improved. On 16-Aug-2022: Corrected from previous follow up inspection. Factory management had provided water proofing layer on roof top and drainage system had also been improved. On 03-Nov-2024: Corrected Previously. | 6 weeks | Corrected
Follow Up Inspection |  | 7 | New Finding 01: Newly Constructed (Not Covered in the Initial Inspection Report) RMS- G- 210 sqft Approx. WASTAGE-G-1200 sqft Approx. CHEMICAL-G-80 sqft Approx. Observations: 1. Lack of As-Built Drawings 2. Inadequate Member size and conncection adequacy. | Building engineer is required to prepare as-built drawings and carry out safety checks for the steel members, connections. The safety check report is required to be prepared according to the Accord Building Standards. | Documents under RSC review | Jan 15 2025 | On 03-Nov-2024: During the inspection, Newly Constructed (Not Covered in the Initial Inspection Report) single-storied sheds were observed. 1. RMS-(G)- 210 sqft Approx. 2. WASTAGE-G-1200 sqft Approx. 3. CHEMICAL-(G)- 80 sqft Approx. Lack of as-built drawings and inadequate member size, inadequate connections were observed. Building engineer is required to prepare as-built drawings and carry out safety checks for the steel members, connections. The safety check report is required to be prepared according to the Accord Building Standards. RPO Comments on 22 Jan 2026- the design documents submitted on 15 Jan 2026 which are under RSC review. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 8 | New Finding 01: Newly Constructed (Not Covered in the Initial Inspection Report) RMS- G- 210 sqft Approx. WASTAGE-G-1200 sqft Approx. CHEMICAL-G-80 sqft Approx. Observations: 1. Lack of As-Built Drawings 2. Inadequate Member size and conncection adequacy. | Carry out remedial works where required. | After review we will start remedial work | May 31 2025 | On 03-Nov-2024: Carry out remedial works where required after the acceptance of the safety check report from the RSC. RPO Comments on 22 Jan 2026- the design documents submitted on 15 Jan 2026 which are under RSC review. | (within 6 months) | In Progress

## Fire
Date
02-Feb-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A Yarn Dyeing Ltd. (Extension buildings)., Kaichabari, West Side of DEPZ, Ashulia, Savar, Savar, Dhaka
Date of Inspection |  | 2021-08-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stairs are not separated from work areas, other spaces on 1st floor by fire-rated construction. Location: Warehouse (Building No-3) Installed fire doors throughout the factory were not swinging and closing properly due to inappropriate installation of door accessories (closer,coordinaator, holding devices etc.). | Stair shall be enclosed with a minimum 1-hr fire-rated construction. Seal all unprotected openings and provide minimum 1-hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. The clearance under the bottom of a fire door shall be a maximum of 3⁄4 in. (19 mm). Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. Provide vestibules to separate any storage areas. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | Corrected | Jan 3 2022 | The work should have been completed as per RSC action plan. On 15/03/2023: During follow up inspection installed fire doors were functional properly in building-2. Penetrations were not sealed properly in building-3 exit stair enclsoure on ground and first floors. On 19-Nov-2023: Corrected. The exit stair has separated as per standared. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Dining area is not separated from other occupancies (storage) with fire rated assemblies. Location: Ground Floor at New Production Buidling-Unit-2 (Building No- 2) | Re-locate the dining area or separate the dining area from other occupancies with 3-hr fire rated construction. Provide required exits that lead directly to the street or exit stairwell or leading to a 3-hr fire rated corridor or open space. | Corrected | Jan 3 2022 | On 15/03/2023: Corrected. The factory has separated dining area from storage room and parking area. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Penetrations through floor/ceiling assemblies are found unsealed. Location(s): Plumbing pipes and Electrical Riser of New Production Buidling-Unit-2 (Building No-2) | Penetrations of fire resistive rated assemblies shall be protected with a listed through penetration fire stop system tested in accordance with ASTME814 in accordance with Accord standard 4.7. | Corrected | Jan 3 2022 | On 15/03/2023: Partially corrected. Penetrations were not sealed properly in several location on several floors. Floor and wall penetrations shall be sealed properly as per standard and sealant manufacturer guidleines to achieve required rating. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 3 months | Corrected
Initial Inspection |  | 4 | The Warehouse (Building No-3) is pre fabricated steel construction. The main structural element of the buildings are constructed by steel which is appears to be nonrated and were found in exposed condition. | The building shall be type-I or type-2 construction as per BNBC 2006 Part 3 Section 3.2.4, page 10356. Provide/ensure required fire rating on the structural elements by following Section 4.4 and Table 4.4.1 of the Accord Standard or Table 3.3.1 and Table 4.1.1 from BNBC. Consult a qualified fire protection engineer to achieve the required fire rating. | WorkS has been completed | Mar 3 2022 | On 15/03/2023: According to the factory personnel, the factory has submitted passive protection design and documents to the RSC for review. On 19-Nov-2023: The PFP design has approved on 09-Nov-2023 and factory management reported that the PFP material has already been in house. On 13-Feb-2024: PFP design for warehouse building has been reviewed from RSC. Reportedly, installation work has been started. RPO Comments: On 27 Mar 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 30-May-2024: PFP of steel sturctural elements of Building-3 were not completed. Please see details on PFP verification report. RPO Comments: On 27 Oct 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 03-Nov-24: The building has been previosuly assesed and the structural fire protection installation has been verified based on the BNBC 2006 requirements. During the inspection the factory management informed that they want to assess the structural fire protection requirements of the building (unprotected non-combustible construction type) according to BNBC 2020 provision refering to the “Ministry of Housing and Public Works” resolution. Subsequently, relevant data was collected regarding building height, front space, and proximity distances as per the BNBC 2020 requirements. The building height was found to be 11.32 meters and front space was found to be 15.16 meters . Ministry of Housing and Public Works resolution is applicable for unprotected non-combustible construction type building of upto 11 meters height. As a result this building is out of scope of the resolution. Later the factory decided to increase the height of the grade level/road level and submitted pictorial evidence on 17-Nov-2024. However, from the pictorial evidence it was observed that the building's surrounding grade level/road level is not uniform and on the same level. Only some portion of the grade level's height has been increased whereas the other portions are at a lower level. The factory is required to increase the height of the surrounding grade level of the building uniformly and not only some portions so that the entire grade/road is on the same level. On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : During inspection it was observed that the factory has increased the sorrounding road levels of Building-3. The building height for 2-storied Building-3 (Warehouse Building) has been measured from various points. The road level of NE corner was the reference of measurement. The building has a pitched roof and the corresponding heights were found as: NE-36'-11'', East-middle-32'- 4'', NW-37'-1.5'', West middle-33'- 6'' and SW-37'-1.5''. Slope angle of the pitched roof was found 08 degree. The structural fire protection requirement of the Building-3 has been assessed as per BNBC 2020 based on the recent resolution of the “Ministry of Housing and Public Works”. Accordingly, the average height considering above measurements was found 35'-2'' ( 10.71 meter) which is below 11 meters. Also, the front space of the building was found to be 15.16 meters therefore the building type has been determined as Group I, Type- 1E. The fire rating requirement of the building has been considered as per the requirements of Table 3.3.1 (a) of BNBC 2020 for TYpe-1E construction. | Within 6 months | Corrected
Initial Inspection |  | 5 | Areas used for combustible storage are not separated by fire rated construction. Location: New Production Buidling-Unit-2 (Building No-2) | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or, Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Jan 3 2022 | On 15/03/2023: Corrected. During follow up inspection work in progress (WIP) storage areas were found according to the standard. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Refer to CAP item-20. | Within 3 months | Corrected
Initial Inspection |  | 6 | Width of aisles is less than 0.9m (36-in.). Location: Warehouse (Building No-3) | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). | Corrected | Nov 3 2021 | On 15/03/2023: Corrected. Provided. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 7 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: 6th floor of New Production Buidling-Unit-2 (Building No-2), both building storage rooms/areas and where applicable. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Nov 3 2021 | On 15/03/2023: Corrected. During follow up inspection illumination level on ailses and exit stair enclosure were found satisfactory. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 8 | Directional signs are not provided where direction of the path of travel to an exit has changed. Location: 6th floor of New Production Buidling-Unit-2 (Building No-2) | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | Corrected | Nov 3 2021 | On 15/03/2023: Corrected. Provided directional exit sign. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 9 | Exit sign not provided at exit. Location: 6th floor of New Production Buidling-Unit-2 (Building No-2) | Lighted exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated. | Corrected | Nov 3 2021 | On 15/03/2023: Corrected On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 10 | Building did not have occupant load signs at required locations. Location: New Production Buidling-Unit-2 (Building No-2) 6th floor and where missed. | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space. | Corrected | Nov 3 2021 | On 15/03/2023: Corrected. Posted. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 11 | Fire evacuation maps is posted inside the stair enclosure. Location: New Production Buidling-Unit-2 (Building No-2) | Fire evacuation maps shall be posted at the entrance to each exit stair. | Corrected | Nov 3 2021 | On 15/03/2023: Corrected. Posted. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 12 | The factory has installed an addressable fire alarm & detection system which is required to be reviewed and verified. Location: For all structures | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review and approval. Modification (if required) shall have to done as per the reviewed design and NFPA- 72. Upon approval & modification (if required) the factory shall inform RSC to conduct final testing and commissioning verification of the system for final acceptance. | Corrected | Nov 3 2021 | On 15/03/2023: Pre T&CVI has been conducted along with follow-up inspection and found system requires Desktop Document Verification prior Full T&CVI. On 19-Nov-2023: T&CVI has been conducted along with follow-up inspection and found that the system was not approved. See the T&CVI report. RPO Comments: On 19 Dec 2023, the factory is determined as ready for T&CVI for FADS on 30 Nov 2023 On 13-Feb-2024: T&CVI has been conducted along with follow-up inspection and found that the system is requires on-site Final Verification. See detailed T&CVI report. RPO Comments: On 27 Mar 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/05/2024: It is approved by FVI. See detailed FVI report. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Design within 1 months, installation/modificati on within 3 months | Corrected
Initial Inspection |  | 13 | The factory has installed a fire pump system which is required to be reviewed and verified. | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review and approval. Modification (if required) shall have to done as per the reviewed design and NFPA- 20. Upon approval & modification (if required) the factory shall inform RSC to conduct final testing and commissioning verification of the system for final acceptance. | Corrected | Nov 3 2021 | On 15/03/2023: Pre T&CVI has been conducted along with follow-up inspection and found system requires Desktop Document Verification prior Full T&CVI. On 19-Nov-2023: T&CVI has been conducted along with follow-up inspection and found that the system was not approved. See the T&CVI report. RPO Comments: On 19 Dec 2023, the factory is determined as ready for T&CVI for SUPS on 30 Nov 2023 On 13-Feb-2024: T&CVI has been conducted along with follow-up inspection and found that the system is approved. See detailed T&CVI report. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Design within 1 months, installation/modificati on within 3 months | Corrected
Initial Inspection |  | 14 | The height of the highest occupied floor is more than 33 ft and the factory has installed a class III standpipe system which is required to be reviewed and verified. Location: New Production Buidling-Unit-2 (Building No-2) | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review and approval. Modification (if required) shall have to done as per the reviewed design and NFPA- 14. Upon approval & modification (if required) the factory shall inform RSC to conduct final testing and commissioning verification of the system for final acceptance. | Corrected | Nov 3 2021 | On 15/03/2023: Pre T&CVI has been conducted along with follow-up inspection and found system requires Desktop Document Verification prior Full T&CVI. On 19-Nov-2023: T&CVI has been conducted along with follow-up inspection and found that the system was not approved. See the T&CVI report. RPO Comments: On 19 Dec 2023, the factory is determined as ready for T&CVI for SUPS on 30 Nov 2023. On 13-Feb-2024: T&CVI has been conducted along with follow-up inspection and found that the system is approved. See detailed T&CVI report. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Design within 1 months, installation/modificati on within 3 months | Corrected
Initial Inspection |  | 15 | A sprinkler system has been installed in the building which is required to be reviewed and verified. Location: New Production Buidling- Unit-2 (Building No-2). Note: Based on the height of the highest occupied floor, sprinkler system is not mandatory however the factory has installed automatic sprinkler system in place of automatic fire detection system in accordance with Accord standard 5.7.3.1 for both fire detection and fire protection. | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review and approval. Modification (if required) shall have to done as per the reviewed design and NFPA- 13. Upon approval & modification (if required) the factory shall inform RSC to conduct final testing and commissioning verification of the system for final acceptance. | Corrected | Nov 3 2021 | On 15/03/2023: Pre T&CVI has been conducted along with follow-up inspection and found system requires Desktop Document Verification prior Full T&CVI. On 19-Nov-2023: T&CVI has been conducted along with follow-up inspection and found that the system was not approved. See the T&CVI report. RPO Comments: On 19 Dec 2023, the factory is determined as ready for T&CVI for SUPS on 30 Nov 2023. On 13-Feb-2024: T&CVI has been conducted along with follow-up inspection and found that the system is approved. See detailed T&CVI report. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Design within 1 months, installation/modificati on within 3 months | Corrected
Initial Inspection |  | 16 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Corrected | Nov 3 2021 | On 15/03/2023: Corrected. Maintaining. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 17 | Inspection, testing and maintenance of the automatic sprinkler system is not in accordance with NFPA 25. | Inspect, test and maintain the automatic sprinkler system and keep written records on- site, in accordance with NFPA 25 and ACCORD standards. | Corrected | Nov 3 2021 | It is an integrated part of Fire Protection System. On 15/03/2023: Corrected. Maintaining. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Initial Inspection |  | 18 | Inspection, testing and maintenance of the addressable fire alarm and detection system is not in accordance with NFPA 72. | Inspect, test and maintain the addressable fire alarm and detection system and keep written records on- site, in accordance with NFPA 72 and ACCORD standards. | Corrected | Nov 3 2021 | It is an integrated part of Fire Protection System. On 15/03/2023: Corrected. Maintaining. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected On 30-May-2024: Corrected. On 03-Nov-24: Corrected On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected
Follow Up Inspection |  | 19 | New Finding(4th FUI): Aisles were found obstructed by process work & storage. | Keep aisle, egress paths and stairs clear of process work & storage. | Corrected. Factory management has taken proactive measures regarding this issue. In this regards, we have removed all osbtructing materials from emergency exit routes, aisles/passageways to make blockage free and pave the way for easily movement of the workers. Further, we have ensured the minumum width of 0.9m between the aisles. | Jun 13 2024 | On 30-May-2024: New Finding RPO Comments: On 27 Oct 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 03-Nov-24: Corrected. During the inspection aisles were observed without any obstructions. On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Immediately | Corrected
Follow Up Inspection |  | 20 | New Finding(4th FUI): Areas used for combustible storage are not separated by fire rated construction. Location: 2nd Floor, Building No-2. | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or, Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected. Factory management has already taken initiatives regarding this issue. In regard of this, we have removed all goods from that floor & those goods move to dedicated warehouse. | Aug 25 2024 | On 30-May-2024: New Finding. RPO Comments: On 27 Oct 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 03-Nov-24: Corrected. During the inspection the process storage was found within limit. On 05-Dec-24 (Special Fire Specific Item Verification Inspection) : Not inspected. | Within 1 month | Corrected

## Electrical
Date
02-Feb-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A Yarn Dyeing Ltd. (Extension buildings)., Kaichabari, West Side of DEPZ, Ashulia, Savar, Savar, Dhaka
Date of Inspection |  | 2021-08-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Electrical Single Line Diagram (SLD) is available in the factory but not as-build. | As built Electrical SLD must be prepared; it must have factory's whole electrical installation information. | Corrected | Dec 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 2 Months | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) and drawing is available but it is not covered for the whole factory. | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is more than 40). Once a LPS is designed properly, installation must be done accordingly asap. | Corrected | Jan 3 2022 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 4 | Generator output cables (laid on floor) are not protected and supported. | Service cables from generator must be supported at its own breaker's terminal and with cable tray. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 6 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 7 | Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 8 | Earth Busbar/Earth Continuity Conductor size is inadequate/undersize. | Earth lead cable/ Earth Continuity Conductor/ECC busbar size (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 9 | Electrical Distribution board/panels are adjacent to water source. | Electrical distribution board/panels must not be installed within 2.5meter of any water source. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 10 | Electrical distribution box/panels are full of fluffs (lint/dirt) | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 11 | Cable duct/channels are filled with fluffs (Lint/dust) | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 12 | Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Distribution Board is installed outside open area without rain water protection. | Distribution board must be protected against rain water. In that case, water resist panel could be used for outside use or panel could be bring inside of the building/shed. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 14 | Uninsulated busbars used inside electrical distribution panel. | Electrical busbar need to be insulated with proper type of insulating materials. In this case it may be used by heat shrink insulating rubber boots. | Corrected | Nov 3 2021 | RSC accepts the time extension mentioned by the factory and expects the issue to be closed as per recommendation within the agreed timeline. On 15/03/2023: Corrected. | 1 Month | Corrected

## Boiler
Date
02-Feb-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A Yarn Dyeing Ltd. (Extension buildings)., Kaichabari, West Side of DEPZ, Ashulia, Savar, Dhaka, Dhaka
Date of Inspection |  | 2022-04-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 11935 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Emergency stop push switches installed on the boiler control panel and outside the boiler room | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 11935 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The Low Low Water Level (LLWL) marked beside the gauge glass on a separate arrangement | Mar 4 2026 | Comments on 01-Feb-2026: Markings should be properly done on a separate arrangement, with the levels clearly marked and written for clear understanding. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 3 | BB 11935 | Necessary technical documents (water treatment report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | All technical documents available | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work status could not be assessed, as no image was provided. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 11935 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Fuel line openings in boiler room diverted outside of the boiler room and also some point sealed off with a bond plug/blind flange to prevent fuel leakage. | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 11935 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Unused steam line terminated | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 11935 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | New pressure gauge installed | Feb 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 14163 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | Valve have been removed from water level limiter | Jan 11 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 14163 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | valve have been removed from steam pressure controller | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 14163 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The Low Low Water Level (LLWL) marked beside the gauge glass on a separate arrangement | Mar 4 2026 | Comments on 01-Feb-2026: Markings should be properly done on a separate arrangement, with the levels clearly marked and written for clear understanding. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 14163 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Unused steam line terminated | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 11935 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve. | From manufacture there are no drain line for water level gauge glass. For water level check we may use blow down line | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 12 | BB 11935 | Salt and scale formation (1~2 mm) was observed on the waterside on inside water tube, top and bottom endplate of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | water side of the boiler water tube cleaned | Feb 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 13 | BB 14163 | Carbon deposition was found in the (smoke tubes). | The furnace and inside of the fire tubes should be cleaned periodically to prevent excessive soot build-up. The fuel burner should be adjusted according to the manufacturer's guidelines. | Smoke tubes habe been cleaned | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification