## Structural
Date
15-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD. (Extension), 14 No. Genda, Karnopara, Ulail, Savar, Dhaka, Dhaka
Date of Inspection |  | 2024-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The design report required to be revised. (Utility Building II) | The building engineer is required to verify in-situ concrete strength by taking cores from lower-tier columns. Otherwise, consider minimum concrete strength. | Core Cutting & Testing has been done and RSC has accepted the EA documents on 30th July 2025. (Done) | May 29 2024 | On 08-Dec-2024: Core are taken as part of EA. The factory has submitted the revised EA to RSC which is currently under review. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 weeks | Pending Verification
Initial Inspection |  | 2 | The design report required to be revised. (Utility Building II) | The building engineer is required to check & confirm the design strength in the design report and submit it to RSC. | RSC has accepted the EA documents on 30th July 2025. (Done) | May 29 2024 | On 08-Dec-2024: The factory has submitted the revised EA to RSC which is currently under review. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 weeks | Pending Verification
Initial Inspection |  | 3 | The design report required to be revised. (Utility Building II) | Implement the recommendations of the design report. | RSC has accepted the EA documents on 30th July 2025. (Done) | Sep 30 2024 | On 08-Dec-2024: After EA acceptance factory will carry out remedial work if required. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 months | Pending Verification
Initial Inspection |  | 4 | The design report required to be revised. (Utility Building II) | Implement floor load plan. | Update Load Plan has been posted on each entrance of all floor and RSC has accepted the EA documents on 30th July 2025. (Done) | Sep 30 2024 | On 08-Dec-2024: During inspection, floor loading was found within the 6kPa for typical floor. After the EA acceptance, the factory will post the final load pan and maintain accordingly. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 months | Pending Verification
Initial Inspection |  | 5 | Exposed rebar. (Utility Building II) | The building engineer is required to provide rust-proof paint on exposed rebars to protect from corrosion. | The factory has provided cement paint on exposed rebars to protect from corrosion. | Sep 30 2024 | On 08-Dec-2024: Exposed rebar has been cut off. During inspection, no exposed rebar was found. | within 6 months | Corrected
Initial Inspection |  | 6 | Lack of information in the provided drawing. (External Steel Stair, Utility Building II) | The building engineer is required to prepare as-built drawings mentioning all the connection details. | The factory has been updated as-built drawing, and RSC has accepted the EA documents on 30th July 2025. (Done) | May 29 2024 | On 08-Dec-2024: As-built drawings are prepared as part of EA. The factory has submitted the revised EA to RSC which is currently under review. During the verification, some mis matches were found which will be addressed in review comments. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 weeks | Pending Verification
Initial Inspection |  | 7 | Connection Gap. (External Steel Stair, Utility Building II) | The building engineer is required to carry out suitable remedial works. | Factory has been minimized the the Connection Gap. | May 29 2024 | On 08-Dec-2024: Connection gap has been repaired. | within 6 weeks | Corrected
Initial Inspection |  | 8 | Mismatches in as-built drawings. (Childcare Building) | The building engineer is required to prepare as-built drawings reflecting the on-site condition. | The factory has been updated as-built drawing. | May 29 2024 | On 08-Dec-2024: As-built drawings were prepared as a part of EA. During the inspection, as built drawings were found satisfactory with as-built condition. | within 6 weeks | Corrected
Initial Inspection |  | 9 | The design report required to be reviewed against lateral loading. (Childcare Building) | Prepared design report to be checked against lateral loads following BNBC 2006 by RSC. | RSC has accepted the EA documents on 30th July 2025. (Done) | May 29 2024 | On 08-Dec-2024: The factory has submitted the revised EA to RSC which is currently under review. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 weeks | Pending Verification
Initial Inspection |  | 10 | The design report required to be reviewed against lateral loading. (Childcare Building) | Carry out remedial works if required. | No Remediation Required and RSC has accepted the EA documents on 30th July 2025. (Done) | Sep 30 2024 | On 08-Dec-2024: After EA acceptance factory will carry out remedial work if required. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 months | Pending Verification
Initial Inspection |  | 11 | Deflected deck slab on the stair. (Childcare Building) | The building engineer is required to check the adequacy of the steel deck and suggest proper remedial methods. | RSC has accepted the EA documents on 30th July 2025. (Done) | May 29 2024 | On 08-Dec-2024: This issue is required to be covered in EA. The factory has submitted the revised EA to RSC which is currently under review. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 weeks | Pending Verification
Initial Inspection |  | 12 | Deflected deck slab on the stair. (Childcare Building) | Carry out remedial works if required. | No Remediation Required, and RSC has accepted the EA documents on 30th July 2025. (Done) | Sep 30 2024 | On 08-Dec-2024: After EA acceptance factory will carry out remedial work if required. RPO Comments: On 30-July-2025 the design documents (DEA) have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | within 6 months | Pending Verification

## Fire
Date
15-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD. (Extension), 14 No. Genda, Karnopara, Ulail, Savar, Dhaka, Dhaka
Date of Inspection |  | 2024-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exterior exit stair is not separated from the building. Location: Child care building and Utility building-2 | Exterior exit stairs shall be separated by minimum 2-hr fire-rated construction and the rating of the exterior wall shall extend 3.05 m (10 ft.) beyond the ends of the stair structure. | We have already completed the exterior exit stair separation work from the building as per RSC Technical guideline. (The issue has been corrected) | Jul 15 2024 | On 02-Jun-25: Corrected. Factory has separated the exterior exit stair from non-rated shed areas by fire rated construction (Brick wall) and sealed all unprotected openings and penetrations from building interior upto 10 ft. Factory has installed vestibules at required locations at Utility Building-2. On 23-Sep-25: Corrected | Within 3 Months | Corrected
Initial Inspection |  | 2 | The exit stair is not separated from other occupancy due to the non-rated construction at child care building and non-functionality of the hardware of the fire rated door. Furthermore, the gap beneath the fire rated door has been found more than 19 mm at utility building. Some fire doors installation is underway. | Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. The clearance under the bottom of a fire door shall be a maximum of 19 mm. From edges and top shall be limited to a maximum 4.8 mm. All measurement shall be taken from the ""pull side"" of the door. Any modification of fire doors beyond the job site preparation shall be approved by the door manufacturer. Install the fire door as per NFPA 80. Factory shall ensure the integrity of the functionality of the fire rated door through proper datasheet, certificate and listing label. | We have alreadysubmited detailed installation documentation for the AAC blocks, including datasheets and certification/test reports, to the RSC on 27-Nov-25 for review. | Jul 15 2024 | On 02-Jun-25: In-progress. Child Care Building: Factory has installed fire doors at all required locations. But the non-rated steel members are not yet separated properly. Gap beneath the fire door has been found more than recommendation in several doors. Utility Building-2: Fire door has been installed at all required locations. The installed fire doors were found functional during inspection. However, the required rating of the wall of exit enclosure has not been ensured at installed fire door frame area. On 23-Sep-25: The gap beneath the fire door has been corrected and is now within the acceptable limit. However, the factory has enclosed the steel portion of the stairs with AAC blocks, which required detail analysis and test report to ensure proper rating of construction materials. Submit detailed installation documentation, including datasheets and certification/test reports to RSC for review and ensure the construction complies with RSC review comments. Comments from RPO: On 13-Jan-2026 the factory management submitted the documents on 27-Nov-2025 which is under review. | Within 3 Months | In Progress
Initial Inspection |  | 3 | The exit discharge path was not fire separated from work areas, or other spaces at ground floor by fire-rated construction due to opening from generator room of the building. Location: Stair-1, Utility building-2 | Ensure that the passageway is fire rated by 2-hour including protection of unprotected opening by minimum 1.5 hour. An egress court serving as a portion of the exit discharge shall be open to the sky or provided with a fire resistance rated enclosure the same as the exit enclosure. Egress courts less than 3050 mm (10 ft) in width (as measured from the building and the adjacent property line) shall be provided with walls having a 1-hr fire resistance rated construction for a distance of 3050 mm (10 ft) above the floor of the court. | Work has been done as per RSC guideline. ( The issue has been corrected) | Jul 15 2024 | On 02-Jun-25: Corrected. Discharge path from stair-1 has been separated by fire rated construction. On 23-Sep-25: Corrected | Within 3 Months | Corrected
Initial Inspection |  | 4 | Ground floor exit-3 discharge path width of child care building is less than 10 feet and not separated from the surrounding building openings. | An egress court serving as a portion of the exit discharge shall be open to the sky or provided with a fire resistance rated enclosure the same as the exit enclosure. Egress courts less than 3050 mm (10 ft) in width (as measured from the building and the adjacent property line) shall be provided with walls having a 1-hr fire resistance rated construction for a distance of 3050 mm (10 ft) above the floor of the court. | Ground floor of childcare building discharge path already separated by fire rated construction. ( The issue has been corrected) | Jul 15 2024 | On 02-Jun-25: Corrected. Discharge path from exit-3 has been separated by fire rated construction. Exit-3 has been permanently sealed by fire rated construction. On 23-Sep-25: Corrected | Within 3 Months | Corrected
Initial Inspection |  | 5 | The substation room is not separated by fire rated construction due to openings and nonrated structure. | Separate the substation room by a minimum 2-hr fire-rated construction. Seal and/or protect all openings to maintain the required fire separations. When located on the exterior of a building 3m (10 ft.) spatial distance shall be maintained around the substation. | We have already completed the sub-station separation work from the building as per RSC Technical guideline. (The issue has been corrected) | Jul 15 2024 | On 02-Jun-25: Corrected. Substation room has been separated by fire rated construction. On 23-Sep-25: Corrected | Within 3 Months | Corrected
Initial Inspection |  | 6 | The intermediate distance between child care building and acid wash shed is only 6 feet 8 inch and exterior wall is not protected by fire rated assembly as per BNBC Part 3 Table 3.2.2 | All new buildings and structures shall be separated from other buildings in accordance with BNBC Part 3 Table 3.2.2 and BNBC Part 3 Section 2.4.1.3. Exterior walls of exit enclosures in new and existing buildings must meet the requirements of BNBC. (See also 6.14.5). | Ground floor of childcare building already separated by fire rated construction. ( The issue has been corrected) | Jul 15 2024 | On 02-Jun-25: Corrected. Factory has constructed 10 inch fire rated brick wall upto 10 ft height between the Child Care building and Acid Wash shed. On 23-Sep-25: Corrected | Within 3 Months | Corrected
Initial Inspection |  | 7 | The main structural element of the building is constructed by steel which is non-rated and were found in exposed condition without any fire protection. Location: Child care building | The building is a new steel structure which shall be type-I or II construction. So, provide require rating in the structural elements of the building. Consult with a qualified fire protection engineer. Follow BNBC 2020-Table 3.3.1, 3.2.4 & 3.1.9. Factory shall ensure that, all the design, data sheet, certificate, and the design-philosophy has been reviewed from the RSC prior to install the structural fire protection system. | PFP Drawing under review with RSC | Oct 15 2024 | On 02-Jun-25: In-progress. The factory has received the rejection feedback letter of the last design submission (3rd time) on 13-May-2025. Reportedly, factory has submitted (4th time) the updated Design philosophy and necessary documents addressing all issues as per the review feedback to RSC for further review on 02-June-2025. On 23-Sep-25: Comment is same as previous follow-up. The factory has submitted (4th time) the updated Design philosophy and necessary documents to RSC for further review on 02-June-2025. Awating RSC feedback. Comments from RPO: On 13-Jan-2026 the factory management has submitted the PFP drawing on 1-Jan-2026 which is under review. | Within 6 Months | In Progress
Initial Inspection |  | 8 | Building did not have adequate evacuation map, stair designation signs and occupant load signs at required locations on all floors Location: Child care building and Utility Building-2 | Provide Evacuation map, stair designation signs and occupant load signs at all required locations as per RSC Technical guideline. | We have already completed the evacuation map, stair designation signs and occupant load signs at all required locations as per RSC Technical guideline.(The issue has been corrected) | May 15 2024 | On 02-Jun-25: Corrected. Provided. On 23-Sep-25: Corrected | Within 1 Month | Corrected
Initial Inspection |  | 9 | Handrails at open side acting as a guard in the exit stair where the height of the handrails found 35 in. Guards shall not be less than 42 inch to avoid falling hazard. Location: Child care building and Utility Building-2 | Stairways serving as means of escape shall have continuous guards and handrails on both sides. Provide guards at all open sides of means of egress with a minimum height of 42 inches. Open guards shall have intermediate rails or pattern such that a sphere 200 mm (8 in.) in diameter cannot pass through any opening up to a height of 865 mm (34 in.). | We have already completed handrails & guards to avoid falling hazard as per RSC Technical guideline. (The issue has been corrected) | Jun 15 2024 | On 02-Jun-25: Corrected. Provided as per recommendation. On 23-Sep-25: Corrected | Within 2 Months | Corrected
Initial Inspection |  | 10 | Handrails are not provided on both sides of the exit stairs on all floors. Location: Child care building, Stair-1 | Provide handrails on both sides of the exit stair. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. | We have already completed handrails & guards to avoid falling hazard as per RSC Technical guideline. (The issue has been corrected) | May 15 2024 | On 02-Jun-25: Corrected. Provided. On 23-Sep-25: Corrected | Within 1 Month | Corrected
Initial Inspection |  | 11 | The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards. Location: Child care building and Utility building-2 | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. Submit the fire alarm system design to RSC for review. Once the design is reviewed, install and modify the fire detection and alarm system throughout the building in accordance with review comment, Accord/ RSC Technical Guidelines (Standard) and NFPA 72. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | The fire alarm system design drawing already reviewed by RSC on october 21, 2024. We are doing installation work as per reviewed drawing. We will submit Pre-T&C documents to RSC within 30-06-2025. | Oct 15 2024 | On 02-Jun-25: Proposed initial drawing has been reviewed by RSC on 21-Oct-2024. Reportedly, Installation work has been completed. Factory has submitted the as built drawing on 28-May-2025 to RSC. It's currently under desk based documents review. Additionally, FACP was found in normal and active condition during inspection. On 23-Sep-25: A pre-T&C has been conducted, and the fire alarm & detection system is not ready for T&C VI. A pre-T&C closure verification inspection is required. For details, see the Pre-T&C report. | Design Review within 2 Months and installation within 4 Months. | Pending Verification
Initial Inspection |  | 12 | Inspection, testing, and maintenance for the fire alarm system is not in accordance with NFPA 72. Location: Child care building and Utility building-2 | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. (After Installation) | It is an integrated part of the fire detection and alarm system. We will maintain inspection, testing and maintenance work as per RSC instructions/guidelines after installation work. | Oct 15 2024 | On 02-Jun-25: It is an integrated part of the Fire Alarm and Detection (FADS) system. On 23-Sep-25: Corrected. Maintained for the existing system. | Within 1 Month after installation | Corrected
Initial Inspection |  | 13 | The building has an occupied floor greater than 10 meter (33 feet) where required standpipe system found under installation. Standpipe installation requires detailed review to confirm compliance with NFPA 14, 20 and RSC standards. Location: Utility building-2 | Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC standard and NFPA 14,20,22 and 24. After installation the owner shall contact the RSC for witness of conducting the final acceptance testing of the standpipe system. | The SUPS design drawing already reviewed by RSC on February 19, 2025. We are doing installation work as per review drawing. Hopefully the work will be completed as per RSC guideline. | Oct 15 2024 | On 02-Jun-25: Proposed initial drawing has been reviewed by RSC on 19-Feb-2025. Reportedly, Installation work has been completed. Factory has submitted the as built drawing on 28-May-2025 to RSC. It's currently under desk based documents review. Both fire pumps were found in active condition during inspection. On 23-Sep-25: A pre-T&C has been conducted, and the fire pump & standpipe system is not ready for T&C VI. A pre-T&C closure verification inspection is required. For details, see the full-T&C report. | Design Review within 2 Months and installation within 4 Months. | Pending Verification
Initial Inspection |  | 14 | Inspection, testing and maintenance of the standpipe system is not found in accordance with NFPA 14 and 25. Location: Utility building-2 | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14 and 25. | It is an integrated part of the SUPS system. We will maintain inspection, testing and maintenance work as per RSC instructions/guidelines after installation work. | Oct 15 2024 | On 02-Jun-25: It is an integrated part of the Fire Protection (SUPS) system. On 23-Sep-25: Corrected. Maintained for the existing system. | Within 1 Month after installation. | Corrected
Initial Inspection |  | 15 | Inspection, testing, and maintenance for the fire pump is not in accordance with NFPA 10 and 25 or as per RSC standard. | Inspect, test and maintain the fire pump, and keep written records on-site, in accordance with NFPA 20 and 25 or as per RSC standard. | It is an integrated part of the SUPS system. We will maintain inspection, testing and maintenance work as per RSC instructions/guidelines after installation work. | Oct 15 2024 | On 02-Jun-25: It is an integrated part of the Fire Protection (SUPS) system. On 23-Sep-25: Corrected. Maintained for the existing system. | Within 1 Month after installation. | Corrected
Initial Inspection |  | 16 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with RSC technical guidelines (standard). (Child care building and Utility building-2) | Inspect, test and maintain the emergency lighting system in accordance with RSC technical guidelines (standard). Keep written records on-site. | We are already maintain inspection, testing, and maintenance for the emergency lighting system according to the RSC technical guidelines. (The issue has been corrected) | May 15 2024 | On 02-Jun-25: Corrected. Maintained as per standard. On 23-Sep-25: Corrected | Within 1 Month | Corrected
Initial Inspection |  | 17 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. (Child care building and Utility building-2) | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | We are already maintain inspection, testing, and maintenance for the portable fire extinguishers according to the RSC technical guidelines. (The issue has been corrected) | May 5 2024 | On 02-Jun-25: Corrected. Maintained as per standard. On 23-Sep-25: Corrected | Within 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding (2nd FU): Penetrations through floor/ceiling assemblies are found unsealed. Location: Day care Building Non-compliance reason: Unsealed Plumbing Pipe | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr./ 2-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating in accordance with section 4.7 of RSC Technical Guideline (Standard) Or, Provide a minimum 2-hr fire rated shaft to separate the penetration from each floor if required. | We have already planned the work of removing PVC pipes from floor to floor penetrations. Hopefully, the work will be completed during the upcoming Eid holidays. | Nov 23 2025 | On 23-Sep-25: NEW FINDING Comments from RPO: On 13-Jan-2026 the factory management has not reported remediation completion and the issue needs to be remediated. | Within 2 Months | In Progress

## Electrical
Date
15-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD. (Extension), 14 No. Genda, Karnopara, Ulail, Savar, Savar, Dhaka
Date of Inspection |  | 2024-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | SLD has already been reviewed in the RSC. and SLD is accepted in RSC on 01-08-2024.We have already completed modification work 100% of the as built electrical SLD work as per RSC guidelines. (Corrected) | Jun 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. | The work has been done as per RSC guidelines. (Corrected) | Jul 17 2024 | RPO Comments: On 02-Mar-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 3 | Insulation resistance test of electrical power cables is not available. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | The work has been done as per RSC guidelines. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 4 | Thermography scanning report is not available. | Thermography survey must be done and recorded at least twice in a year. | The work has been done as per RSC guidelines. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 5 | Earth pit resistance record is not available. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made, and the result shall be available to the Inspector when required. | The work has been done as per RSC guidelines. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 6 | No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all using records. | By introducing and implementing the LOTO policy we are working on using LOTO (Lock-Out-Tag-Out) devices to ensure the safety of personnel during any maintenance. and keeping records of all usage. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 7 | Flexible PVC pipe is used to cover power and signal cable for boiler. | Power and signal cable for boilers shall be distributed using proper type insulator to avoid damage of cables. | The work has been done as per RSC guidelines. (Corrected) | Jun 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 8 | Generator room is filled with debris (or used as temporary storage). | Generator room must be kept neat and clean. | Materials stored temporarily in the generator room are kept in specific stores.(Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 9 | Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | The work has been done as per RSC guidelines. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 10 | Distribution Board's bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Each electrical distribution board/panel is properly sealed. (Corrected) | Jun 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 11 | Phase separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | The work has been done as per RSC guidelines. (Corrected) | Jun 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 12 | Non-rated and non-certified comb bar used for powering multiple MCB. | For connecting multiple MCB use rated and listed comb bar. | The work has been done as per RSC guidelines. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. The factory uses a 32A TP breaker as the incoming breaker. | 1 MONTH | Corrected
Initial Inspection |  | 13 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | The work has been done as per RSC guidelines. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 14 | Earthing bar installed on insulator. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | The work has been done as per RSC guidelines. (Corrected) | May 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 15 | Outdoor cables are not covered to protect from weather effects. | Outdoor cable trays/ladders shall be covered properly to avoid seasonal effects on cables and its longevity. | The work has been done as per RSC guidelines. (Corrected) | Jun 17 2024 | RPO Comments: On 02-Mar-20254: the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 16 | Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). | The work has been done as per RSC guidelines. (Corrected) | Jun 17 2024 | RPO Comments on 16-OCT-2024 : the factory management reported the remediation completion. This item will be verified in the next inspection. On 02/06/2025: Corrected. Factory removed all hanging cable. | 2 MONTHS | Corrected

## Boiler
Date
15-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD. (Extension), 14 No. Genda, Karnopara, Ulail, Savar, Dhaka, Dhaka
Date of Inspection |  | 2022-04-26
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 9109 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 9110 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9900 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have sell this boiler | Apr 9 2026 | Comments on 07-Mar-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 5405 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 12846 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Temporary ShutDown | Apr 9 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 6 | BB 12847 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 5737 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 6464 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 3583 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 9109 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 11 | BB 9110 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 9900 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have sell this boiler | Apr 9 2026 | Comments on 07-Mar-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 13 | BB 5405 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | This worK will be done with in 2 months | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 14 | BB 12847 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 12846 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Temporary ShutDown | Apr 9 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 16 | BB 5737 | Necessary technical documents (Piping & Instrumentation diagram, commissioning documents, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 17 | BB 9900 | Necessary technical documents (Piping & Instrumentation diagram, commissioning documents, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have sell this boiler | Apr 9 2026 | Comments on 07-Mar-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 18 | BB 6464 | Necessary technical documents (Piping & Instrumentation diagram, commissioning documents, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 19 | BB 12847 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have already solve this issue | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 20 | BB 9109 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have already solve this issue | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 21 | BB 9110 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have already solve this issue | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 22 | BB 5405 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have install drain arrangement system in proper way of the safety valve. | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 23 | BB 5737 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already solve this issue | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 24 | BB 6464 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already solve this issue | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 25 | BB 3583 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 26 | BB 9109 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 27 | BB 9110 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 28 | BB 9900 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | Sell | Mar 9 2026 | Comments on 07-Mar-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 29 | BB 5405 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 30 | BB 9109 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 31 | BB 9110 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 32 | BB 9900 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have sell this boiler | Feb 23 2026 | Comments on 07-Mar-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 33 | BB 5405 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 34 | BB 12847 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 35 | BB 5737 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This worK will be done with in 2 months | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 36 | BB 6464 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This work is Completed | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 37 | BB 12847 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This work is Completed | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 38 | BB 12846 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | Temporary ShutDown | Apr 9 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 39 | BB 3583 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 40 | BB 5405 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 41 | BB 9109 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 42 | BB 9110 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 43 | BB 12846 | Necessary technical documents (except boiler operational logbook) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Temporary ShutDown | Apr 9 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 44 | BB 12847 | Necessary technical documents (except boiler operational logbook) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 45 | BB 12846 | Inconsistency was observed between the nameplate data and the CIoB provided certificate copy for the boiler regarding maker's number. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | Temporary ShutDown | Apr 9 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 46 | BB 5405 | Boiler's initial registration certificate was not available on-site during the inspection | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | This issue will be done with in 2 Months | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 47 | BB 5737 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | We have already terminated fuel line opening with bond flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 48 | BB 13729 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 49 | BB 13729 | Steam leakage was observed in the boiler near feed tank. | The steam leakage shall be repaired to prevent burn hazard. | We already solve this issue | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 50 | BB 12848 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Temporary ShutDown | Apr 9 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 51 | BB 13073 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 52 | BB 13073 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 53 | BB 13729 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 54 | BB 13073 | Boiler steam header safety valve outlet line was not directed outside of the boiler room. | Boiler steam header safety valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We already solve this issue. | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 55 | BB 13073 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop . | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 56 | BB 13073 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | We have already install proper steam pressure gauge(20Kg). | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 57 | BB 5737 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly on the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 58 | BB 15072 | Boiler registration number plate was not found mounted on the boiler. | Boiler registration number plate shall be made available on the boiler according to the Bangladesh Boiler Act 2022. | We already mounted Boiler registration number on the Boiler. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 59 | BB 15072 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | We have already terminated fuel line opening with bond flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 60 | BB 15072 | Drainage arrangement was not installed or installed in an inadequate manner for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per the manufacturer's published guidelines or at the lowest point of the outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 61 | BB 15072 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 62 | BB 15072 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly on the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 63 | BB 15072 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 64 | BB 15072 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 65 | BB 6464 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop . | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 66 | BB 6464 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 67 | BB 6464 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 68 | BB 5405 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | This worK will be done with in 2 months | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 69 | BB 5405 | Steam leakage was observed in the boiler gauge glass. | The steam leakage shall be repaired to prevent burn hazard. | This worK will be done with in 2 months | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 70 | BB 5737 | Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. | This worK will be done with in 2 months | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 71 | BB 5737 | Drainage arrangement was not installed or installed in an inadequate manner for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 72 | BB 5737 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 73 | BB 5737 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 74 | BB 13729 | Drainage arrangement was not installed for one safety valve. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 75 | BB 9109 | Drainage arrangement was not installed for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 76 | BB 13729 | Inconsistency was observed between the commissioning and nameplate data and the CIoB provided certificate copy for the boiler regarding Maximum Allowable Working Pressure of the boiler. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | This worK will be done with in 2 months | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 77 | BB 15072 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This worK will be done with in 2 months | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 78 | BB 15072 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 79 | BB 13073 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 80 | BB 15072 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We already proper insulation of the boiler body and Steam Distribution pipe line | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 81 | BB 13073 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We already proper insulation of the boiler body and Steam Distribution pipe line | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 82 | BB 15072 | The economizer was not equipped with a safety valve. | Economizers that can be isolated from a boiler allowing the economizer to become a fired pressure vessel, shall have a minimum of one pressure safety valve in a location recommended by the manufacturer or as close as practical to the economizer outlet. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 83 | BB 13073 | Steam leakage was observed in the boiler steam header valve. | The steam leakage shall be repaired to prevent burn hazard. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 84 | BB 15072 | Visual flame monitoring glass was out of order. | The visual flame monitoring glass shall be replaced with an appropriate one. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 85 | BB 13073 | Visual flame monitoring glass was out of order. | The visual flame monitoring glass shall be replaced with an appropriate one. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 86 | BB 12847 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 87 | BB 12847 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 23 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 88 | BB 12847 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop . | Apr 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 89 | BB 9109 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | We already install Proper Steam Pressure Gauge(16KGg). | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 90 | BB 3583 | Steam leakage was observed in the boiler from gauge glass joints & safety valve flange | The steam leakage shall be repaired to prevent burn hazard. | This work is Completed | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 91 | BB 5405 | Salt and scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 92 | BB 5737 | Salt and scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 93 | BB 6464 | Salt and scale formation was observed on the fire tubes of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 94 | BB 13073 | Salt and scale formation was observed on the waterside of the boiler. The scale is thin with 1mm. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 95 | BB 13729 | The refractory lining near the burner was damaged. | The lining should be repaired according to the manufacturer's guideline. | We have already repaired the refractory lining according to the manufacturer. | May 9 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 96 | BB 3583 | Salt and thin scale formation was observed on the waterside on smoke tube and end plate. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This worK will be done with in 2 months | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 97 | BB 5405 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 98 | BB 5737 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 99 | BB 9110 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 100 | BB 5737 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 101 | BB 9110 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 102 | BB 5405 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 103 | BB 5737 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 104 | BB 6464 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 105 | BB 12847 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 106 | BB 12847 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 107 | BB 13729 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 108 | BB 9109 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 109 | BB 9109 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 110 | BB 3583 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 9 2026 | Comments on 07-Mar-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 111 | BB 3583 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 16 2026 | Comments on 07-Mar-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification