## Structural
Date
29-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB Mart Fashion Wear Ltd. (Extension), Plot No 786, Kakil Sataish Borodawra, 13/3, Purbopara Mudafa, Tongi, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2025-07-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Inconsistencies in the design report & material strength. (Extension Building) | Building engineer is required to review the design report and prepare the design report as per BNBC 1.9 | Already related documents submitted to RSC which are currently under review | Sep 12 2025 | On 08-Jan-2026: Factory has revised the design documents and as-built drawing and submitted to RSC, which is now under pre-submission stage. Progress Status: 20% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 weeks | In Progress
Initial Inspection |  | 2 | Inconsistencies in the design report & material strength. (Extension Building) | Verify in-situ concrete strength by taking min four cores from the lower-tier columns & four cores from the beam-slab (100 diameter core). | Already related documents submitted to RSC which are currently under review | Sep 12 2025 | On 08-Jan-2026: No concrete core was taken by the factory. Factory has revised the design documents consideing 3500 &3000 psi without adequate material test report and submitted to RSC, which is now under pre-submission stage. Progress Status: 0% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 weeks | In Progress
Initial Inspection |  | 3 | Inconsistencies in the design report & material strength. (Extension Building) | Verify the rebar grade. | Already related documents submitted to RSC which are currently under review | Sep 12 2025 | On 08-Jan-2026: Factory has revised the design documents consideing rebar strength 420 Mpa as per material test report and submitted to RSC, which is now under pre-submission stage. Progress Status: 30% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 weeks | In Progress
Initial Inspection |  | 4 | Inconsistencies in the design report & material strength. (Extension Building) | Carry out the suggested remedial work if required. | Already related documents submitted to RSC which are currently under review | Jan 29 2026 | On 08-Jan-2026: After EA acceptance the factory will carry out retrofitting work (if required). Progress Status: 0% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 months | In Progress
Initial Inspection |  | 5 | Lack of details in the as-built drawing. (Extension Building) | Building engineer is required to prepare detailed and accurate as-built drawings. | Already related documents submitted to RSC which are currently under review | Sep 12 2025 | On 08-Jan-2026: Factory has revised the as-built drawing and submitted to RSC, which is now under pre-submission stage. Progress Status: 30% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 weeks | In Progress
Initial Inspection |  | 6 | Undocumented non-engineered shed on the roof. (Extension Building) | Building engineer is required to carry out an Engineering Assessment on the roof prayer shed, including it in the permit drawing otherwise demolish the shed. | In Progress. We are working on it accompanied by Building consultant to remediation this issue accordingly as well as we will process the permit Drawing from Local Govt. Authority. | Sep 12 2025 | On 08-Jan-2026: No design documents were prepared for Undocumented non-engineered shed on the roof. The building engineer is required to carry out an Engineering Assessment on the roof prayer shed, including it in the permit drawing otherwise demolish the shed. Progress Status: 0% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 weeks | In Progress
Initial Inspection |  | 7 | Undocumented non-engineered shed on the roof. (Extension Building) | Carry out the suggested remedial work if required. | In Progress : We are working on it accompanied by Building Engineer & consultant to prepare the necessary drawing and documents. Also will do remedial work if required.) | Jan 29 2026 | On 08-Jan-2026: After EA acceptance the factory will carry out retrofitting work (if required). Progress Status: 0% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 months | In Progress
Initial Inspection |  | 8 | Anchorage of non-structural elements (Extension Building) | Provide anchorage on the non-structural elements. | In Progress : Non-structural elements layout have not finalized & fixed yet. After finalized we will remediate the issue. We are working on it, need more time. | Jan 29 2026 | On 08-Jan-2026:During inspection, no anchorage was found on the storage racks. Provide anchorage on the non-structural elements. Progress Status: 0% RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 months | In Progress
Initial Inspection |  | 9 | Dampness on the brick wall (Extension Building) | Building engineer is required to remove the dampness and repair with a suitable method. | Corrected | Sep 12 2025 | On 08-Jan-2026: Factory has repaired the damped area. No dampness was observed during inspection. | within 6 weeks | Corrected
Initial Inspection |  | 10 | Uncontrolled loading on all floors (Extension Building) | The building engineer is required to implement the load management program (posting load plan, marking storage area & height and maintaining loading within limit) | In Progress : We are working on it accompanied by Building consultant to remediate this issue of Load management accordingly. Need more time. | Sep 12 2025 | On 08-Jan-2026: During inspection, no floor load plan was found posted. Also no height marking was observed at storage area. However, floor load was found below 6 kPa. The building engineer is required to implement the load management program (posting load plan, marking storage area & height and maintaining loading within limit). Progress Status: 0%. RPO Comments On 15-Mar-2026: The design documents of revised DEA is under review by the RSC. | within 6 weeks | In Progress
Initial Inspection |  | 11 | Exposed rebar on the roof. (Extension Building) | Building engineer is required to remove the rust and provide anti-corrosive coating. | Corrected | Sep 12 2025 | On 08-Jan-2026: No exposed re-bar was found during inspection. | within 6 weeks | Corrected

## Fire
Date
29-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB Mart Fashion Wear Ltd. (Extension), Plot No 786, Kakil Sataish Borodawra, 13/3, Purbopara Mudafa, Tongi, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2025-07-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The occupiable roof was not provided with an adequate parapet/guard rail (available 40 inches). | All occupiable roofs shall be provided with parapets or guards with a minimum height of 1067 mm (42 in.) | Corrected | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 2 | The building did not have stair designation signs at the required locations.Location: All floors. | Provide stair designation sign at at each floor entrance from the stair to the floor in English and Bengali. Signs shall indicate the name of the stair and the floor level. Signs shall be posted adjacent to the door in accordance with RSC Technical Guidelines (Standard), Section 6.9.3. | Corrected | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 3 | Exit stairs serve more than 5 stories and do not have required re-entry provisions on all floors. | Every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets RSC Technical Guidelines (Standard)¹ V1.0. Section 6.8.3.1 | In progress. This issue is very new to us, need to details information, need to siting with RSC technical team. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 4 | Building does not have occupant load signs at required locations on all floors. Location: All floors. | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.4.4 . | Corrected. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 5 | Fire evacuation maps are not updated as per site condition. Location: All floors. | Update the fire evacuation map and shall be posted at the entrance to each exit stair in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 13.3. | Corrected. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 6 | The exit stair enclosures are not separated from work areas and other spaces on each floor by fire-rated construction because the fire doors at the exit stair enclosures are not interfaced with any fire alarm & detection system.Locations: All floors. | The exit stair enclosure shall be provided with a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1.5 hr. fire-rated door and seal all penetrations and openings by 2 hr. fire rated fire-rated barrier construction for buildings with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system.Keep proper datasheet & certifications for installed fire doors & accessories on-site for verification. The clearance under the bottom of a door shall be a maximum of 3⁄4 in. (19 mm). | In Progress. All Exit Stair have been separated by adequate fire rated doors. But Interfacing with Fire Alarm is not completed yet. Because, Fire Alarm System is not installed yet. F.A. Installation work is in progress. | Oct 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 7 | Storage areas discharge directly into the exit stair enclosure.Location(s): 1st, 2nd, 4th & 5th floors. | Openings from the exit enclosure to Storage areas shall be provided with a vestibule with fire-rated construction and openings in accordance with section 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a min 1-hr fire-rated door on the exit stair side and a 1.5-hr fire-rated door on the Store side. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure as per RSC Technical Guidelines (Standard)¹ V1.0. section 6.14.3. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. | In Progress. This issue is very new to us, need to details information/ discussion and need to siting with RSC technical team. | Oct 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 8 | Aisles were found missing in several locations throughout the building. Location(s): 1st floor, 4th floor, 5th floor. | Provide minimum aisle widths of 36-in. Aisles mark shall be clearly visible. | In Progress. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 9 | Width of aisles is less than 0.9m (36-in.). Location: 3rd floor. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.) in accordance with section 6.5.1 of RSC Technical Guidelines (Standard)¹ V1.0. | In progress Actually our extension building occupied partially , not yet floor lay out finalized. After floor setting complete , we confirmed each aisle widths of 36 inch. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 10 | A single means of exit has been provided in the 6-storied building.Location: Building-C. | The number of means of egress from any floor, story, or portion thereof shall not be less than 2 except where a single exit is permitted by RSC Technical Guideline (Standard), section 6.6.2. Provide additional exit and ensure that the exit doors or means of egress openings are located a distance apart as per RSC Technical Guideline (Standard) section 6.6.6 | In Progress. Need to details information/ discussion and need to siting with RSC technical team. | Oct 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 11 | Minimum ceiling height of the production floors is less than 3.3 meters for New Building. Location(s): Ground floor, 3rd floor. | The ceiling height of a production floor shall not be less than 3.3 meter as per article 1.2, chapter 1, part III and article 2.11, Part III, Chapter -2, BNBC 2020. | In Progress. This is critical issue as this is built in problem, need to further more discussion with RSC technical team. | Oct 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 12 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes.Location(s): All floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | In Progress Floor lay out not yet complete, just m/C setting, production furniture fixing, after completion lay out , we confirm maintained aisles adequate illumination levels are not anticipated along egress routes.Location(s) in all floors. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 13 | Directional signs are not provided where the direction of the path of travel to an exit has changed.Location(s): All floors. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | In Progress Floor occupaid partially, after completion the floor layout , we will finalized the Directional signs. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 14 | Exit signs are not provided at the exits.Location(s): All floors. | Lighted exit signs shall be placed at entrance to an exit. Additional directional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious.Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated at all times. Exit Sign shall provide in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11. | Work in Progress. We will set Exit signs with battery backup/ IPS support. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 15 | The main structural element of the prayer room on the rooftop (Building height up to prayer room shed: approx 72 feet) is constructed of steel, which is non-rated and was found in exposed condition without any fire protection. | The construction type shall confirm to be in accordance with BNBC 2020 Part-3, Table 3.1.7. Ensure fire resistive rated construction following Table 3.3.1 (a) Part 3 Section-3, Table 3.2.2 and Table 3.2.3 Part 3 Section 2 and Table 4.1.1 from BNBC 2020 Part 4 Section 1. Provide design philosophy to determine the construction type as per BNBC 2020. If any construction rating requires, Consult a qualified fire protection engineer to achieve the require fire rating.Submit the design philosophy along with the required documents to RSC for review the required construction type. Once the design philosophy is reviewed, provide fire ratings of structural members. | In Progress We will prepare accordingly | Jan 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 6 months | In Progress
Initial Inspection |  | 16 | The required fire separation distance for Building-C does not comply with the requirements of BNBC 2020. | The exterior walls shall have a fire resistance and opening protection as specified in BNBC 2020 Part 3 Table 3.2.2 & 3.2.3 and BNBC 2020 Part 3 Section 2.4.1.3. | In Progress We will appoint fire consultant and proceed for remediation this issue with accordance of BNBC2020 | Jan 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 6 months | In Progress
Initial Inspection |  | 17 | Fire drills are not conducted according to section 13.2 of RSC Technical Guidelines (Standard)¹ V1.0. | Fire drills shall be conducted according to section 13.2 of RSC Technical Guidelines (Standard)¹ V1.0. Fire drills shall be conducted on a monthly basis as outlined in BNBC 2020 Part 4 Appendix A. | Corrected. We have taken initiatives and we are conducting Fire Drill accordingly. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 18 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The RSC standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC standard. Keep written records on-site. | In Progress. After installing completion of exit sign and emergency light will confirm maintain the testing and maintenance as per following with the RSC standard. Floor layouts are not completed yet. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 19 | Fire Alarm & Detection System (not installed yet) requires a detailed review to confirm compliance with NFPA 72 and RSC Technical Guidelines (Standard). | Submit the fire alarm and detection system design to RSC for review. Once the design is reviewed, install and modify the fire detection and alarm system throughout the building in accordance with review comment, RSC Technical Guidelines (Standard) and NFPA 72. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | In Progress : After completed all floor layouts we will start this work. We will arrange to prepare the Fire Alarm & Detection System by Fire consultant and submit for approval to RSC. After Approval will installed Fire Alarm & Detection System. | Jan 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Design within 2 month and installation within 4 months | In Progress
Initial Inspection |  | 20 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72and RSC Technical Guidelines (Standard)¹ V1.0. | In Progress. After installation completed then start the Inspection , testing and maintenance for the Fire alarm System is in accordance with NFPA72. | Feb 28 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month after installation. | In Progress
Initial Inspection |  | 21 | Standpipe & Hose system (not installed yet) requires a detailed review to confirm compliance with NFPA 14,20, 24, and RSC Technical Guidelines (Standard). | Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC Technical Guidelines (Standard)¹ V1.0. and NFPA 14, 20,22 and 24. After installation the owner shall contact the RSC for witness of conducting the final acceptance testing of the standpipe system. | In Progress : We are working on it, we are hiring a Fire consultant to prepare the design and will submit for RSC approval. After got the approval will installation Standpipe and hose system as per following NFPA 14,20,24 and RSC Guidelines (standard) | Jan 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Design within 2 month and installation within 4 months | In Progress
Initial Inspection |  | 22 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 25. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 25 and RSC Technical Guidelines (Standard)¹ V1.0.s. | In Progress : After installation completed then start the Inspection , testing and maintenance for the stand pipe system in accordance with NFPA 25. | Feb 28 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month after installation. | In Progress
Initial Inspection |  | 23 | Fire pump installation requires detailed review to confirm compliance with NFPA 20 and RSC Technical Guidelines (Standard)¹ V1.0. | Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC Technical Guidelines (Standard)¹ V1.0. and NFPA 14 and 20. The factory management shall contact RSC to conduct the final acceptance testing after the installation, testing & commissioning. | In Progress : We are working on it, we are hiring a Fire consultant to prepare the design and will submit for RSC approval. After got the approval will installation Fire Pump as per following NFPA 20 and RSC Guidelines (standard) V1.0 . | Jan 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Design within 2 month and installation within 4 months | In Progress
Initial Inspection |  | 24 | The required no smoking signs are not present in the factory. | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. Smoking sign shall post in accordance with section 13.5 of RSC Technical Guideline (Standard) | Corrected. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Initial Inspection |  | 25 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC Technical Guidelines (Standard)¹ V1.0.s. | Corrected. | Aug 29 2025 | Factory shall complete remediation action within the given timeline. RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification

## Electrical
Date
29-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | AB Mart Fashion Wear Ltd. (Extension), Plot No 786, Kakil Sataish Borodawra, 13/3, Purbopara Mudafa, Tongi, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2025-07-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. | In Progress. A proposed SLD was submitted to RSC, it has reviewed & approved from RSC. Now implementing work is going on as per accepted SLD. | Jan 29 2026 | On 07/01/2026: Not Corrected. Factory need to submit SLD to RSC for review. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 6 Months | In Progress
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | For factory buildings with a Risk Index of 40 or higher, a comprehensive Lightning Protection System (LPS) required to be designed as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | In Progress. We are working on it. Need more time. | Jan 29 2026 | On 07/01/2026: Not Corrected. No progress observed. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 6 Months | In Progress
Initial Inspection |  | 3 | No policies for PPE are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE (Personal Protective Equipment) to ensure personnel safety during maintenance activities. |  | Aug 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 4 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instructions must be posted near all electrical installations (such as LT panels, MDBs, FDBs, DBs, and SDBs) in a clearly visible location. | Corrected. | Aug 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Power cables touch other phase busbar/s. | Power bus bars must be installed with clearance of minimum 50 mm between them to prevent contact. Cables must not touch opposite bus bars under any circumstances to avoid electrical hazards. |  | Sep 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 6 | Distribution boards have no clear identification markings. | Clearly mark all distribution boards, switchboards, sub-main boards, and switches for identification. |  | Sep 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 7 | Power cables are not identified properly. | All power cables must be clearly and distinctly marked in accordance with the Single Line Diagram (SLD) to ensure proper identification, safe handling, and efficient operation. |  | Sep 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 8 | Indicator lights are mounted without disconnecting device. | Indicator lights must be connected through a control device, such as a rated fuse or Circuit Breaker (CB), to ensure they are properly protected and can be safely operated. | Corrected. | Sep 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 9 | Panel doors are not connected with earth. | All metal components within the electrical system must be securely connected to the earth. This earthing is essential to mitigate the risk of electrical shock or electrocution by providing a safe path for fault currents to dissipate. | Corrected. | Aug 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 10 | Distribution Board's top/bottom is left open (typical issue). | Each electrical distribution board or panel must be sealed to prevent the ingress of fluffs and dust. Adequate ventilation must also be ensured to maintain optimal operating temperatures. Cable glands should be used where required to secure cables and maintain the integrity of the seal. |  | Sep 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 11 | Protective device is not installed / adjusted per load demand. | Protective devices must be installed or adjusted according to the connected load current. If adjustment is not feasible, replacement is necessary. Each motor load exceeding 376W requires separate protection, adhering to nameplate data for selecting the appropriate protective device. | In Progress. We are working on it. Need more time. | Sep 29 2025 | On 07/01/2026: Not Corrected. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 12 | Multiple cables connected/terminated at the bus bar. | Each cable must be terminated at any connection point using single cable lug. | Corrected. | Sep 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 13 | Improper terminations are available at panel boards (heat shrink tube below cable lugs). | Cables needs to be terminated in busbar with proper sized cable lugs, washer, nut-bolts with direct contact to the buses. No busbar tubes shall be in between the contacts. |  | Sep 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 14 | Panel door lock broken. | Provide proper type lock on panel door and keep the panel door close. | Corrected. | Sep 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 15 | Power Cables are hanging without support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor cables must be covered, if required. | In Progress. We are working on it. Need more time. | Sep 29 2025 | On 07/01/2026: Not Corrected. Factory need to follow recommendation to provide adequate cable support. RPO Comments: On 15-Mar-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Initial Inspection |  | 16 | Wiring or extensions connecting equipment/devices are laid on floors without protection, using flexible PVC. | Run the cable connections to machines/equipment through trenches covered with checkered plates or within rigid conduits/cable trays and supports to prevent external damage. |  | Sep 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 2 Months | Corrected
Initial Inspection |  | 17 | Uncovered cable used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. |  | Oct 29 2025 | RPO Comments: On 28-OCT-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/01/2026: Corrected. | 3 Month | Corrected
Initial Inspection |  | 18 | No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation, with a thickness of at least 3 mm for rubber mats, must be provided at the working area of each electrical installation. Length of the mat shall be equal to 1 meter or the width of the board/panel, whichever is greater. This includes areas of LT panels, MDBs, DBs, SDBs, and other manually operated machinery to ensure safety and prevent electrical hazards. | Corrected. | Aug 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Corrected. | 1 Month | Corrected
Initial Inspection |  | 19 | Indicator lamps and metering devices (Ammeter, Voltmeter) installed on panel board are not operational. | All indicator lamps and metering devices installed on the panel board must be fully operational to prevent the risk of false or misleading information, which could compromise the safety and proper functioning of the electrical system. Regular checks and maintenance should be conducted to ensure their accuracy and reliability. | Corrected. | Sep 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Not Corrected. | 2 Months | Corrected
Initial Inspection |  | 20 | Power sockets are kept on floor/hung without support. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200mm above the floor level. | Corrected. | Sep 29 2025 | RPO Comments On 28-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/01/2026: Corrected. | 2 Months | Corrected

## Boiler
Date
29-Mar-2026 | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address
Date of Inspection
Finance Plan Agreed | Yes