## Structural
Date
01-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD., 14 No. Genda, Karnopara, Ulail, Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-04-02
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Verify concrete strengths in columns in GF | Factory Engineer to review design, loads and columns stresses in both buildings. | This issue has been included in EA of Utility building. EA of Utility building has been been re-approved by Accord on 27th December, 2018. No remediation is required for RCC portion of the building. We are waiting for Accord verification.(Corrected) | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: This issue will be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: This issue is required to be covered in DEA. DEA of Main factory building (Basement +11 story) & Accessories building( 6 stories) have been accepted by Accord on 28 May 2017, But revised DEA of Utility building and Steel Structures has been submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: This issue is required to be covered in DEA. DEA of Main factory building (Basement +11 story) & Accessories building( 6 stories) have been accepted by Accord on 28 May 2017. After that factory management submitted another submission on 08/03/2018 and got a review mail from ACCORD for utility building, dry process building and R & D building on 29/03/2018. So factory was required to submit revised DEA within 12/04/2018. On 31/07/2018: DEA report for Utility building, Dry process building, and R & D building have been reviewed and accepted by Accord on 22 July 2018. All the retrofitting works are required to be completed by September 15, 2018. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Accord within mentioned time-line. On 6th Feb 2019 & 17th Feb 2019: DEA has been reviewed and re-accepted from Accord on 27th Dec 2018. However, during inspection some discrepancies were found between as-built drawing and as-built condition (two steel columns were missing but one new steel column was found at stair area) in Utility Building. After that factory has updated the as-built drawing, retrofitting drawing and FEM model which have been reviewed and found acceptable. On 21st Aug-2019: Corrected from previous inspection. This issue has been covered in DEA which has been re-accepted from Accord on 27th Dec 2018. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. This issue has been covered in DEA which has been re-accepted from Accord on 27th Dec 2018. On 27-Jan-2022: Corrected from previous inspection. This issue has been covered in DEA. Factory got acceptance of DEA from ACCORD on 28 May 2017 for the Main Building. On 18-Sep-2022: Corrected in the previous inspection. DEA has been re-accepted by Accord on 27th Dec 2018. On 16-Oct-2023: Corrected from previous inspection. DEA has been re-accepted by Accord on 27th Dec 2018. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 2 | Verify concrete strengths in columns in GF | Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for cores from 4 columns. | This issue has been included in EA of Utility building. EA of Utility building has been submitted to Accord on 24th December, 2017. DEA of Accessories Building has already been approved by Accord on 28th May, 2017. | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: This issue will be covered in DEA & its verification. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: This issue is required to be covered in DEA report. Core test has been done. So this issue will be corrected after DEA verification. On 23/08/2017: Core test location has been verified for main building and accessories building except utility building. Core test report for utility building were not available on site. On 03/04/2018: Original core test reports of utility building were available on site. During inspection core test location were found ok. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. Cores have been taken and covered in DEA. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. On 27-Jan-2022: Corrected from previous inspection. Cores were taken and this issue was covered in DEA. On 18-Sep-2022: Corrected in the previous inspection. Cores have been taken and covered in DEA. On 16-Oct-2023: Corrected from previous inspection. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 3 | Steel infill floor in 4 Storey structure is constructed independent of the main concrete structure. | Provide calculations showing the structural adequacy of all supports for steel infill floor including wall and slab supports. Stability of the steel structure to be confirmed by calculation by Engineer. | Steel infill floor in this building is being demolished. | Aug 14 2014 | On 13/02/2015: As above. On 21/07/2016: This issue will be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: This issue is required to be covered in DEA. Revised DEA of Utility building and Steel Structures has been submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: Steel infill floor in utility building was found demolished. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. Steel infill floor in utility building was found demolished. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. Steel infill floor in utility building was found demolished. On 27-Jan-2022: Corrected from previous inspection. Factory had demolished the steel infill floor. On 18-Sep-2022: Corrected in the previous inspection. On 16-Oct-2023: Corrected previously. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 4 | Stability of steel roof to dining area. | The steel roof over the Dining Area should be reviewed by the Building Engineer and, if required, upgraded to support code vertical and wind loads or the area should be vacated and removed. | The Steel roof over the Dining Area has been removed. | Aug 14 2014 | On 13/02/2015: They have demolished their roof top structure. On 21/07/2016: Corrected in 1st follow up; found same in current. On 23/04/2017: Corrected in 1st follow up inspection. On 23/08/2017: Corrected from previous inspection. On 03/04/2018: Corrected from previous inspection. Roof top shed was found demolished. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. Factory has demolished their roof top structure. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. During inspection, Roof top shed was found demolished. On 27-Jan-2022: Corrected from previous inspection. Factory had demolished the steel roof shed. On 18-Sep-2022: Corrected in the previous inspection. On 16-Oct-2023: Corrected in the previous inspection. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 5 | Beam layout of 4 Storey Utility building | The concrete structure should be reviewed by the Building Engineer to show that the built structure matches the design intent. Particularly a check should be carried out on the beams that are shown on the drawings to be in line with the columns but are not in reality. | This issue has been included in EA of Utility building. EA of Utility building has been been re-approved by Accord on 27th December, 2018. No remediation is required for RCC portion of the building. We are waiting for Accord verification.(Corrected) | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: This issue will be covered in DEA & its verification. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017:This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: This issue is required to be covered in DEA. Revised DEA of Utility building and Steel Structures has submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: This issue is required to be covered in DEA. Factory management submitted another submission on 08/03/2018 and got a review mail from ACCORD for utility building, dry process building and R & D building on 29/03/2018. So factory was required to submit revised DEA within 12/04/2018. On 31/07/2018: DEA report for Utility building, Dry process building, and R & D building have been reviewed and accepted by Accord on 22 July 2018. All the retrofitting works are required to be completed by September 15, 2018. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Accord within mentioned time-line. On 6th Feb 2019 & 17th Feb 2019: DEA has been reviewed and re-accepted from Accord on 27th Dec 2018. Factory has completed retrofitting works as per accepted retrofitting drawing. However, during inspection some discrepancies were found between as-built drawing and as-built condition (two steel columns were missing and one new steel column was found at stair area). After that factory has updated the as-built drawing, retrofitting drawing and FEM which have been reviewed and found acceptable. Retrofitting completion certificate has also provided by the factory consultant. On 21st Aug-2019: Corrected from previous inspection. This issue has been covered in DEA which has been re-accepted from Accord on 27th Dec 2018. Factory has completed retrofitting works as per drawing. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. This issue has been covered in DEA which has been re-accepted from Accord on 27th Dec 2018. On 27-Jan-2022: Corrected from previous inspection. This issue has been covered in DEA. Factory got re-acceptance of DEA from ACCORD on 27th December 2018. On 18-Sep-2022: Corrected in the previous inspection. DEA has been re-accepted by Accord on 27th Dec 2018. On 16-Oct-2023: Corrected in previous inspection. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 6 | Beam layout of 4 Storey Utility building | All drawings to be revised to match built structure. | This issue has been included in EA of Utility building. EA of Utility building has been been re-approved by Accord on 27th December, 2018. No remediation is required for RCC portion of the building. We are waiting for Accord verification.(Corrected) | Dec 30 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: This issue will be covered in DEA & its verification. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: A set of as built drawing has been produced and submitted along with DEA which was not finalized yet. Revised DEA has been submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: This issue is required to be covered in DEA. Factory management submitted another submission on 08/03/2018 and got a review mail from ACCORD for utility building, dry process building and R & D building on 29/03/2018. So factory was required to submit revised DEA within 12/04/2018. On 31/07/2018: As-built drawings are prepared as a part of DEA. DEA report for Utility building, Dry process building, and R & D building have been reviewed and accepted by Accord on 22 July 2018. All the retrofitting works are required to be completed by September 15, 2018. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Accord within mentioned time-line. On 6th Feb 2019 & 17th Feb 2019: DEA has been reviewed and re-accepted from Accord on 27th Dec 2018. However, during inspection some discrepancies were found between as-built drawing and as-built condition (two steel columns were missing and one new steel column was found at stair area). After that factory has updated the as-built drawing and retrofitting drawing which have been reviewed and found acceptable. On 21st Aug-2019: Corrected from previous inspection. As-built drawing has been produced and accepted as a part of DEA. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. This issue has been covered in DEA which has been re-accepted from Accord on 27th Dec 2018. On 27-Jan-2022: Corrected from previous inspection. As-built drawing had been produced as a part of DEA and re-accepted from ACCORD on 27th Dec 2018. On 18-Sep-2022: Corrected in the previous inspection. As-built drawing has been produced and accepted as a part of DEA. On 16-Oct-2023: Corrected from previous inspection. As-built drawing was matched with on site condition. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 7 | Exposed Reinforcement. | Exposed reinforcement should be protected with suitable resin | Exposed reinforcement has been made protected. | Aug 14 2014 | On 13/02/2015: They have protected exposed reinforcement. On 21/07/2016: Corrected in 1st follow up; found same in current. On 23/04/2017: Corrected in the 1st follow up inspection. On 23/08/2017:Corrected in 1st follow up; found same in current. On 03/04/2018: Corrected from previous inspection. Found same during inspection. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. Exposed reinforcement has been removed. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. During the inspection no exposed rebar was found. On 27-Jan-2022: Corrected from previous inspection. During the inspection no exposed rebar was found. On 18-Sep-2022: Corrected in the previous inspection. Exposed reinforcement has been removed. On 16-Oct-2023: Corrected from previous inspection. No exposed rebar was observed. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 8 | Management of storage loads | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | This issue has been included in EA of Utility building. EA of Utility building has been been re-approved by Accord on 27th December, 2018. No remediation is required for RCC portion of the building. We are waiting for Accord verification.(Corrected) | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: Load plan found prepared & posted to each floor. Factory management submitted their DEA report to ACCORD which is under review. So this issue will be covered in DEA. On 23/04/2017: Load plan has been prepared and posted but not approved from ACCORD yet. During inspection overall loading found below 3 kpa. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: Load plans of Main factory building & Accessories building have been accepted along with DEA by Accord. During inspection, load plan were posted on each floor and maintained accordingly. Load plans of Utility building and Steel Structure were prepared as a part of DEA which were not finalized yet. Revised DEA of Utility building and Steel Structures has submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: Load plans had been prepared and accepted for main factory building & accessories building on 30/08/2017. During inspection load plans were found posted to all building but load plans of utility building and all steel structures were prepared as a part of DEA which were not finalized yet. Factory management submitted another submission on 08/03/2018 and got a review mail from ACCORD for utility building, dry process building and R & D building on 29/03/2018. So factory was required to submit revised DEA within 12/04/2018. On 31/07/2018: Load plan has been prepared as a part of DEA. DEA report for Utility building, Dry process building, and R & D building have been reviewed and accepted by Accord on 22 July 2018. All the retrofitting works are required to be completed by September 15, 2018. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Accord within mentioned time-line. However, floor loading was found below 42 psf (except dining) in the time of inspection. On 6th Feb 2019 & 17th Feb 2019: Load plan has been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and load was found below allowable limit (42 psf). On 21st Aug-2019: Corrected from previous inspection. Load plan has been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and load was found below allowable limit (42 psf). On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. Load plan was accepted as a part of DEA. During inspection accepted load plan was found posted at every floor. On 27-Jan-2022: Corrected from previous inspection. Load plan had been had been produced as a part of DEA and re-accepted from ACCORD on 27th Dec 2018. During inspection accepted load plan was found posted at every floor and live load was found below the allowable limit (6 kPa at storage areas and 3 kPa at normal floor area) at Main Building. On 18-Sep-2022: Corrected in the previous inspection. During inspection accepted load plan was found posted and floor loading was found within it. (6 kPa at storage areas and 3 kPa at normal floor area at Main Building) On 16-Oct-2023: Corrected from previous inspection. Load plan had been had been produced as a part of DEA and re-accepted from ACCORD on 27th Dec 2018. Load plan was found posted and floor loading was found within allowable limit (6 kPa at storage areas and 3 kPa at typica production floor area). On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 9 | Management of storage loads | Continue to implement load management plan | This issue has been included in EA of Utility building. EA of Utility building has been been re-approved by Accord on 27th December, 2018. No remediation is required for RCC portion of the building. We are waiting for Accord verification.(Corrected) | Dec 30 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: Load plan found prepared & posted to each floor. During inspection high loading not observed. Overall loading found satisfactory. On 23/04/2017: Load plan has been prepared and posted but not approved from ACCORD yet. During inspection overall loading found below 3 kpa. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: Load plans of Main factory building & Accessories building have been accepted along with DEA by Accord. During inspection, load plan were posted on each floor and maintained accordingly. Load plans of Utility building and Steel Structure were prepared as a part of DEA which were not finalized yet. Revised DEA of Utility building and Steel Structures has been submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: Load plans had been prepared and accepted for main factory building & accessories building on 30/08/2017. Overall loading was found within the acceptable limit. During inspection load plans were found posted to all building but load plans of utility building and all steel structures were prepared as a part of DEA which were not finalized yet. Factory management submitted another submission on 08/03/2018 and got a review mail from ACCORD for utility building, dry process building and R & D building on 29/03/2018. So factory was required to submit revised DEA within 12/04/2018. On 31/07/2018: Load plan has been prepared as a part of DEA. DEA report for Utility building, Dry process building, and R & D building have been reviewed and accepted by Accord on 22 July 2018. All the retrofitting works are required to be completed by September 15, 2018. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Accord within mentioned time-line. However, floor loading was found below 42 psf (except dining) in the time of inspection. On 6th Feb 2019 & 17th Feb 2019: Load plan has been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and load was found below allowable limit (42 psf) On 21st Aug-2019: Corrected from previous inspection. During inspection accepted load plan was found posted at every floor and load was found below allowable limit (42 psf). On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. Load plan was accepted as a part of DEA. During inspection accepted load plan was found posted at every floor. On 27-Jan-2022: Corrected from previous inspection. During inspection accepted load plan was found posted at every floor and live load was found below the allowable limit (6 kPa at storage areas and 3 kPa at normal floor area) at Main Building. On 18-Sep-2022: Corrected in the previous inspection. During inspection accepted load plan was found posted and floor loading was found within it. (6 kPa at storage areas and 3 kPa at normal floor area at Main Building) On 16-Oct-2023: Corrected previously. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 10 | Columns at ground floor level of chemical store are susceptible to vehicle impact. | Column to be protected from vehicle impact | Column has been made protected from vehicle impact. . | Aug 14 2014 | On 13/02/2015: They have made a new construction there, so why no way for vehicle impact. On 21/07/2016: Corrected in 1st follow up; found same in current. On 23/04/2017: Corrected in 1st follow up inspection. On 23/08/2017: Corrected in 1st follow up; found same in current. On 03/04/2018: Corrected from previous inspection. Found same during inspection. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. This structure is not existed now. New structure has been constructed in place of chemical store. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. On 27-Jan-2022: Corrected from previous inspection. This structure had been modified after initial inspection (currently name as R & D) and document of this structure had been re-accepted from ACCORD. No vehicle impact related issue is existed in this structure as no exposed column was observed. On 18-Sep-2022: Corrected in the previous inspection. No vehicle impact related issue is existed in this structure. On 16-Oct-2023: Corrected previously. Chemical store has been demolished. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 11 | Stability and connections in steel structures | Building Engineer to provide calculations to prove adequacy of as-built structures. Stability of all steel structures to be reviewed and upgraded where required. All connections in steel structures to be checked and upgraded where required. | As-built EA of Dry process building has been re-approved on 12th, May 2019. No remediation is required. We are waiting for Accord verification.(Corrected) | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: This issue will be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: This issue is required to be covered in DEA report. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017:This issue is required to be covered in DEA. Revised DEA has been submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: This issue is required to be covered in DEA. DEA of Main factory building (Basement +11 story) & Accessories building( 6 stories) have been accepted by Accord on 28 May 2017. After that factory management submitted another submission on 08/03/2018 and got a review mail from ACCORD for utility building, dry process building and R & D building on 29/03/2018. So factory was required to submit revised DEA within 12/04/2018. On 31/07/2018: This issue has been covered in DEA. DEA report for Utility building, Dry process building, and R & D building have been reviewed and accepted by Accord on 22 July 2018. All the retrofitting works are required to be completed by September 15, 2018. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Accord within mentioned time-line. On 6th Feb 2019 & 17th Feb 2019: DEA report for utility building , Dry process building and R & D building were accepted from ACCORD on 22th July, 2018. The factory got re-acceptance from ACCORD on 27th December, 2018 as discrepancy was found during DEA verification inspection. And the remediation time line was 31st January, 2019. During last inspection some mismatch was found in the retrofitting work of Dry process building. Bracing arrangements was not matched with re-accepted retrofitting drawing. The factory is required to complete the retrofitting as per accepted drawing. On 21st Aug-2019: This issue has been covered in DEA for Dry process Building which has been re-accepted from Accord on 12th May 2019. Factory has completed all remediation works as per re-accepted DEA. Retrofitting completion certificate has also been provided by the factory consultant. On 05-Sep-2021: This issue has been covered in the DEA which has been re-accepted from Accord on 12th May 2019. Factory has completed all remediation works as per re-accepted DEA. On 27-Jan-2022: Corrected from previous inspection. This issue has been covered in the DEA. Factory got DEA re-acceptance from ACCORD on 12th May 2019. Factory had completed all remediation works as per re-accepted DEA. On 18-Sep-2022: Corrected in the previous inspection. DEA which has been re-accepted from Accord on 12th May 2019. Factory has completed all remediation works as per re-accepted DEA. On 16-Oct-2023: Corrected in the previous inspection. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 12 | Stability of lightweight steel canopy adjacent to Utility Building | Lightweight steel canopy should be reviewed by the Building Engineer and, if required, upgraded to support code vertical and wind loads or the area should be vacated and removed. | This issue has been included in EA of Steel Structures. EA of Steel Structures has been re-approved by Accord on 27th December, 2018. Remediation work of steel structures has been completed on 12th January, 2019. We are waiting for Accord verification.(Corrected) | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: This issue will be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: This issue is required to be covered in DEA. Revised DEA has been submitted to Accord on 30 Aug 2017 which is in under review. On 03/04/2018: This issue is required to be covered in DEA. DEA of Main factory building (Basement +11 story) & Accessories building( 6 stories) have been accepted by Accord on 28 May 2017. After that factory management submitted another submission on 08/03/2018 and got a review mail from ACCORD for utility building, dry process building and R & D building on 29/03/2018. So factory was required to submit revised DEA within 12/04/2018. On 31/07/2018: DEA report for Utility building (including canopy), Dry process building, and R & D building have been reviewed and accepted by Accord on 22 July 2018. All the retrofitting works are required to be completed by September 15, 2018. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Accord within mentioned time-line. On 6th Feb 2019 & 17th Feb 2019: DEA has been reviewed and re-accepted from Accord on 27th Dec 2018. During inspection some discrepancies have been found between as-built drawing and as-built condition. After that factory has updated the as-built drawing which has been reviewed and found acceptable. On 21st Aug-2019: Corrected from previous inspection. DEA has been reviewed and re-accepted from Accord on 27th Dec 2018. Factory has completed remediation works as per drawing. On 05-Sep-2021: This issue has been covered in the DEA which has been re-accepted from Accord on 27th Dec 2018. Factory has completed all remediation works as per re-accepted DEA. On 27-Jan-2022: Corrected from previous inspection. (reopened, see item no-23) On 18-Sep-2022: Corrected in the previous inspection. (See item no-23) On 16-Oct-2023: Corrected in the previous inspection. Accepted drawing was matched with as built condition. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 13 | Concrete column capacity | Engineer to review structural analysis carried out on building to ensure model represents the as constructed building and concrete strengths inputted to model are based on cylinder results. | This issue has been covered in DEA. DEA of main builidng and Accessories building has been approved by Accord on 28th May, 2017. | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: This issue will be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: This issue is required to be covered in DEA. DEA of Main factory building have been accepted by Accord. On 03/04/2018: Corrected in previous follow inspection. DEA of Main factory building (Basement +11 story) & Accessories building( 6 stories) had been accepted by Accord on 28 May 2017 and during DEA verification on 23/08/2017 major discrepancies were not found. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. DEA has been reviewed and re-accepted from Accord on 27th Dec 2018. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. This issue has been covered in DEA which has been re-accepted from Accord on 27th Dec 2018. On 27-Jan-2022: Corrected from previous inspection. This issue has been covered in DEA. Factory got re-acceptance of DEA from ACCORD on 27th December 2018. Factory has completed all remediation works as per re-accepted DEA. On 18-Sep-2022: Corrected in the previous inspection. DEA which has been re-accepted from Accord on 27th December 2018.. Factory has completed all remediation works as per re-accepted DEA. On 16-Oct-2023: Corrected in the previous inspection. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 14 | Management of storage loads | Review load plans based on outcome of analysis review and actively manage this for all floor plates within the factory giving consideration to floor capacity and column capacity. | This issue has been covered in DEA. DEA of main building and Accessories building has been approved by Accord on 28th May, 2017. We have posted the approved load plan on floor areas. | Aug 14 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: Load plan found prepared & posted to each floor. During inspection high loading not observed. Overall loading found satisfactory. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: Load plan has been prepared and posted but not approved from ACCORD yet. During inspection overall loading found below 3 kpa. This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: Load plans of Main factory building have been accepted along with DEA by Accord. During inspection, load plan were posted on each floor and maintained accordingly. On 03/04/2018: Corrected in previous follow up inspection. Load plans had been prepared and accepted for main factory building & accessories building on 30/08/2017. During inspection load plans were found posted on each floor of maintained accordingly. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. Load plan has been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and load was found below allowable limit (42 psf). On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. Load plan was accepted as a part of DEA. During inspection accepted load plan was found posted at every floor. The loading condition was found as per accepted load plan. On 27-Jan-2022: Corrected from previous inspection. Load plan had been had been produced as a part of DEA and re-accepted from ACCORD on 27th Dec 2018. During inspection accepted load plan was found posted at every floor and live load was found below the allowable limit (3 kPa-Accessories Building, 2 kPa- Utility Building). On 18-Sep-2022: Corrected in the previous inspection. During inspection accepted load plan was found posted and floor loading was found within it. (3 kPa-Accessories Building, 2 kPa- Utility Building). On 16-Oct-2023: Corrected in the previous inspection. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 15 | Management of storage loads | Continually inspect floor plates based on load plans and reduce loading if necessary. | Load plan along with DEA of Main Building and Accessories Building has been approved by Accord approved by Accord on 28th May, 2017. We have posted the approved load plan on floor areas. | Dec 30 2014 | On 13/02/2015: This issue will cover under DEA. On 21/07/2016: Load plan found prepared & posted to each floor. During inspection high loading not observed. Overall loading found satisfactory. Factory management submitted their DEA report to ACCORD which is under review. On 23/04/2017: Load plan has been prepared and posted but not approved from ACCORD yet. During inspection overall loading found below 3 kpa. This issue is required to be covered in DEA. Factory management submitted DEA report to ACCORD on 16th March 2017 and it is under review. On 23/08/2017: Load plans of Main factory building have been accepted along with DEA by Accord. During inspection, load plan were posted on each floor and maintained accordingly. On 03/04/2018: Corrected in previous follow up inspection. Load plans had been prepared and accepted for main factory building & accessories building on 30/08/2017. During inspection load plans were found posted on each floor of maintained accordingly. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. Load plan has been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and load was found below allowable limit (42 psf). On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. Load plan was accepted as a part of DEA. During inspection accepted load plan was found posted at every floor. The loading condition was found as per accepted load plan. On 27-Jan-2022: Corrected from previous inspection. Load plan had been had been produced as a part of DEA and re-accepted from ACCORD on 27th Dec 2018. During inspection accepted load plan was found posted at every floor and live load was found below the allowable limit (3 kPa-Accessories Building, 2 kPa- Utility Building). On 18-Sep-2022: Corrected in the previous inspection. During inspection accepted load plan was found posted and floor loading was found within it. (3 kPa-Accessories Building, 2 kPa- Utility Building). On 16-Oct-2023: Corrected in the previous inspection. During inspection accepted load plan was found posted and floor loading was found within allowable limit (3 kPa-Accessories Building, 2 kPa- Utility Building & 6kpa-storage area). On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 16 | Cracking to Façade and structural elements | Record details of all cracking and start to monitor for any changes. | Details of all cracking and start to monitor for any changes have been recorded. | Aug 14 2014 | On 21/07/2016: Corrected in 1st follow up; found same in current. On 23/04/2017: This issue has been corrected in the 1st follow up inspection. On 23/08/2017: Found corrected from previous inspection. During inspection, no façade cracks were observed. On 03/04/2018: Found corrected from previous inspection. During inspection, no façade crack was observed. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. See Item no.20. On 21st Aug-2019: Corrected from previous inspection. During inspection no crack was found in any facade wall. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. During inspection no crack was found in any facade wall. On 27-Jan-2022: Corrected from previous inspection. During inspection no crack was found in any facade wall. On 18-Sep-2022: Corrected in the previous inspection. During inspection no crack was found in any facade wall. On 16-Oct-2023: Corrected in the previous inspection. No crack was observed on facade wall and structural element. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 17 | Cracking to Façade and structural elements | Continue to monitor cracking on the façade | Monitoring is being continued. | Dec 30 2014 | On 21/07/2016: Corrected in 1st follow up; found same in current. On 23/04/2017: This issue has been corrected in the 1st follow up inspection. On 23/08/2017: Found corrected from previous inspection. During inspection, no façade cracks were observed. On 03/04/2018: Found corrected from previous inspection. During inspection, no façade crack was observed. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. See Item no.20. On 21st Aug-2019: Corrected from previous inspection. During inspection no crack was found in any facade wall. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. During inspection no crack was found in any facade wall. On 27-Jan-2022: Corrected from previous inspection. During inspection no crack was found in any facade wall. On 18-Sep-2022: Corrected in the previous inspection. During inspection no crack was found in any facade wall. On 16-Oct-2023: Corrected in the previous inspection. No crack was observed on facade wall and structural element. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Initial Inspection |  | 18 | Water Ingress | Building Engineer to investigate source of water ingress and remedy if necessary with appropriate sealant. | This is occurred for shrinkage cracks of slab due to 1st phase construction work had been off for 3 years. For remedial actions, we have used appropriate sealants such as Deck-O-Seal to implement corrective procedures. | Aug 14 2014 | On 21/07/2016: Corrected in 1st follow up; found same in current. On 23/04/2017: This issue has been corrected in the 1st follow up inspection. During inspection water proofing work found on going. On 23/08/2017: Found corrected from previous inspection. On 03/04/2018: Corrected from previous inspection. Water ingress was not observed at the time of inspection. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. On 27-Jan-2022: Corrected from previous inspection. Water ingress was not observed at the time of inspection. On 18-Sep-2022: Corrected in the previous inspection. Water ingress was not observed at the time of inspection. On 16-Oct-2023: Corrected in the previous inspection. Water ingress was not observed at the time of inspection. On 30-Sep-2025: Previously corrected. | (within 6-weeks) | Corrected
Initial Inspection |  | 19 | Water Ingress | Continue to monitor for water ingress throughout building and implement corrective procedures if necessary. | Continuous monitoring is on. | Dec 30 2014 | On 21/07/2016: Corrected in 1st follow up; found same in current. On 23/04/2017: This issue has been corrected in the 1st follow up inspection. On 23/08/2017: Found corrected from previous inspection. On 03/04/2018: Corrected from previous inspection. Water ingress was not observed at the time of inspection. On 31/07/2018: Corrected in previous inspection. On 6th Feb 2019 & 17th Feb 2019: Corrected from previous inspection. On 21st Aug-2019: Corrected from previous inspection. No dampness or water ingress was found during inspection. Drainage system has also been improved. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. On 27-Jan-2022: Corrected from previous inspection. Water ingress was not observed at the time of inspection. On 18-Sep-2022: Corrected in the previous inspection. Water ingress was not observed at the time of inspection. On 16-Oct-2023: Corrected previously. No water ingress was observed. On 30-Sep-2025: Previously corrected. | (within 6-months) | Corrected
Follow Up Inspection |  | 20 | New Finding 1: Re-opening of issue number 16& 17: Cracking to Façade and structural elements | Record details of all cracking and start to monitor for any changes& Continue to monitor cracking on the façade | Investigation and repair of the cracks in different locations of facade wall and internal walls have been done by following appropriate method. We are waiting for Accord verification.(Corrected) | Apr 15 2019 | On 6th Feb 2019 & 17th Feb 2019: During inspection cracking was observed in different locations of facade wall and internal walls. The factory is required to investigate the cracks and repair with suitable method. Also keep monitoring the cracking on the facade. On 21st Aug-2019: As per investigation report all cracks are non structural. Factory has re-plastered all cracked areas. On 05-Sep-2021: This issue was found corrected from previous follow-up inspection. During inspection no crack was found in any facade wall. On 27-Jan-2022: Corrected from previous inspection. No crack was observed on facade wall. On 18-Sep-2022: Corrected in the previous inspection. During inspection no crack was found in any facade wall. On 16-Oct-2023: Corrected in the previous inspection. No crack was observed on facade wall and structural element. On 30-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 21 | New finding 2: Stability, capacity and connection check for new connecting bridge between 1st floor of R & D building and 2nd floor of dry processing. | Building engineer to provide the design and drawing of the bridge | We have submitted the relevant documents (analysis file, As-built drawing & EA Report) on 27th-April-2022. We have also Submit hard copy of accepted DEA documents on 22th may 2022. | Oct 10 2021 | On 05-Sep-2021: During the inspection, a newly constructed connecting bridge was found between 1st floor of R & D building (Previously chemical store) and 2nd floor of dry processing. Also, the columns were poorly connected with the roof of the connecting bridge. The factory is required to produce as-built drawing with design report and submit to RSC within 10-10-2021. On 27-Jan-2022: This issue is required to be covered in Engineering Assessment (EA) of the connecting bridge. Factory submitted the EA to RSC on 17th January 2022 which is under review. On 18-Sep-2022: Engineering Assessment (EA) of the connecting bridge was accepted by RSC on 30 May 2022. During verification, minor mismatches was found in as-built drawings. After that factory has updated the as-built drawing and FEM which was found acceptable. On 16-Oct-2023: Corrected in the previous inspection. As-built drawing was available and matched with on site conditions. On 30-Sep-2025: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 22 | New Finding 3: Cracks appeared on internal brick wall of main building | Factory engineer is require to produce crack investigation report and suggest remedial measures. | The Engineering team has investigated the reason for the crack. It is found that it is not the structural crack. We have submitted a crack investigation report & drawing for remedial measures on 27th-April-2022. All Cracks have been repaired. (The issue has been corrected) | Oct 10 2021 | On 05-Sep-2021: During inspection cracking was observed in different locations of internal wall at ground floor level of the main building. The factory is required to investigate the type of cracks and repair with suitable method as per consultant's suggestion. On 27-Jan-2022: As per crack investigation report the cracks are non structural. During inspection it was observed that factory has repaired (plastered) the crack areas as per investigation report. On 18-Sep-2022: As per crack investigation report the cracks are non structural. During inspection it was observed that factory has repaired the crack areas as per investigation report. On 16-Oct-2023: Corrected previously. No crack was observed on internal brick wall. On 30-Sep-2025: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 23 | New Finding 4: Undocumented extension of lightweight steel canopy adjacent to Utility Building. | Building Engineer to update the as-built drawing and confirm the stability of the steel structure accordingly. | We have submitted the relevant documents (analysis file, As-built drawing & EA Report) on on 27th-April-2022. We have also Submit hard copy of accepted DEA documents on 22th may 2022. | Oct 10 2021 | On 05-Sep-2021: During the inspection, undocumented extension of lightweight steel canopy was found adjacent to Utility Building. Building Engineer is required to update the as-built drawing as per on site condition & check the stability of the steel structure accordingly and submit to RSC within 10-10-2021. On 27-Jan-2022: This issue is required to be covered in Engineering Assessment (EA) of the steel canopy. Factory submitted the as-built drawing along with EA to RSC on 17th January 2022 which is under review. On 18-Sep-2022: Engineering Assessment (EA) of the steel canopy was accepted by RSC on 30 May 2022. During the inspection as-built drawings was found indicative with as built condition. On 16-Oct-2023: Corrected in the previous inspection. Accepted drawing was matched with as built condition. On 30-Sep-2025: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 24 | New finding 5: Stability, capacity and connection check for new connecting bridge between Utility and accessories building | Building engineer to provide the design and drawing of the bridge | We have submitted the relevant documents (analysis file, As-built drawing & EA Report) on on 27th-April-2022. We have also Submit hard copy of accepted DEA documents on 22th may 2022. | Oct 10 2021 | On 05-Sep-2021: During the inspection, a connecting bridge was found between 2nd floor of Utility building and accessories building. The factory is required to produce as-built drawing with design report and submit to RSC within 10-10-2021. On 27-Jan-2022: This issue is required to be covered in Engineering Assessment (EA) of the connecting bridge. Factory submitted the EA to RSC on 17th January 2022 which is under review. On 18-Sep-2022: Engineering Assessment (EA) of the connecting bridge was accepted by RSC on 30 May 2022. As per accepted EA factory has completed the required remediation. On 16-Oct-2023: Corrected in the previous inspection. Accepted drawing was matched with as built condition. On 30-Sep-2025: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 25 | New finding-6: Undocumented floor build up at toilet areas at grid (A-C, 3-4) and grid (B-F,15-16) (Main building) | Remove the floor build up from every floor of the mentioned areas | Built Up removing work from all toilet has been completed. | Mar 15 2022 | On 27-Jan-2022: During inspection undocumented floor build up found at toilet areas at grid (A-C, 3-4) and grid (B-F,15-16) in Main building which results in additional stress in the columns, beams and foundations. Factory is required remove the floor build up from every floor of the mentioned areas. On 18-Sep-2022: Factory has started the demolition work of toilet build-up which is not finished yet. On 16-Oct-2023: Factory has completed the demolition work. During inspection, undocumented floor built up was not observed in toiet area. On 30-Sep-2025: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 26 | New finding-7: Undocumented & apparently inadequate mezzanine floor inside Ground Floor (Main Building) | Relocate operation from this structure or carryout adequacy check of the structure along with the impact on main structure as it is resting on a suspended floor | RSC has accepted DEA documents. Retrofitting work on the mezzanine has been completed. | Mar 15 2022 | On 27-Jan-2022: During inspection an undocumented and apparently inadequate mezzanine floor was observed inside Ground Floor (Main Building). Factory is required to relocate operation from this structure or carryout adequacy check of the structure along with the impact on main structure because it is resting on a suspended floor. Also, implement necessary action from the adequacy check. On 18-Sep-2022: This issue is required to be covered in DEA of Main Building (West Part). Factory has submitted the DEA to RSC which is under review. On 16-Oct-2023: Factory has got DEA acceptance on 9th-August-2023. Factory has completed the remediation work. Work completion certificate was available on site. However, as-built mezzanaine column layout was not matched with as-built drawing. Factory is required to revised the design documents as per site condition and submit to RSC for review. On 30-Sep-2025: This issue has been covered in the EA, which was re-accepted by RSC on 29 January 2025. Retrofitting works were found completed as per the accepted EA, except for the continuous welding, some beam-to-column connections, and the reduced size of the anchor bolts. Later, the factory completed the continuous welding and developed the beam-to-column connections as per the accepted drawings, and sent pictorial evidence, which was found satisfactory. The building engineer also revised the drawings and adequacy calculations for the column anchor bolt details with the reduced size, which were found adequate. Pictorial evidence and the retrofitting completion certificate were available onsite. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 27 | New finding-8: Load management of 1st floor (Main Building). | Maintaining floor loading according to accepted load plan or revise the load plan as per onsite condition. | RSC has accepted the DEA documents, there is no remediation work. | Dec 10 2023 | On 16-Oct-2023: During inspection, interchange between office and store area was observed on 1st floor of main building. Factory engineer is required to maintain the floor loading according to accepted load plan and floor usages or revise the load plan as per onsite condition. On 30-Sep-2025: The load plan has been prepared as part of EA which was re-accepted by RSC dated 29-January-2025. During the inspection, accepted load plan was found posted on the floors and loading was found within the allowable limit of the accepted load plan (6 kPa for storage area; 3 kPa for production and canteen area). | (within 6 weeks) | Corrected
Follow Up Inspection |  | 28 | New finding-9: Undocumented canopy at ground floor of Main Building. | Prepare as-built drawings for canopy. | RSC has accepted DEA documents. Retrofitting work on the canopy-3 has been completed. | Dec 10 2023 | On 16-Oct-2023: An undocumented canopy was observed at ground floor of main building. Factory engineer is required to prepare the as-built drawings for canopy. On 30-Sep-2025: The Safety Check Report of the steel Canopy-3 was re-accepted by RSC dated 29-January-2025. The factory has carried out the remedial work. The retrofitting completion certificate was available on-site. During the inspection mismatches were observed in the as-built drawing, grid distances and knee bracing lengths. However, the mismatches do not affect the integrity of the structure. Additionally, two canopy adjacent to main building (Canopy 1- RC, Canopy 2- Steel) were found on-site. As-built drawing was available which matched the site condition. | (within 6 weeks) | Corrected

## Fire
Date
01-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD., 14 No. Genda, Karnopara, Ulail, Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boilers and generators on the ground floor of the Utility Building are not separated by fire rated construction. The transformer and generators in the northwest building are not separated by firerated construction. | Separate these utilities by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | All fire doors have been interfaced with FACP and ensure with door closer and push bar according to ACCORD recommendations. (Pending Verification) | Feb 28 2015 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Areas used for combustible storage noted on the 1, 3, 4 and 5th floors are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Our engineering team already made a plan to complete the task according to Accord guidelines. Hopefully the task will complete within 3 months. (In progress) | Feb 28 2015 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | The exit stairs are not separated on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. | Due to misinformation the issue has been reported. There are no penetration of exhaust duct located chemical storage at ground floor. (Pending Verification) | Feb 28 2015 | On 23/08/2017: In progress. Work has been In progress. On 31/01/2018: Corrected, all the exit doors are interfaced with functional fire alarm system. On 27/06//2018: Corrected on previous follow-up. Note: Factory shall ensure proper functioning of small part of door leaf. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Refer to issue no. 61. On 02/04/2024: Refer to issue no. 61. | Within 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies including plumbing and electrical utility risers. | Provide a minimum 2-hr firerated shaft to separate the utility risers from each floor level. | To ensure adequate departure, we have added two additional egress door at the utility building and now four exits can be use to depart from the dinning hall.((Pending Verification) | Dec 30 2014 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 56. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | A shaft (possibly for future elevator) is located adjacent to the north exit stairs. The shaft is open to the stairwell in several locations including an impromptu linen shaft. | Provide a minimum 2-hr firerated shaft to separate the shaft from each floor level and stairwell. Seal all penetrations and openings in shaft assemblies to maintain the fire separation. |  | Dec 30 2014 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. Issue is merged with issue no: 56. On 17/02/2019: Refer to issue 57. On 02/04/2024: Refer to issue 57. | Within 3 months | Corrected
Initial Inspection |  | 6 | Doors / gates with locking features are provided along some egress paths. All gates/doors were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 30 2014 | On 23/04/2017: Corrected. On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 59. On 02/04/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | Storage was located in the exit stair (storage lockers). | Remove all storage from exit stairs and egress paths. |  | Dec 30 2014 | On 23/08/2017: Corrected . On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Please see issue no. 74. On 02/04/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Collapsible gates / sliding doors are provided at building exits, exit stairs, along egress routes, and at exit discharge locations. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 30 2014 | On 23/04/2017: Corrected. On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 59. On 02/04/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 9 | North exit stairs at the main entrance discharge inside the building on the ground floor floor. | Modify stair to discharge directly outside or provide 2-hr fire-rated exit passageway leading directly outside. |  | Apr 30 2016 | On 23/08/2017: It has found same as before. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 10 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected as per previous follow up. Installation shall be as per NFPA 72. On 31/01/2018: Corrected as per last follow ups. During inspection the system found functional. Note: Sound level recommended to be increased on each floors. On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Refer to issue 58. On 02/04/2024: Refer to issue 58. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 11 | Inspection, testing, and maintenance records for the fire alarm system were not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | The fire alarm system does not appear to provide adequate audible notification coverage based upon 3rd floor observation during functional testing. | Provide additional notification appliances such that the fire alarm system is audible throughout the building in accordance with NFPA 72. |  | Feb 29 2016 | On 24/01/2017: It is an integrated part of fire alarm system. On 23/04/2017: Corrected as per Tic. On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected. On 17/02/2019: Refer to issue 58. On 02/04/2024: Refer to issue 58. | Within 6 months | Corrected
Initial Inspection |  | 13 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove the single-station smoke alarms. Provided automatic smoke detectors throughout the building in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 14 | Manual on-off switch is provided for some emergency lighting exit sign units. | Remove manual on/off switches from emergency lighting / exit sign units to prevent them from being switched off. |  | Dec 30 2014 | On 23/04/2017: Corrected. On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. Removed. On 02/04/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 15 | Directional exit signage missing from northwest corner of 2nd floor. | Provide directional exit signs where exit pathway may not be obvious. |  | Dec 30 2014 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. Provided. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | [Accessories Building]: Hazardous materials /flammable liquid storage area in the 5th floor is not separated by firerated construction (openings, non-rated doors, penetrations). | Separate the hazardous materials / flammable liquid storage room by a minimum 2- hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. |  | Feb 28 2015 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 17 | Areas used for combustible storage room in the 1st and 5th floors are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. |  | Feb 28 2015 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. Note: Factory shall separate the work station located inside the storage room. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 18 | The exit stairs are not separated from work areas or other spaces on each floor by firerated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. |  | Feb 28 2015 | On 23/08/2017: In progress. Still few area has not been separated as per ACCORD standard. On 31/01/2018: Corrected. Doors were found functional during inspection. On 27/06/2018: Corrected as per previous follow-up. Note: Interfacing of fire door was not found proper during follow-up inspection. On 17/02/2019: Corrected based on previous follow ups. Interfacing still not done, refer to issue 61. On 02/04/2024: Referred to Issue 61. | Within 3 months | Corrected
Initial Inspection |  | 19 | Unsealed penetrations and openings on several floors are located in the fire-rated floor/ceiling assemblies. | Provide a minimum 2-hr firerated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 3 months F-4 | Corrected
Initial Inspection |  | 20 | Buildings connected by raised walkways. | Provide a minimum 2-hr firerated construction between building and another building. |  | Feb 28 2015 | On 23/08/2017: Corrected On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 21 | Unprotected openings are located in the 3rd and 4th floors between the building and utility building. | Provide a minimum 2-hr firerated construction between building and another building. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Refer to issue 51. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 22 | Areas used for combustible storage in ground, 1st and 2nd floors are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. |  | Feb 28 2015 | On 23/04/2017: In progress. Factory is working on this issue. On 23/08/2017: It is found same as before. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 23 | Exit capacity and number in 4th floor are not adequate for the occupant load. The occupant load for 4th floor is 600 persons, however this exceeds the egress capacity provided which is 353 persons. | Reduce occupant load to not more than available exit capacity and Provide additional exits in the future to increase capacity. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 24 | Egress doors / gates with locking features are provided at building exits and exit stairs All gates/doors were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Refer to issue no. 59. On 02/04/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 25 | Storage was located in the exit stairs. | Remove all storage from exit stairs and egress paths. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Refer to issue no. 74. On 02/04/2024: Refer to issue no. 74. | Immediate | Corrected
Initial Inspection |  | 26 | Collapsible gates / sliding doors are provided at building exits and exit stairs | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 30 2014 | On 23/04/2017: Corrected. On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Refer to issue no. 59. On 02/04/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 27 | The SW exit stairs discharge inside the building. | Modify stair to discharge directly outside or Provide 2-hr fire-rated exit passageway leading direclty outside (vestibules to separate any storage areas) or Provide sprinkler protection for discharge floor in accordance with NFPA 13. |  | Apr 30 2016 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 60. On 02/04/2024: Refer to issue 60. | Within 6 months | Corrected
Initial Inspection |  | 28 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected as per previous follow up. Installation shall be as per NFPA 72. On 31/01/2018: Corrected, during inspection the system found functional. On 27/06/2018: Factory need to re-orient the installed fire alarm & detection system at the accessories building. Several places were not under the detection system. Moreover, detector coverage and spacing was not maintained. Interfacing of fire doors, elevator & exhaust fan with the FACP was not observed. On 17/02/2019: Refer to issue 58. On 02/04/2024: Refer to issue 58. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 29 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 30 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove the single-station smoke alarms. Provided automatic smoke detectors throughout the building in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 60. On 02/04/2024: Refer to issue 60. | Within 6 months | Corrected
Initial Inspection |  | 31 | Manual on-off switches in several locations are provided for emergency lighting / exit signage units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 32 | Exit sign not provided at the southwest exits. | Provide exit signs above all exits to the exterior and all doors to the exit stairs. |  | Dec 30 2014 | On 23/04/2017: Corrected. On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 33 | Hazardous materials / flammable liquid storage area in the ground floor and ground is not separated by fire-rated construction (openings, non-rated doors, penetrations). | Separate the hazardous materials / flammable liquid storage room by a minimum 2- hr fire-rated construction. Seal and or protected all openings to maintain the required fire separations. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 54. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 34 | The boiler, generator and transformer rooms are not separated by fire-rated construction (openings, non-rated doors, penetrations). | Separate the boiler, generator and transformer rooms by a minimum 2-hr fire-rated construction. Seal and or protected all openings to maintain the required fire separations |  | Feb 28 2015 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 35 | Areas used for combustible storage in the 2nd floor are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. |  | Feb 28 2015 | On 23/08/2017: Corrected On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 36 | The exit stairs are not separated from work areas or other spaces on each floor by firerated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. |  | Feb 28 2015 | On 23/08/2017: In progress. Installation of fire rated door has been almost completed. Interfacing shall be as per NFPA 72. On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Refer to issue no. 61. On 02/04/2024: Refer to issue no. 61. | Within 3 months | Corrected
Initial Inspection |  | 37 | The compressor room in ground floor is not separated by fire-rated construction (openings, non-rated doors, penetrations). | Separate the compressor room by a minimum 2-hr firerated construction. Seal and or protected all openings to maintain the required fire separations |  | Feb 29 2016 | On 23/08/2017: In progress. On 31/01/2018: Work is going on. On 27/06/2018: In progress. On 17/02/2019: Corrected. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 38 | Storage rooms used for combustible storage in the 1st and 2nd floors are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. |  | Feb 29 2016 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 39 | Egress doors / gates with locking features are provided at building exits and exit stairs. All gates/doors were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 59. On 02/04/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 40 | Storage was located in the north exit stairs. | Remove all storage from exit stairs and egress paths. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Refer to issue no. 74. On 02/04/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 41 | Collapsible gates / sliding doors are provided at building exits and exit stairs | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Dec 30 2014 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 59. On 02/04/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 42 | Exit stair door / egress door serving 50 or more occupants in the 2nd floor does not swing in the direction of egress travel. | Modify the egress door to swing in the direction of egress travel. |  | Feb 29 2016 | On 23/08/2017: Corrected On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 43 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. |  | Feb 29 2016 | On 23/04/2017: Corrected as per T&Cx. On 23/08/2017: Corrected as per previous follow up. Note : Installation shall be as per NFPA 72. On 31/01/2018: Corrected as per last follow ups. Modifications were ongoing. On 27/06/2018: Factory need to re-orient the installed fire alarm & detection system at the utility building. Several places were not under the detection system. Moreover, detector coverage and spacing was not maintained. Interfacing of fire doors, elevator & exhaust fan with the FACP was not observed. On 17/02/2019: Refer to issue 58. On 02/04/2024: Refer to issue 58. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 44 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 45 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove the single-station smoke alarms. Provided automatic smoke detectors throughout the building in accordance with NFPA 72. |  | Feb 29 2016 | On 23/08/2017: Corrected On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Refer to issue 58. On 02/04/2024: Refer to issue 58. | Within 6 months | Corrected
Initial Inspection |  | 46 | Manual on-off switches in several locations are provided for emergency lighting / exit signage units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. |  | Dec 30 2014 | On 23/08/2017: Corrected On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. Removed. On 02/04/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 47 | Exit sign not provided at the 2nd floor exit. | Provide exit signs above all exits to the exterior and all doors to the exit stairs. |  | Feb 28 2015 | On 23/04/2017: Corrected. On 23/08/2017: Corrected On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. Provided. On 02/04/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 48 | New Findings: The existing high-rise building with an occupiable floor greater than 23 m (75 ft) above the finished grade is not protected with an approved automatic sprinkler system. The large occupant loads, heavy fuel loading, and anticipated extended | Provide automatic sprinkler protection throught the building in accordance with NFPA 13. | Sprinkler & Fire Hydrant System installation work has been done as per review drawing. Now, Sprinkler & Fire Hydrant System ready for full T&C. Beside,we already submited revise Pre-T&C documents to RSC on 06-10-2025. | Apr 30 2016 | On 27/06/2018: T&C observation is incorporated below: Battery trouble was present for the diesel engine fire pump. Operation of fire pump initiates Fire alarm instead of supervisory signal. Flow Meter was present outside the pump room & was not in proper test mood. Diesel tank was undersized. Auto re-fil for fire reservoir shares the domestic supply line. Dedicated water supply for fire fighting shall have to ensure. Fire pump room not separated from the adjacent occupancies. At the store room on 1st & 10th Floor, sprinkler head with K-5.6 has been used instead of K-8. Old hydrant system is still present. I/O module for ZCV was not identified & at several places address of ZCV did not match with the as-built drawing. All the required modification work shall have to be completed as per NFPA-13, 20 & 72. On 17/02/2019: T&C observations (not limited to): Incomplete certification documentation, anti-vortex plate missing, no pump performance test report was found, only pump run is interfaced, no drainage and ventilation in pump room, concentric reducer is used, distance between pump flange and elbow/tee flange is less than 10 diameter of pipe, pressure setting is not proper, negative pressure exceed limit at pump suction side, excessive water leakage from delivery NRV and gaskets, OS&Y valve in Class-I landing valves not electrically supervised, Class-I hose valve has no coupling, sprinkler head is missing at several required locations, coverage area not meet standard at some areas and rooms, sprinkler head spacing is not correct at several locations, head missing under some suspended ceiling areas, hose valve caps were missing. All the deficiencies shall be remediated as soon as possible as per NFPA 13, 14, 20 and 22 prior to acceptance test again. On 02/07/2019: Not Approved. See the T&C report for details. On 05/Sep/2021: The electrical pump is found out of order. Reportedly all installation work is completed but electrical pump is malfunctioning since 4/5 days. On 14/11/2022: During follow up inspection it was observed that automatic sprinkler system modification work is in progress. On 02/04/2024: Progress has been found. Modification work has been found on going based on newly reviewed drawing of SUPS and reportedly factory will complete the modification work by 30-Jul-2024. Factory shall apply for Full T&CVI immediately after completion of installation work. RPO Comments: On 13-Jan-2026: the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Design within 3 months and install within 9 months | In Progress
Follow Up Inspection |  | 49 | 'New Finding'' Handrails are not provided on both sides of the exit stairs and ramps. | Provide handrails on both sides of the exit stairs and ramps. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | The work has been done as per RSC guideline. We have already removed the sutter door from the exit enclosure (Main building, Stair-1 in Ground floor) (The issue has been corrected) | Feb 29 2016 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. Provided. On 02/04/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 50 | New Finding(3rd Follow-up): Elevator is situated inside the production area without fire rated separation Location: Utility Building. | Provide 2 hours fire rated separation to separate the elevator lift from production area. | he work has been done as per RSC review drawing. We have already submitted pre-T&C documents to RSC on 28-03-25 (The issue has been corrected) | Aug 9 2016 | On 23/08/2017: Corrected as per previous follow up. On 31/01/2018: Corrected as per last follow ups. During inspection modification work found ongoing for the building. On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 51 | New Finding (4th follow up): Dining room is not separated with storage area. | Remove storage or Provide 1 hr. fire separation of dining room with other occupancy. | We have already completed all fire doors interface with FACP and ensure with door closer and push as per RSC guideline. (The issue has been corrected) | Dec 16 2016 | On 27/06/2018: It was found same as it was before. On 17/02/2019: Main building dining has been separated from storage however separated dining discharge occupants inside the storage (egress through storage). Additionally utility building dining floor has no separation or partition from accessories building storage floor (door, windows and connection bridge). On 05/Sep/2021: Main building and utility building dining has been separated from storage areas/floors however separated dining of both buildings discharge the occupants inside the adjacent storage (egress through storage). Additionally connection bridge is used as egress which is non-rated where rated is required to separate/protect the bridge from lower floor. On 14/11/2022: Dining areas are not separated from the boiler exhaust on 3rd floor in utility building. Dining areas south-middle (stair-7) discharge through storage areas on 10th floor main (knitting) building. On 02/04/2024: Corrected as per site condition. Setting arrangement has been found reduced to less than 300 person. | Within 2 months | Corrected
Follow Up Inspection |  | 52 | (NEW FINDING(5th Follow up):Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Feb 16 2017 | On 23/08/2017: Corrected On 31/01/2018: Corrected On 27/06/2018: Corrected as per previous follow-up. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 53 | New Finding: Inspection, test & maintenance of the exit sign & emergency lighting system has not been done on regular basis. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Jan 30 2017 | On 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Corrected based on previous follow ups. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 54 | New Finding (On 23/04/2017): Hazardous materials/flammable liquid storage area in the ground floor and ground is not separated by fire-rated construction. | Separate the hazardous materials/flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and or protected all openings to maintain the required fire separations. | The work has been done as per RSC review drawing. We have already submitted pre-T&C documents to RSC on 28-03-25 (The issue has been corrected) | May 23 2017 | 23/08/2017: Corrected. On 31/01/2018: Corrected On 27/06/2018: Corrected. On 17/02/2019: Re-opened. Non-rated diesel storage container and storage room is present in front of utility building and not fire separated. On 05/Sep/2021: Removed. Not found. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 55 | New Finding (On 23/04/2017): The exit discharge path is less than 10 ft wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. | The design philosophy and the documents already reviewed by RSC on 12-05-25, no structural fire protection is required for the chemical distribution room (as per BNBC 2020 and also based on limited storage of Chemicals). (The issue has been corrected) | May 23 2017 | On 23/08/2017: In progress. On 31/01/2018: Modified and now measured 9 ft 7 inch, which is considered corrected based on site observation. On 27/06/2018: Corrected as per previous follow-up. Note: Discharge path width shall not be obstructed which decrease the width of discharge path. On 17/02/2019: Corrected based on previous follow ups. However some window opening still present and shall be sealed. On 14/11/2022: Corrected as per previous follow up. On 02/04/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 56 | New Finding (On 23/04/2017): Unsealed penetrations and openings on several floors are located in the fire-rated floor/ceiling assemblies. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | We are working on fire rated sealan modification work as per RSC Engineer guideline & base on UL design of Dry Process building & main building. | May 23 2017 | On 23/08/2017: Partially corrected. Work shall be completed as per ACCORD standard. On 31/01/2018: Partially Corrected. Modification work going on. On 27/06/2018: Not corrected. Factory shall separate the lifts (newly constructed) located inside floor area. On 17/02/2019: New lift has been separated. However basement ceiling has non-rated construction on N-W corner of main building. Also non-rated boiler chimney penetrates all floor of utility building. On 05/Sep/2021: Fire rated construction has been provided at basement ceiling on N-W corner of main building. Fire rated shaft has been provided for 2 boiler chimnies among 5 chimnies at utility building. On 14/11/2022: Fire rated shaft has not been provided for boiler chimnies at utility building. On 02/04/2024: Corrected as per site condition. Connecting bridge containing boiler chimneys were found separated by fire rated construction and with rated shaft construction. | Within 1 month | Corrected
Follow Up Inspection |  | 57 | New Finding (10th Follow Up): Unsealed penetrations and openings are located in exit stair enclosure (Main building, Stair-1 in Ground floor & window opening in utility building) | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | The work has been done as per RSC guideline. We have already removed the sutter door from the exit enclosure (Main building, Stair-1 in Ground floor) (The issue has been corrected) | Jul 27 2018 | On 27/06/2018: New Finding On 17/02/2019: N-E stair is not properly separated from accessories building window opening on ground floor of main building. Main building stair-8 is not protected from sanitary shaft opening. Electrical cable riser/raceway penetrates almost all stair enclosures on ground floor of main building which is not permitted. SBD installed by penetrating stairwell of accessories building. On 05/Sep/2021: N-E stair is not properly separated from accessories building window opening on ground floor of main building. Cable (electrical/optical) riser/raceway penetrates several stair enclosures on ground floor of main building which is not permitted. On 14/11/2022: The factory has installed shutter (listed according to the factory personnel) in the North-East exit stair and interfaced with the FADS (reportedly) to separate from the accessories building openings and egress path on the ground floor but supporting documents were not available on-site during follow up inspection. However, during follow up inspection fire alarm and detection system (FADS) was found in abnormal condition. On 02/04/2024: Progress has been found but not corrected yet. Fire rated shutter door has been found installed but factory shall ensure the integrity of the fire rated shutter through proper datasheet, certificate and testing report of all assembly. RPO Comments: On 2-Nov-2025 the factory management has reported remediation completion and the issue will be verified during the next follow up inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 58 | New Finding: Installed fire alarm and detection system does not comply with NFPA 72. Alarm signal is not temporal three type, low audibility, MCP not working/responding, detector coverage not to standard, MCP is in stair and more than 5ft in floors, battery calculation and as-built design not up to date, trouble/pre-alarm exist in FACP. | Fire alarm and detection system shall confirm compliant to NFPA 72. After re-configuring the system notify the Accord for a testing and commissioning verification inspection. | Fire alarm and detection system installation work has been done as per review drawing. Now, Fire alarm and detection system ready for full T&C. Beside,we already submited revise Pre-T&C documents to RSC on 06-10-2025. | Apr 17 2019 | On 05/Sep/2021: reportedly modification is completed however system is found unhealthy condition with lots of trouble/pre alarm/supervisory in FACP and repeater panels. On 14/11/2022: During follow up inspection fire alarm and detection system (FADS) was found in abnormal condition. Modification work is in progress according to the factory personnel. On 02/04/2024: Progress has been found. Modification work has been found on going based on newly reviewed drawing of FADS. After completion of the modification work factory needs to apply for Full T&CVI. RPO Comments: On 13-Jan-2026: the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Within 2 months | In Progress
Follow Up Inspection |  | 59 | New Finding: Non-compliant collapsible gate at main building office portion and sliding gate present at utility building stair discharge on ground floor. | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | We have already completed unsealed penetratio work by fire rated construction & fire door of connecting bridge & Electrical cable. (The issue has been corrected) | Feb 20 2019 | On 05/Sep/2021: removed. Not found. On 14/11/2022: Issue re-open. During follow up inspection non-compliant exit doors/gates (sliding door) with locking features are found at the South-Middle exit (exit stair-7) on the ground floor of Main Building-1 and at the North-East exit door/gates on the ground floor of the Accessories building. Non-compliant locking features are found at the North-West exit (stair-1) on the ground floor of the R&D building. All doors were open and unlocked during the inspection. On 02/04/2024: Corrected as per site condition. | Immediate | Corrected
Follow Up Inspection |  | 60 | New Finding: Front exit stairs of accessories building and utility building is discharge the occupants inside the building. Both building has extended canopy made by steel construction and non-separated utilities, offices and building openings present there. | 1. Modify stair to discharge directly outside. Or 2. Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). Or 3. Provide sprinkler protection for discharge floor in accordance with NFPA 13. | We have already completed all the unsealed penetration work due to electrical cables and BBT. (The issue has been corrected) | Apr 17 2019 | On 05/Sep/2021: Found almost same as before. N-E exit of main building also discharge the occupant under the extended canopy. On 14/11/2022: Still front exit stair (North-East) of accessories building, North-West of utility building and West-North (exit Stair-2) of main building discharge inside the building on the ground floor. On 02/04/2024: Issue has been corrected on Main building, accessories and utility building as per site condition. | Within 2 months | Corrected
Follow Up Inspection |  | 61 | New Finding: Some fire doors are not interfaced with FACP and some fire doors has narrower leaf interfaced with FACP without door closer and push bar. | Re-configure fire door installation and interfacing with FACP thus it satisfy standard as well as fire separation integrity. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Mar 17 2019 | On 05/Sep/2021: Corrected. On 14/11/2022: During follow up inspection it was observed that installed fire doors with door accessories (door co-ordinator for double leaf door, panic bar, door closer, etc.) were not functional properly at exit on several floors of all buildings. Factory management confirms that they will keep re-entry provision and post re-entry at required location in accordance with the RSC Technical Guidelines (StandardV1.0) 6.8.3. On 02/04/2024: Progress has been observed but not corrected yet. Re entry provision has been provided but hardware of the fire rated door has been found non functional on several locations and some cases magnetic door holder has not been interfaced with FADS [ 10th Floor of Main Building]. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 62 | New Finding: Building expansion joint opening is not protected by fire rated material. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated sealant to seal the expansion joint openings from each floor. | We are working to replace hardware and accessories that are not functional or under unauthorized maintenance. | Apr 17 2019 | On 05/Sep/2021: Reportedly listed material is used to seal the joint however product sample/packaging/drum is not provided to check UL certification mark and classification mark on the product also application is not as per UL certified design. On 14/11/2022: Corrected based on the provided certificate and site observations. On 02/04/2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 63 | New Finding: Non-rated exhaust duct penetration located within separated chemical storage at ground floor. | Re-route the exhaust duct and seal all penetrations and openings in the fire rated separation walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Apr 17 2019 | On 05/Sep/2021: Corrected. On 14/11/2022: Corrected. On 02/04/2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 64 | New Finding: Utility building dining floor exit capacity is not adequate for the occupant load. Dining capacity more than 500 and provided with only 2 exit. | 1. Reduce occupant load to not more than available exit capacity as per Accord 6.5.4 and 6.6.3. Or 2. Provide additional exits to increase exit capacity as per Accord 6.5.4 and 6.6.3. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Mar 17 2019 | On 05/Sep/2021: Additional 2 exit is provided for the utility building dining. See issue 51 for access to stair/egress discharge feature. On 14/11/2022: Issue re-open. Dining capacity (sitting arrangement) was found 1400 (provided only 3 exit stair) on 10th floor in main building and 880 (provided 2 exit stair) on 3rd floor in utility building which is not complied RSC Technical Guidelines (StandardV1.0) section 6.6.3. As per existing exit stair maximum occupant load dining area is 1000 for main building on 10th floor and 334 for utility building on 3rd floor. On 02/04/2024: Progress has been observed but not corrected yet. Issue has been corrected for Utility building, but not corrected on Main Building. However 4 no's of exit serves the dinning area but due to non functional hardware of Fire Rated Doors, direct exits are not properly separated from storage area. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 65 | New Finding (12th follow up): The exit stairs are not separated from work areas, other spaces on each floor by fire-rated construction. (Location: Dry process and R&D building. Fire doors are provided however door hardware missing/not working and unprotected opening/penetration observed.) | Stair shall be enclosed with a minimum 1-hr fire-rated construction. Seal all unprotected openings and provide minimum 1-hr fire rated doors to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing, positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Nov 13 2021 | On 13/Sep/2021: Both buildings are added in the scope of fire safety follow-up inspection. On 14/11/2022: During follow up inspection it was observed that installed fire doors with door accessories (door co-ordinator for double leaf door, panic bar, door closer, etc.) were not functional properly at exit on several floors in dry process and R&D building. On 02/04/2024: Progress has been observed, some unseale penetrations have been found on stair enclosure. Hardware of Fire Rated Doors have been found functional. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 66 | New Finding (12th follow up): Existing 3 story non-rated building (dry process building) having floor area more than 2000 sqm (22000 sft) is required to be protected with an approved automatic sprinkler system where sprinkler installation is going on. Automatic sprinkler system installation requires detailed review to confirm compliance with NFPA 20 and ACCORD standards. | Install an automatic sprinkler protection throughout the building in accordance with NFPA 13. Before that, Submit the drawings, equipment certification and other relevant documentation to the RSC for review and approval. | Sprinkler & Fire Hydrant System installation work has been done as per review drawing. Now, Sprinkler & Fire Hydrant System ready for full T&C. Beside,we already submited revise Pre-T&C documents to RSC on 06-10-2025. | Jan 13 2022 | On 14/11/2022: The factory has installed fire alarm and detection system (FADS) but during follow up inspection fire alarm control panel (FACP) was found in abnormal condition. RPO Comments: On 13-Jan-2026: the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Design within 1 months, install within 3 months | In Progress
Follow Up Inspection |  | 67 | New Finding (12th follow up): The water pump room is located within the exit stair enclosure at dry process building and not provided with adequate fire separation from the stair. | Separate the water pump room by minimum 1-hr fire-rated construction. If factory wants to provide pump room exit within the exit stair then vestibule shall be provided. If required, provide a 1 hr fire rated door on the exit stair side and a 1-hr fire rated door on the water pump room side. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure. | The design philosophy and the documents already reviewed by RSC on 12-05-25, no structural fire protection is required for the chemical distribution room (as per BNBC 2020 and also based on limited storage of Chemicals). (The issue has been corrected) | Nov 13 2021 | On 14/11/2022: Corrected. The factory has installed fire door at pump room exit. On 02/04/2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 68 | New Finding (12th follow up): Chemical storage is not separated by fire-rated construction having rated door and unsealed penetrations and openings. (Location: Both building, non-rated construction). | Ensure that the chemical room is located within a Type-1 construction and separate the chemical storage room by 2-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. Keep 16-points MSDS of all chemicals in the storage area. As per BNBC, chemical storage room shall be Type-1 construction. | Chemical store seperation work has been done as per RSC engineer guideline. (The issue has been corrected) | Nov 13 2021 | On 14/11/2022: During follow up inspection it was observed that installed fire doors with door accessories (door co-ordinator for double leaf door, panic bar, door closer, etc.) were not functional properly at exit in chemical room. However, chemical room was not in Type-1 construction. On 02/04/2024: Progress has been observed. Dry process building: Chemical distribution store is separated by fire rated constructions and doors from building interior but, type-1 construction was not done yet. The factory has submitted the passive fire protection proposed drawings for the chemical storerooms to RSC and the drawings are under review. Main building (ground floor): Not corrected yet due to non-functional hardware of the fire rated doors. RPO Comments: On 2-Nov-2025 the factory management has reported remediation completion and the issue will be verified during the next follow up inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 69 | New Finding (12th follow up): Clear headroom in the means of egress (exit stair) is less than 2.03 m (6 ft 8 in.) at dry process building S-E exit. | Increase the headroom in the means of egress in accordance with Accord standard 6.3.3. | The work has been done as per RSC review drawing. We have already submitted pre-T&C documents to RSC on 28-03-25 (The issue has been corrected) | Nov 13 2021 | On 14/11/2022: During follow up inspection some exit door height was found 6ft 6 inch which is below as per standard. On 02/04/2024: Corrected as per site condition. Height of the Head room has been found 6'-8". | Within 2 months | Corrected
Follow Up Inspection |  | 70 | New Finding (12th follow up): Building expansion joint opening is provided with fire rated material however manufacturer and listing body guideline and design method is not maintained. Location: Dry process building. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated sealant to seal the expansion joint openings from each floor in accordance with manufacturer and listing body guideline. | The expansion joint work has been completed. Now we are waiting for a meeting with RSC to properly resolve the expansion joint work. | Nov 13 2021 | On 14/11/2022: Building expansion joint certificate for the steel structure building was not available on-site during installation. On 02/04/2024: Progress has been observed but not corrected yet. Dry Process building: Factory has been installed fire rated sealant material on 1st floor and on 2nd floor installation is not completed. Installation has not been done as per UL design on both Dry Process and Main Building. The factory needs to compete the sealing work by listed materials or rated constructions. RPO Comments: On 2-Nov-2025 the factory management has reported remediation completion and the issue will be verified during the next follow up inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 71 | New Finding (12th follow up): Dining facility with seating arrangement of 700 person is provided at R&D building 2nd floor with cutting section. | Mixed occupancy of E3 and G2 is not permitted as per Table-3.2.1, BNBC 2006. E3 - Large assembly without fixed seat (accommodation for more than 300 persons) and G2 - Moderate hazard industries. Remove any one occupancy from 2nd floor. Or Modify the seating arrangement to reduce the accommodation to less than 300 person to have E4 occupancy and separate the E4-small assembly occupancy without fixed seat (accommodation for less than 300 persons) by a minimum 3-hr fire rated construction having two (2) direct access to exit stair/outside of the building. Seal and/or protect all openings to maintain the required fire separations. | We have already completed unsealed penetratio work by fire rated construction & fire door of connecting bridge & Electrical cable. (The issue has been corrected) | Oct 13 2021 | On 14/11/2022: Not corrected. The factory has created an extra exit from the dining areas which work is in progress. On 02/04/2024: Corrected as per site condition. Setting arrangement has been found reduced to less than 300 person. | Within 1 month | Corrected
Follow Up Inspection |  | 72 | New Finding (12th follow up): Exit capacity is not adequate for the occupant load. Location: 1st and 2nd floor at R&D building. All floor of the building is provided with 2 exit, available capacity is 500 at ground floor and 368 at other floors. Available occupant load is 50+dining seating arrangement of 700 person at 2nd floor, 421 at 1st floor and 315 at ground floor. | Reduce occupant load within given timeline to not more than available exit capacity. Provide additional exits in the future to increase exit capacity. | We have already completed all the unsealed penetration work due to electrical cables and BBT. (The issue has been corrected) | Oct 13 2021 | On 14/11/2022: Corrected. The factory has reduced occupant load. On 02/04/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 73 | New Finding (12th follow up): The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards. Location: Both building. | Replace the fire alarm system with a new, listed automatic addressable fire alarm system in accordance with NFPA 72 and ACCORD standards. | Fire alarm and detection system installation work has been done as per review drawing. Now, Fire alarm and detection system ready for full T&C. Beside,we already submited revise Pre-T&C documents to RSC on 06-10-2025. | Jan 13 2022 | On 14/11/2022: The factory has installed fire alarm and detection system (FADS) but during follow up inspection fire alarm control panel (FACP) was found in abnormal condition. On 02/04/2024: Progress has been found. Modification work has been found on going based on newly reviewed drawing of FADS. After completion of the modification work factory needs to apply for Full T&CVI. RPO Comments: On 13-Jan-2026: the T&CVI documents are currently under RSC’s review. Once the factory becomes ready for the Pre-T&CVI then the CAP status will be changed to pending verification. | Design within 1 month, install within 3 months | In Progress
Follow Up Inspection |  | 74 | New Finding (On 14/11/2022): During follow up inspection storages/obstacles were observed in all building's exit stair enclosures and on aisles on several floors. Storages were observed on the ground floor south and east egress path of the Main building and the west egress path of the accessories building. | Remove all storage from exit stairs and egress paths. | We are working to replace hardware and accessories that are not functional or under unauthorized maintenance. | Nov 16 2022 | On 14/11/2022: New Finding On 02/04/2024: Corrected as per site condition. Stair enclosure has been found free from storage. | Immediately | Corrected
Follow Up Inspection |  | 75 | New Finding (14th FUI): Top of elevator shaft is not separate from the production floor.on the 2nd floor and elevator opens into the inside of exit enclosure. Location: Elevator on stair- I of dry process building. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Jun 16 2024 | On 02/04/2024: New Finding. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 76 | New Finding (14th FUI): Unsealed penetrations and openings are located.in the firerated floor/ceiling assemblies due to non-rated-connecting bridge of Accessories Building. Also, Electrical cable riser passes through rated walls on several floors of the Accessories Building and Dry Process Building. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Jun 16 2024 | On 02/04/2024: New Finding. RPO Comments: On 25-05-2025: The facotry reported remediation completion. It will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 77 | New Finding (14th FUI): Several unsealed penetrations were found in between the separation walls of Accessories Building to Utility Building due to electrical cable and BBT. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's datasheet. Or Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | We have already completed all the unsealed penetration work due to electrical cables and BBT. (The issue has been corrected) | Jun 16 2024 | On 02/04/2024: New Finding. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 78 | New Finding (14th FUI): Manual on-off switch is provided for emergency lighting I exit signage units. | Remove manual on/off switches from [emergency lighting /exit signage] units to prevent them from being switched off | The work has been done as per RSC engineer guideline. (The issue has been corrected) | May 16 2024 | On 02/04/2024: New Finding. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 79 | New Finding (14th FUI): Fire rated door hardware has been found under unauthorized maintenance (Welding) and somceses damaged (Leaf) so that required separation has not been ensured. Location: Main Building. | Factory shall ensure that the maintenance work shall be done for the door hardware and accessories on a regular basis as per NFPA 80 [Ch-5] and manufacturer's published guideline. Repair/ replace the hardware and accessories which are not functional or under unauthorized maintenance. Doors shall not be tied up with rope or blocked by obstacles. Keep the fire rated doors close all time, if for functional reason require to keep open then interfacing facility with functional FACP shall be ensured. | We are working to replace hardware and accessories that are not functional or under unauthorized maintenance. | May 16 2024 | On 02/04/2024: New Finding. RPO Comments on 13-Jan-2026 the factory management has not reported remediation completion and the issue needs to be remediated. | Within 1 month | In Progress
Follow Up Inspection |  | 80 | New Finding (14th FUI): Lift shaft has been found not separated due to non functional fire rated door. Location: Main Building. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Jun 16 2024 | On 02/04/2024: New Finding. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 81 | New Finding (14th FUI): In process storage has been found not within the limit. Location: 2nd floor of Main Building and Washing Building. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | The work has been done as per RSC engineer guideline. (The issue has been corrected) | Jun 16 2024 | On 02/04/2024: New Finding. RPO Comments: On 01-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification

## Electrical
Date
01-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD., 14 No. Genda, Karnopara, Ulail, Savar, Dhaka, Dhaka
Date of Inspection |  | 2014-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Cables not supported (and not protected). | Cables used in factory must be supported in trays or ladders throughout its whole length. Provide cover of metal sheet to the tray to prevent any physical damage. | Cables have already been made supported. | Mar 31 2015 | Already verified on previous follow up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 2 | Cables partially supported in tray and raceways (cables are not placed inside tray in few sections). | Cables supported in tray must be securely laid in the tray and tied with using cable tie at a regular interval. Provide cover of metal sheet to the tray to prevent any physical damage. | Cables are fully supported. | Sep 2 2014 | Already verified on previous follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 3 | Panel not readily accessible. | Existing panel installed above readily reachable heights. Top end of the panel may be at 2 meter from the floor level. | 3 step stairs install in front of every panel all panels are in accessible. | Sep 2 2014 | On 13/02/2015: Corrected at 1st follow up. On 09/05/2016: This issue is not corrected, because there are still some MCCB panels which are inaccessible. On 28/07/2016: Corrected. | 3 Months | Corrected
Initial Inspection |  | 4 | Gland holes in cable base plates left open. | Compression glands may be used to fix existing cables to the base plates or cable gland may be used according to the respective cable. | Gap has been closed between cable and glands. | Sep 2 2014 | Already verified on previous follow up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 5 | Openings in the panel top cover plate. | Make circular hole at the base plate/top plate of panels and provide cable gland according to the respective cable size for cable entry an exit so that the cables are not stressed on the sharp edges of the hole of panels. | Upper cover of panel is enclosed | Sep 2 2014 | Already verified on previous follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 6 | Panel base plates removed to allow cable entry. | Make circular hole at the base plate/top plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. | all panels are covered and vermin proof (done). | Sep 2 2014 | On 13/02/2015: Corrected at 1st follow up. On 09/05/2016: This issue is not corrected, because there are still some panels which have no base plate. On 28/07/2016: Corrected. | Within 1 Month | Corrected
Initial Inspection |  | 7 | Wire terminating to MCBs inside panel are looped. | MCB input connection loop may be established by standard plug-in busbar or separate cable may be used for each load. Phase separators must be installed between different MCBs grouped by phase it is connected. | Cable of MCB are not looped inside the panel. | Sep 2 2014 | Already verified on previous follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 8 | Multiple wires installed in single lug/terminal. | Individual circuit breaker must be used for protecting each circuit. If the cables are from same circuit, a bigger size cable may be used. | Single cables entering into a single connector of MCCB. | Sep 2 2014 | Already verified on previous follow up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 9 | Panel doors not connected with earth bond. | Existing panel door bonding by PVC insulated wires may be replaced with bonding-braid as most of them (installed wires) are loosen due to repeated opening and closing of door. | Door of panel board adding earth bonding. | Sep 2 2014 | Already verified on previous follow up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 10 | Cables are laid on concrete floor. | Cables on floor may be supported into covered cable trays installed at safe locations to prevent any physical damages. | Cables from panel are not laid on floor. Used cable tray for supported. | Sep 2 2014 | Already verified on previous follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 11 | Combustible materials are kept near to power cables. | Combustible materials near power cables must be removed. | Combustible cloths clear from near the power cable. | Sep 2 2014 | Already verified on previous follow up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 12 | Flexible PVC conduit wiring not supported. | Flexible PVC conduit wiring must be additionally supported on cable tray and risers. | Flexible PVC cable drawn with supported by cable tray. | Sep 2 2014 | Already verified on previous follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 13 | Cables joint with tape inside the panel. | PVC connector and PIB tape wound around the joint must be provided for every cable-joint. | No electrical cable here. | Sep 2 2014 | Already verified on previous follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 14 | Cables supported on trays or/and raceways are not securely fixed. | Cables supported in cable trays must be firmly tied to the tray using cable-tie at regular intervals. Provide cover made of metal sheet onto the tray. | Wires not exposed while cable transiting in cable tray | Sep 2 2014 | Already verified on previous follow up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 15 | Main cable electrical room to other building is partially supported in trays and/or raceways. | Cables on trays/raceways/ risers must be supported throughout its length. Cable accessories including junctions, tee, drops and risers must be installed to support cables throughout length. | Flexible PVC cable drawn from roof with supported cable tray. | Sep 2 2014 | Already verified on previous follow up inspection. | Within 1 Month | Corrected
Follow Up Inspection |  | 16 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend electrical SLD properly. Mention all the modification there as present in the factory and review it by ACCORD. | SLD is reviewed by ACCORD. | Feb 29 2016 | On 17/01/2016: Drawing is available but inadequate information. New committed timeline is given till 29-02-2016. On 09/05/2016: This issue is still not corrected yet. The factory is behind schedule. On 28/07/2016: Not corrected. SLD need few modifications. On 16/11/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Thermal inspection record is unavailable. | Thermal inspection is needed to be conducted and recorded bi-annually. Record/ask for the calibration certificate of the scanner. | Done. | Jun 10 2016 | On 17/01/2016: This issue was verified in 2nd follow-up inspection. On 09/05/2016: This issue is not corrected. New committed timeline has given till 10-06-2016. On 28/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding Insulation resistance test of electrical equipment is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Done | Mar 13 2016 | Already verified on previous follow up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: Earth pit resistance record is unavailable. | Record earth pit resistance for all the earth pit and do once in a year. | The test has been done and the report does cover all panels. | Mar 13 2015 | Already verified on previous follow up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Lightning Protection System (LPS) has not installed yet. | Design and install LPS for your factory by following BNBC/ NFPA. | Earth pit resistance for all earth pit has been recorded. | Jun 10 2016 | On 09/05/2016: This issue is not corrected yet but they have drawing and installation pending. New committed timeline has given till 10-06-2016. On 28/07/2016: Not corrected. On 16/11/2016: Not corrected. On 24/01/2017: Not corrected. On 23/04/2017: Not corrected. LPS of the main building is installed properly. On 23/08/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Light in store room/storage areas is uncovered. | Lights in store room/storage areas shall be covered. | Done | Mar 27 2016 | Already verified on previous follow up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Higher rated circuit breakers with lower rated electrical cable. | Consult with a qualified Electrical Engineer and ensure electrical cables are sized according to capacity of circuit breakers. | Cover system lights have been installed in the storage areas. (Corrected) | Aug 30 2016 | On 28/07/2016: Not corrected. Factory committed timeline: 30/08/2016. On 16/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Cable tranches are filled with fluffs (dust and water). | Clean all the cable tranches; then seal them for permanent (you may use checkered/ perforated plate at the bottom). But ensure that you have used proper sized cable for all of your electrical loads. |  | Jun 10 2016 | On 28/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Inadequate working clearance around the generator/s. | Working clearance around each generator should be 1.07 m. If multiple generators are installed then the gap between two generators must be equal to the width of bigger generator. | Done | Jul 10 2016 | On 28/07/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Wirings in flexible PVC conduit in boiler room. | Wires close/attached to boiler and generator must be protected from external heat and moisture by metallic heat resistant conduits. If possible, keep sufficient clearance between heat sources and cable/wires. | Done | Jun 10 2016 | On 28/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Cable duct/channels are damaged and it has no cover. | Clean all the cable channels/ducts; then cover them (you may use checkered/ perforated plate at the bottom) and install end cover with proper support. After each maintenance, keep record. | All PVC flexible pipe replaced by metal flexible pipe (done). | Jul 10 2016 | On 28/07/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Lint and dust deposited on transformer top. | Keep transformer top always neat and clean. | Cable duct repaired and cleaned (done). | May 25 2016 | On 28/07/2016: Corrected. | 2 Weeks | Corrected
Follow Up Inspection |  | 28 | New Finding: Electric safety training program is not initiated. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. | Transformer top is now neat and clean (done). | Aug 30 2016 | On 28/07/2016: Not corrected. Factory shall conduct the safety training again as minor influence observed among the electrician. Factory committed timeline: 30/08/2016. On 16/11/2016: Corrected. | 2 Weeks | Corrected
Follow Up Inspection |  | 29 | New Finding: There is improper programmed schedule for periodical inspection & testing of electrical equipment available on site which reflects inadequate for the factory. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance). |  | Jun 10 2016 | On 28/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Oil leakage has been observed from transformer. | Stop oil leakage from transformer and keep clean top of transformer. | Already yearly maintenance schedule is prepared and being followed accordingly (done). | Sep 10 2016 | On 16/11/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Cables are hanging without support. Cable terminals may be in tension. | Use cable tray/ladder to support cables at any where to keep cable out of tension. | Oil leakage issue is resolved. | Oct 10 2016 | On 16/11/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 32 | New Finding: Horizontal bus bur are kept uninsulated between terminals on circuit breakers. | Power bus bar must be installed with adequate clearance (not less than 2.5 inch for LV) between two bars otherwise insulation must be provided. | Done | May 31 2017 | On 23/08/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Hot spots have been observed at some points. | Thermography survey must be done at least twice in a year. Hot spots must be removed as soon as possible. | All the cables are now supported by the cable tray (done). | Sep 10 2017 | On 31/01/2018: Corrected. No such issue was found during inspection. | 2 Weeks | Corrected
Follow Up Inspection |  | 34 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Done | Sep 15 2018 | On 06/02/2019: Not corrected. On 05/09/2021: Not corrected. Factory is working on this issue. On 14/11/2022: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Panel/distribution boxes are not readily accessible. | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2 m from base; and door opening shall be at least 90 degree. | Done | Apr 25 2019 | On 05/09/2021: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCB/MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Phase, neutral & earthing cable marking is completed according to SLD. This issue has been corrected. | Mar 25 2019 | On 05/09/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Cable duct/channels are filled with fluffs (lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. |  | Mar 25 2019 | On 05/09/2021: Corrected. Cable duct have been replaced by BBT. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Non-metallic sheathed (types NM, NMC, and NMS) cables are run and exposed over the suspended ceiling. | Use the metallic sheathed cable or provide enclosed cable raceway to run the cable over the suspended ceiling. Suspended ceiling shall not be used for the cable support. |  | Mar 25 2019 | On 05/09/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. |  | Mar 25 2019 | On 05/09/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/ panels is obstacles. | At least 1 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. |  | Dec 24 2022 | On 16/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Air terminals are not installed at required height. | Factory shall design Lightning Protection System (LPS) for the whole factory (where the risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. |  | Dec 24 2022 | On 16/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. |  | Dec 24 2022 | On 16/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Field information has less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. | SLD has already been reviewed in the RSC and SLD is accepted in RSC on 05-09-2024. We have already completed modification work 100% of the as built electrical SLD work. On 24/10/2024. Corrected. | Feb 28 2023 | On 18/03/2024: Not corrected. Factory will submit SLD to RSC within 26 March 2024. RPO Comments: On 03-Dec-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 06/01/2025: Corrected. The factory got acceptance on SLD and implemented it properly. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Earth pit resistance test record doesn't match with field. | Adequate number of earth pits must be ensured (if it's lower in numbers) and record must be made accordingly. | The work has been done as per RSC guidelines (corrected). | Feb 28 2023 | On 18/03/2024: Not corrected. ER test not conducted after last follow-up. Factory is working to increase earth pit. On 06/01/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record. Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | The work has been done as per RSC guidelines (corrected). | Feb 28 2023 | On 18/03/2024: Not corrected. IR test not conducted for all cables (3 no's generator and some panels cable missing). On 06/01/2025: Corrected. IR test report include all the cables. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Thermographic survey is not performed for whole panel board (partially done on circuit breaker). | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | The Thermographic survey work has been done as per RSC guidelines (corrected). | Feb 28 2023 | On 18/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | The work has been done as per RSC guidelines. | Feb 28 2023 | On 18/03/2024: Not corrected. Some progress observed at Utility building, Dry process and R&D section. On 06/01/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Uncovered/Perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | The work has been done as per RSC guidelines. | Feb 28 2023 | On 18/03/2024: Not corrected. Some progress observed at AKM building (1st & 10th floor). On 06/01/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Power cables are laid on floor without proper protection and support. | Service/distribution cables are laid on floor shall be avoided; in unavoidable cases it must be distributed through a covered cable duct for the protection and support. | The work has been done as per RSC guidelines (corrected). | Feb 28 2023 | On 18/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Outdoor cables are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | The work has been done as per RSC guidelines (corrected). | Feb 28 2023 | On 18/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Hot spots have been observed at some points. | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | 01.Loose terminations tightened 02.Heated lugs/cables replaced where needed 03.Busbar & breaker terminals serviced 04.Re-thermal test performed and no hot spot found. The work has been done as per RSC guidelines. | Oct 30 2025 | Comments from RPO: On 2-Nov-2025 the factory management has reported remediation completion and the issue will be verified during the next follow up inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 52 | New Finding: No/oversized individual protection found where motor load more than 376 W. | Every electric motor having a rating exceeding 0.376 kW shall be provided with individual control equipment incorporating means of protection against overcurrent. | Currently, individual motor circuits are protected using fuse/circuit breaker-based overcurrent protection. The work has been done as per RSC guidelines. | Nov 30 2025 | Comments from RPO: On 2-Nov-2025 the factory management has reported remediation completion and the issue will be verified during the next follow up inspection. | 2 Months | Pending Verification

## Boiler
Date
01-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.K.M. KNIT WEAR LTD., 14 No. Genda, Karnopara, Ulail, Savar, Dhaka, Dhaka
Date of Inspection |  | 2022-04-26
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 9109 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 9110 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9900 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Sold | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 5405 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 12846 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Temporary ShutDown | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 6 | BB 12847 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 5737 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 6464 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 3583 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 9109 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | This worK will be done with in 1 months | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 11 | BB 9110 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | This worK will be done with in 1 months | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 12 | BB 9900 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Sell | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 13 | BB 5405 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | This worK will be done with in 2 months | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 14 | BB 12847 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 12846 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Temporary ShutDown | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 16 | BB 5737 | Necessary technical documents (Piping & Instrumentation diagram, commissioning documents, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 17 | BB 9900 | Necessary technical documents (Piping & Instrumentation diagram, commissioning documents, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Sell | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 18 | BB 6464 | Necessary technical documents (Piping & Instrumentation diagram, commissioning documents, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 19 | BB 12847 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have already solve this issue | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 20 | BB 9109 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have already solve this issue | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 21 | BB 9110 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have already solve this issue | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 22 | BB 5405 | Boiler Steam Header Safety Valve outlet line was not directed outside of the boiler room. | Safety Steam Header Valve outlet lines should be directed outside of the boiler room with proper support and drainage system. | We have install drain arrangement system in proper way of the safety valve. | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 23 | BB 5737 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already solve this issue | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 24 | BB 6464 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already solve this issue | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 25 | BB 3583 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 26 | BB 9109 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 27 | BB 9110 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 28 | BB 9900 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | Sell | Mar 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 29 | BB 5405 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 30 | BB 9109 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 31 | BB 9110 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 32 | BB 9900 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Sell | Feb 16 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 33 | BB 5405 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 34 | BB 12847 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 35 | BB 5737 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This worK will be done with in 2 months | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 36 | BB 6464 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This work is Completed | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 37 | BB 12847 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This work is Completed | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 38 | BB 12846 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | Temporary ShutDown | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 39 | BB 3583 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 40 | BB 5405 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 41 | BB 9109 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 42 | BB 9110 | Necessary technical documents (manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, water treatment design & calculation) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 43 | BB 12846 | Necessary technical documents (except boiler operational logbook) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Temporary ShutDown | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 44 | BB 12847 | Necessary technical documents (except boiler operational logbook) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 45 | BB 12846 | Inconsistency was observed between the nameplate data and the CIoB provided certificate copy for the boiler regarding maker's number. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | Temporary ShutDown | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 46 | BB 5405 | Boiler's initial registration certificate was not available on-site during the inspection | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | This issue will be done with in 2 Months | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 47 | BB 5737 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | We have already terminated fuel line opening with bond flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 48 | BB 13729 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 49 | BB 13729 | Steam leakage was observed in the boiler near feed tank. | The steam leakage shall be repaired to prevent burn hazard. | We already solve this issue | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 50 | BB 12848 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Temporary ShutDown | Apr 2 2026 | Comments on 24-Feb-2026: Proper documentations regarding the Dismatling/Permanent Shutdown/Temporary Shutdown/Registration cancellation/Selling should be provided by the factory management within given timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 51 | BB 13073 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 52 | BB 13073 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 53 | BB 13729 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 54 | BB 13073 | Boiler steam header safety valve outlet line was not directed outside of the boiler room. | Boiler steam header safety valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We already solve this issue. | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 55 | BB 13073 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 56 | BB 13073 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | We have already install proper steam pressure gauge(20Kg). | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 57 | BB 5737 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly on the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 58 | BB 15072 | Boiler registration number plate was not found mounted on the boiler. | Boiler registration number plate shall be made available on the boiler according to the Bangladesh Boiler Act 2022. | We already mounted Boiler registration number on the Boiler. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 59 | BB 15072 | Fuel line connection was not terminated properly | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | We have already terminated fuel line opening with bond flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 60 | BB 15072 | Drainage arrangement was not installed or installed in an inadequate manner for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per the manufacturer's published guidelines or at the lowest point of the outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 61 | BB 15072 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have already marked the low low water level Beside the gauge glass. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 62 | BB 15072 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly on the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 63 | BB 15072 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already show the Documents during internal & Hydrostatic pressure test inspection | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work status could not be assessed, as no image was provided. It shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 64 | BB 15072 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 65 | BB 6464 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 66 | BB 6464 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 67 | BB 6464 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 68 | BB 5405 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | This worK will be done with in 2 months | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 69 | BB 5405 | Steam leakage was observed in the boiler gauge glass. | The steam leakage shall be repaired to prevent burn hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 70 | BB 5737 | Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 71 | BB 5737 | Drainage arrangement was not installed or installed in an inadequate manner for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 72 | BB 5737 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 73 | BB 5737 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 74 | Non BBR-9178-1 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 75 | Non BBR-9178-2 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 76 | Non BBR-9178-3 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 77 | Non BBR-9178-4 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 78 | Non BBR-9178-5 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 79 | Non BBR-9178-6 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 80 | Non BBR-9178-7 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 81 | Non BBR-9178-8 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 82 | Non BBR-9178-9 | Necessary technical documents were not available to verify boiler design and operation parameters | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 83 | Non BBR-9178-10 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 84 | Non BBR-9178-1 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 85 | Non BBR-9178-2 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 86 | Non BBR-9178-3 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 87 | Non BBR-9178-4 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 88 | Non BBR-9178-5 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 89 | Non BBR-9178-6 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 90 | Non BBR-9178-7 | The steam pressure gauge range was insufficient | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 91 | Non BBR-9178-8 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 92 | Non BBR-9178-9 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 93 | Non BBR-9178-10 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | This work wil be done with in 1 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 94 | Non BBR-9178-1 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 95 | Non BBR-9178-2 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 96 | Non BBR-9178-3 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 97 | Non BBR-9178-4 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 98 | Non BBR-9178-5 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 99 | Non BBR-9178-6 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 100 | Non BBR-9178-7 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 101 | Non BBR-9178-8 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 102 | Non BBR-9178-9 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 103 | Non BBR-9178-10 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop Switch . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 104 | Non BBR-9178-1 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 105 | Non BBR-9178-2 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 106 | Non BBR-9178-3 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 107 | Non BBR-9178-4 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 108 | Non BBR-9178-5 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 109 | Non BBR-9178-6 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 110 | Non BBR-9178-7 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 111 | Non BBR-9178-8 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 112 | Non BBR-9178-9 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 113 | Non BBR-9178-10 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 114 | Non BBR-9178-1 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 115 | Non BBR-9178-2 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 116 | Non BBR-9178-3 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 117 | Non BBR-9178-4 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 118 | Non BBR-9178-5 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 119 | Non BBR-9178-6 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 120 | Non BBR-9178-7 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 121 | Non BBR-9178-8 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 122 | Non BBR-9178-9 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 123 | Non BBR-9178-10 | The boiler's bottom blowdown line was not safely installed and was posing a scalding hazard. | The blowdown line must be installed safely and directed either into a drain line or outside of the boiler room without creating any scalding hazard. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTHS | In Progress
Initial Inspection | External visual inspection | 124 | BB 13729 | Drainage arrangement was not installed for one safety valve. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 125 | BB 9109 | Drainage arrangement was not installed for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. | We have install drain arrangement system in proper way of the safety valve. | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 126 | BB 13729 | Inconsistency was observed between the commissioning and nameplate data and the CIoB provided certificate copy for the boiler regarding Maximum Allowable Working Pressure of the boiler. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | This worK will be done with in 2 months | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 127 | BB 15072 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | This worK will be done with in 2 months | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 128 | BB 15072 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 129 | BB 13073 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | We have protected unused & Unprotective steam line with Bond Flange. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 130 | BB 15072 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We already proper insulation of the boiler body and Steam Distribution pipe line | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 131 | BB 13073 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We already proper insulation of the boiler body and Steam Distribution pipe line | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 132 | BB 15072 | The economizer was not equipped with a safety valve. | Economizers that can be isolated from a boiler allowing the economizer to become a fired pressure vessel, shall have a minimum of one pressure safety valve in a location recommended by the manufacturer or as close as practical to the economizer outlet. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 133 | BB 13073 | Steam leakage was observed in the boiler steam header valve. | The steam leakage shall be repaired to prevent burn hazard. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 134 | BB 15072 | Visual flame monitoring glass was out of order. | The visual flame monitoring glass shall be replaced with an appropriate one. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 135 | BB 13073 | Visual flame monitoring glass was out of order. | The visual flame monitoring glass shall be replaced with an appropriate one. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 136 | BB 12847 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | We removed the valve between the Boiler & the water level limiter sensor. | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 137 | BB 12847 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | We removed the valve between the Boiler & the Pressure Controller. | Feb 16 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 138 | BB 12847 | No emergency stop push switch was available on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We have already installed the Emergency Stop . | Apr 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 139 | BB 9109 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | We already install Proper Steam Pressure Gauge(16KGg). | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 140 | BB 3583 | Steam leakage was observed in the boiler from gauge glass joints & safety valve flange | The steam leakage shall be repaired to prevent burn hazard. | This work is Completed | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 141 | BB 5405 | Salt and scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 142 | BB 5737 | Salt and scale formation was observed on the waterside. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 143 | BB 6464 | Salt and scale formation was observed on the fire tubes of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 144 | BB 13073 | Salt and scale formation was observed on the waterside of the boiler. The scale is thin with 1mm. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This work wil be done with in 2 Months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 145 | BB 13729 | The refractory lining near the burner was damaged. | The lining should be repaired according to the manufacturer's guideline. | We have already repaired the refractory lining according to the manufacturer. | May 2 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 146 | Non BBR-9178-3 | Salt and soft scale formation was observed on the waterside of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 147 | Non BBR-9178-5 | Salt and soft scale formation was observed on the waterside of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 148 | Non BBR-9178-6 | Salt and soft scale formation was observed on the waterside of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 149 | Non BBR-9178-7 | Salt and soft scale formation was observed on the waterside of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 150 | BB 3583 | Salt and thin scale formation was observed on the waterside on smoke tube and end plate. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | This worK will be done with in 2 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 151 | BB 5405 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 152 | BB 5737 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 153 | BB 9110 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 154 | BB 5737 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 155 | BB 9110 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 156 | BB 5405 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 157 | BB 5737 | There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 158 | BB 6464 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 159 | BB 12847 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 160 | BB 12847 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 161 | BB 13729 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have already contact with Supplier,We are try to solve this issue as soon as possible | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 162 | BB 9109 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 163 | BB 9109 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 164 | BB 3583 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have made purchase requisition for the Matertials,the work will be be Completed once the materials are in-house | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 165 | BB 3583 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We have completed the work of low low water level trip of the boiler.Now The low low water level tripping mechanism is functional | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 166 | Non BBR-9178-1 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 167 | Non BBR-9178-2 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 168 | Non BBR-9178-3 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 169 | Non BBR-9178-4 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 170 | Non BBR-9178-5 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 171 | Non BBR-9178-6 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 172 | Non BBR-9178-7 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 173 | Non BBR-9178-8 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 174 | Non BBR-9178-9 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 175 | Non BBR-9178-10 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | This worK will be done with in 1 months | Mar 2 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 176 | Non BBR-9178-1 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 177 | Non BBR-9178-2 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 178 | Non BBR-9178-3 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 179 | Non BBR-9178-4 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 180 | Non BBR-9178-5 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 181 | Non BBR-9178-6 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 182 | Non BBR-9178-7 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 183 | Non BBR-9178-8 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 184 | Non BBR-9178-9 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 185 | Non BBR-9178-10 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | This worK will be done with in 2 months | Feb 9 2026 | Comments on 24-Feb-2026: The remediation work shall be done following provided guidelines and applicable standard within 5-Mar-26 | 1 WEEK | In Progress