## Structural
Date
02-Feb-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A YARN DYEING LTD., Kaichabari, West Side of DEPZ,Savar,Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2014-03-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Highly stressed columns | Factory Engineer to review design, loads and columns stresses including any additional loading as documented in the observations chapter. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. DEA was accepted on 28 April 2016. As per accepted DEA all footings, some columns were required to be retrofitted but yet the factory management has not taken any steps to start the remediation works. Factory management must complete all remediation works. On 13/10/2016:Factory management got their DEA approval on 28/04/2016. As per approved DEA retrofitting is required & during inspection retrofitting work was ongoing found in ground floor. On 16/02/2017: Factory has done DEA and submitted to ACCORD which was accepted on 02/12/2017. As per accepted DEA, Factory is required to retrofit the 4 columns of lift core and to demolish the roof shed. During inspection, the roof shed was found demolished. As the factory will not install lift, they have provided a written document and modified the retrofitting drawing and submitted the related documents to ACCORD. As per revision, factory is required to demolish two outer columns of lift core which was not done till inspection. On 04/06/2017: Factory has demolished roof top shed. Factory has given written declaration that they will not install lift in the lift core. They have demolished two columns of the lift core . On 13-Feb-2018: As per DEA recommendation, factory was required to carry out remediation. Instead of remediation, factory has demolished the roof top shed and columns of the lift core. This issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Factory has demolished the roof top shed. Factory has also demolished two lift core column and completed retrofitting of two other lift core column. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. As per accepted DEA rooftop shed and two lift core columns were demolished. Another two lift core columns were retrofitted. Issue remains corrected. On 14-Jan-2025: Corrected previously. This issue has been covered in DEA. DEA of the Main Production Building was re-accepted from ACCORD on 02-Dec-2016. | Within 6 weeks | Corrected
Initial Inspection |  | 2 | Highly stressed columns | Verify insitu concrete stresses either by 100mm diameter cores or existing cylinder strength data for cores from minimum 4 columns. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On verification we found that they have taken cores from column. On 07/08/2016: During inspection factory management could not show any core location or original test result. On 13/10/2016: This issue has been covered in DEA. During inspection factory management provided a copy of core test report. So this issue will be corrected after DEA verification. On 16/02/2017: Factory took cores from slabs and columns to verify concrete strength. Core test was done as a part of EA. During inspection, Original core test report was available. On 04/06/2017: Factory has completed core test. During inspection core locations were verified. On 13-Feb-2018: Cores were taken and original reports were available on site. Issue remains corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Cores were taken and original reports were available on site. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Cores were taken as part of DEA. Issue remains corrected. On 14-Jan-2025: Corrected previously. During inspection, core test report was available. | Within 6 weeks | Corrected
Initial Inspection |  | 3 | Highly stressed columns | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: During inspection intermediate load plan was not posted in any floor. Only some light storage was observed on roof level and load was observed below 30 psf in that area. In other floors no storage was observed and load was below 20 psf. Factory management shall post and maintain intermediate load plan until the remediation works are completed. On 13/10/2016: During inspection intermediate load plan was not posted in any floor. Only some light storage was observed on roof level (< 30 psf). In other floors no storage was observed (< 20 psf). Factory management will post and maintain intermediate load plan until the completion of retrofitting work. On 16/02/2017: Load Plan was prepared as a part of DEA. Factory has completed retrofitting as per revised drawing and loading was found within limit as per final load Plan(42 psf). Load plan was found posted on each floor. On 04/06/2017: Factory has produced load plan which is accepted along with DEA. They are maintaining load plan. Load plan found posted on each floor. On 13-Feb-2018: Load plan has been prepared and found posted on each floor. Floor loading observed below the allowable limit of final load plan. On 30-Jul-2018: Corrected from previous follow up inspection. Load plan has been prepared and found posted on each floor. Floor loading observed below the allowable limit of final load plan. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Accepted load plan was posted. Loading was found within allowable limit(42psf). Issue remains corrected. On 14-Jan-2025: Corrected previously. Load plan has been prepared as part of DEA. During inspection, load plan was found posted in each floor and loading was found within allowable limit (42 psf). | Within 6 months | Corrected
Initial Inspection |  | 4 | Undocumented vertical extensions | The Building Engineer should check the load plans and confirm that the main building structure is capable of safely supporting the additional loading on the structure from the roof extension. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA footings and some columns are required to be retrofitted. On 13/10/2016: Factory management got their DEA approval on 28/04/2016. As per approved DEA retrofitting is required & during inspection retrofitting work was ongoing found in ground floor. On 16/02/2017: This issue was covered in DEA which was accepted by ACCORD on 02/12/2016. As per accepted DEA, Factory must demolish the roof shed. During inspection, roof shed was found completely demolished. On 04/06/2017: Factory has demolished the roof shed. On 13-Feb-2018: Roof top shed was found demolished. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Roof top shed was found demolished. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. No vertical extension was done. Accepted load plan was posted. Loading was found within allowable limit(42psf). Issue remains corrected. On 14-Jan-2025: Corrected previously. Rooftop shed has been demolished. During inspection, Main production Building was found 4 storied (G+3) and no horizontal and vertical extension was observed. | Within 6 weeks | Corrected
Initial Inspection |  | 5 | Undocumented vertical extensions | Building Engineer to provide detailed calculations for the temporary rooftop structures and the associated light steel roofs. These should confirm their ability to withstand all wind loading pressure, suctions and uplift forces. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA the light steel roof is required to be demolished but during inspection it was observed that the factory management has not started the remediation work. On 13/10/2016: Same as previous comment. On 16/02/2017: This issue was covered in DEA which was accepted by ACCORD on 02/12/2016. As per accepted DEA, Factory must demolish the roof shed. During inspection, roof shed was found completely demolished. On 04/06/2017: Factory has demolished the roof shed. On 13-Feb-2018: Roof top shed was found demolished. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Roof top shed was found demolished. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Rooftop structures were removed. Issue remains corrected. On 14-Jan-2025: Corrected previously. This issue has been covered in DEA. Factory has removed temporary roof top steel structure. | Within 6 months | Corrected
Initial Inspection |  | 6 | Undocumented vertical extensions | Building engineer to check, collect information and produce accurate and complete as-built documentation. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On verification they were asked to change the as built drawing of Shed building since the actual condition does not match. On 07/08/2016: This issue has been covered in DEA. The as built drawing will be checked during DEA verification inspection. On 13/10/2016: This issue has been covered in DEA report. So this issue will be checked after DEA verification. On 16/02/2017: This issue was covered in DEA which was accepted by ACCORD on 02/12/2016. As per accepted DEA, Factory must demolish the roof shed. During inspection, roof shed was found completely demolished. On 04/06/2017: Factory has demolished the roof shed. On 13-Feb-2018: As-built drawing has been prepared along with DEA. This issue was found corrected from previous follow up inspection. On 13-Feb-2018: This issue was covered in DEA. DEA was accepted on 26th April 2016. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Roof top shed was found demolished On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Rooftop structures were removed. Issue remains corrected. On 14-Jan-2025: Corrected previously. As built drawings have been prepared as part of DEA which was re-accepted from ACCORD on 02-Dec-2016. | Within 6 months | Corrected
Initial Inspection |  | 7 | Cracking in slab below full-height partition | Flat slab capacity to be assessed for additional loading due to brick partitions, and extent of cracking within slab depth to be investigated. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA retrofitting is required for the flat slab but during inspection it was observed that retrofitting of flat slab was not done. Factory management must complete retrofitting work. On 13/10/2016: This issue has been covered in DEA report. As per accepted DEA retrofitting is required for the flat slab but slab retrofitting not started yet. Factory management told they have demolished the full height partition wall from 2nd floor. On 16/02/2017: This issue was covered in DEA. As a part of DEA, factory has checked the capacity of the flat slab and found ok. The crack on slab was investigated by the factory engineer and the crack was found not structural. On 04/06/2017:This issue is covered in DEA. Factory has checked the capacity of flat slab which is adequate. Crack is found non structural . Factory has removed the partition wall. On 13-Feb-2018: This issue was covered in DEA. DEA was accepted on 26th April 2016. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. This issue was covered in accepted DEA on 26th April 2016. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by Accord on 26-April-2016. No crack was found. Issue remains corrected. On 14-Jan-2025: Corrected previously. During inspection, no crack was observed on slab. | Within 6 weeks | Corrected
Initial Inspection |  | 8 | Cracking in slab below full-height partition | Remove partitions if required by design check | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA retrofitting is required for the flat slab but during inspection it was observed that retrofitting of flat slab was not done. Factory management must complete retrofitting work. On 13/10/2016: This issue has been covered in DEA report. As per accepted DEA retrofitting is required for the flat slab but slab retrofitting not started yet. Factory management told they have demolished the full height partition wall from 2nd floor. On 16/02/2017: This issue was covered in DEA. As a part of DEA, factory has checked the capacity of the flat slab and found ok. The crack on slab was investigated by the factory engineer and the crack was found not structural. factory has demolished the partition wall on 2nd floor above the crack portion. On 04/06/2017:This issue is covered in DEA. Factory has checked the capacity of flat slab which is adequate. Crack is found non structural . Factory has removed the partition wall. On 13-Feb-2018:This issue was covered in DEA. DEA was accepted on 26th April 2016. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. This issue was covered in accepted DEA on 26th April 2016. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by Accord on 26-April-2016. Partition walls were removed. Issue remains corrected. On 14-Jan-2025: Corrected previously. Factory has removed the partition wall. | Within 6 months | Corrected
Initial Inspection |  | 9 | Cracking in slab below full-height partition | Repair slab if required following investigation of crack | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA retrofitting is required for the flat slab but during inspection it was observed that retrofitting of flat slab was not done. Factory management must complete retrofitting work. On 13/10/2016: This issue has been covered in DEA report. As per accepted DEA retrofitting is required for the flat slab but slab retrofitting not started yet. Factory management told they have demolished the full height partition wall from 2nd floor. On 16/02/2017: This issue was covered in DEA. As a part of DEA, factory has checked the capacity of the flat slab and found ok. The crack on slab was investigated by the factory engineer and the crack was found not structural. factory has demolished the partition wall on 2nd floor above the crack portion On 04/06/2017:This issue is covered in DEA. Factory has checked the capacity of flat slab which is adequate. Crack is found non structural . Factory has removed the partition wall. On 13-Feb-2018:This issue was covered in DEA. DEA was accepted on 26th April 2016. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Crack investigation report was found and recommended as non structural crack. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by Accord on 26-April-2016. Cracks were repaired. No further crack was observed. Issue remains corrected. On 14-Jan-2025: Corrected previously. During inspection, no crack was found on slab. | Within 6 months | Corrected
Initial Inspection |  | 10 | Cracking in slab below full-height partition | Design check of building required prior to installing any new brick partition walls. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA retrofitting is required for the flat slab but during inspection it was observed that retrofitting of flat slab was not done. Factory management must complete retrofitting work. On 13/10/2016: This issue has been covered in DEA report. As per accepted DEA retrofitting is required for the flat slab but slab retrofitting not started yet. Factory management told they have demolished the full height partition wall from 2nd floor. On 16/02/2017: This issue was covered in DEA. As a part of DEA, factory has checked the capacity of the flat slab and found ok. The crack on slab was investigated by the factory engineer and the crack was found not structural. factory has demolished the partition wall on 2nd floor above the crack portion. On 04/06/2017:This issue is covered in DEA. Factory has checked the capacity of flat slab which is adequate. Crack is found non structural . Factory has removed the partition wall. On 13-Feb-2018:This issue was covered in DEA. DEA was accepted on 26th April 2016. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. This issue was covered in accepted DEA on 26th April 2016. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by Accord on 26-April-2016. Partition walls were removed. Issue remains corrected. On 14-Jan-2025: Corrected previously. | Within 6 months | Corrected
Initial Inspection |  | 11 | Localised areas of high loading in all buildings | Extent of build-up loading in toilet and wash areas to be surveyed and weight of water tanks on roof to be assessed. The capacity of floor & roof slabs to be assessed to confirm that the structure is designed to carry these loads. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA all footings, some columns were required to be retrofitted but yet the factory management has not taken any steps to start the remediation works. Factory management must complete all remediation works. On 13/10/2016: This issue has been covered in DEA report. As per accepted DEA retrofitting is required for all footing & some of columns. During inspection retrofitting was ongoing in ground floor. On 16/02/2017: This issue was covered in DEA. Factory has done DEA which was accepted by ACCORD on 02/12/2016.As per DEA, flat slab was found ok. On 04/06/2017:This issue is covered in DEA. Factory has checked the capacity of flat slab which is adequate. On 13-Feb-2018:This issue was covered in DEA. DEA was accepted on 26th April 2016. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. This issue was covered in accepted DEA on 26th April 2016. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. DEA was accepted by Accord on 26-April-2016. No high loading area was observed. Issue remains corrected. On 14-Jan-2025: Corrected previously. This issue has been covered in DEA which was re-accepted from ACCORD on 02-Dec-2016. | Within 6 weeks | Corrected
Initial Inspection |  | 12 | Localised areas of high loading in all buildings | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. Loading plans to be put on each factory floor. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: During inspection intermediate load plan was not posted in any floor. Only some light storage was observed on roof level and load was observed below 30 psf in that area. In other floors no storage was observed and load was below 20 psf. Factory management shall post and maintain intermediate load plan until the remediation works are completed. On 13/10/2016: During inspection intermediate load plan was not posted in any floor. Only some light storage was observed on roof level (< 30 psf). In other floors no storage was observed (< 20 psf). Factory management will post and maintain intermediate load plan until the completion of retrofitting work. On 16/02/2017: Load Plan was prepared as a part of DEA. Factory has completed retrofitting as per revised drawing and loading was found within limit as per final load Plan(42 psf). Load plan was found posted on each floor. On 04/06/2017: Factory has produced load plan which is accepted along with DEA. They are maintaining load plan. Load plan found posted on each floor. On 13-Feb-2018: Load plan has been prepared and posted in each floor. Floor loading observed below the allowable limit of final load plan. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Load plan has been prepared and found posted on each floor. Floor loading observed below the allowable limit of final load plan. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Accepted load plan was posted. Loading was found within allowable limit(42psf). Issue remains corrected. On 14-Jan-2025: Corrected previously. Load plan has been produced as part of DEA. During inspection, load plan was found posted in each floor and loading was found within allowable limit (42 psf). | Within 6 months | Corrected
Initial Inspection |  | 13 | Unrestrained parapet at roof level | Building engineer to assess stability of the roof partitions. | Completed | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On site we found that they have already installed an angle on roof. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA retrofitting is required for the parapet wall on the roof top level. During inspection it was observed that no work was done, Factory management shall complete the retrofitting work. On 13/10/2016: Corrected; Factory management retrofitted the parapet wall at roof level as per recommendation of DEA. On 16/02/2017: Corrected from previous follow up inspection report. On 04/06/2017: This issue is corrected from previous inspection. On 13-Feb-2018:This issue was covered in DEA. DEA was accepted on 26th April 2016. Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Factory has demolished the parapet at roof level. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. The parapet at roof level was demolished. Issue remains corrected. On 14-Jan-2025: Corrected previously. Factory has removed wall adjacent to water tank storage from roof. | Within 6 weeks | Corrected
Initial Inspection |  | 14 | Unrestrained parapet at roof level | Repairs to be carried out as required by engineering assessment. | Completed | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On site we found that they have already installed an angle on roof. On 07/08/2016: This issue has been covered in DEA. As per accepted DEA retrofitting is required for the parapet wall on the roof top level. During inspection it was observed that no work was done, Factory management shall complete the retrofitting work. On 13/10/2016: Corrected; Factory management retrofitted the parapet wall at roof level as per recommendation of DEA. On 16/02/2017: Corrected from previous follow up inspection report. 04/06/2017: This issue is corrected from previous inspection. On 13-Feb-2018: Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Factory has replace the previous wall with the new parapet wall which was found restrained. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. The parapet at roof level was replaced. Issue remains corrected. On 14-Jan-2025: Corrected previously. Factory has removed wall adjacent to water tank storage from roof. | Within 6 months | Corrected
Initial Inspection |  | 15 | Undocumented single storey industrial and utility buildings | Building Engineer to verify that building has an appropriate lateral stability system and submit relevant design document | Completed | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in EA of the industrial and Utility building. As per accepted EA retrofitting is required for the shed. On 13/10/2016: As per EA recommendation retrofitting is required for the shed but during inspection no retrofitting work seen started. On 16/02/2017: Factory has done Engineering Assessment of Industrial building which was accepted by ACCORD. As per accepted EA, retrofitting is required to the industrial shed which was not started till inspection date. Factory has provided a written document stated that they will not use the industrial shed. Besides, They informed us that they will demolish the industrial shed. 04/06/2017: This issue is corrected from previous inspection. Factory has given declaration that they will not use the shed. They are constructing new shed to relocate materials. On 13-Feb-2018: Issue was found corrected from previous follow up inspection. On 30-Jul-2018: Corrected from previous follow up inspection. Factory management has demolished those buildings. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Those buildings were demolished. Issue remains corrected. On 14-Jan-2025: Corrected previously. Factory has demolished single storey industrial & utility building and constructed new structure in that place. | Within 6 weeks | Corrected
Initial Inspection |  | 16 | Undocumented single storey industrial and utility buildings | Carry out remedial work if required. | Corrected. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: During inspection it was observed that no work was done, Factory management shall complete the retrofitting work. On 13/10/2016: As per EA recommendation retrofitting is required for the shed but during inspection no retrofitting work seen started. On 16/02/2017: Factory has done Engineering Assessment of Industrial building which was accepted by ACCORD. As per accepted EA, retrofitting is required to the industrial shed which was not started till inspection date. Factory has provided a written document stated that they will not use the industrial shed. 04/06/2017: Factory has given declaration that they will not use the single story industrial and utility building. They are constructing new shed to relocate materials. They have said that they will demolish the single story industrial and utility building after new shed is completed. On 13-Feb-2018: As per DEA, remedial works were required for the single storey industrial building. Instead of completing remediation, Factory management confirmed that they will not use this shed in future and new shed was found constructing in the factory premises. They also informed that, after completing the new shed, this old shed will be demolished. On 30-Jul-2018: Factory management has demolished those buildings. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Those buildings were demolished. Issue remains corrected. On 14-Jan-2025: Corrected previously. Factory has demolished single storey industrial & utility building and constructed new structure in that place. | Within 6 months | Corrected
Initial Inspection |  | 17 | Undocumented single storey industrial and utility buildings.. | Building engineer to assess single storey utility building and confirm its ability to withstand all wind loading pressure, suctions and uplift forces | It has been decided to relocate all facilities from the undocumented industrial shed to the newly constructed warehouse and this abandoned shed will be only used for Non-commercial purpose. The construction work of new Industrial shed is about completed. | Nov 15 2016 | On 01/07/2015: This issue will be covered under DEA. They have submitted the DEA which is under review. On 07/08/2016: This issue has been covered in EA of the industrial and Utility building. As per accepted EA retrofitting is required for the shed. On 13/10/2016: As per EA recommendation retrofitting is required for the shed but during inspection no retrofitting work seen started. On 16/02/2017: No documents of Utility building was observed. Factory is required to assess the utility shed & submit assessment to ACCORD as soon as possible. On 04/06/2017: Factory has given declaration that they will not use the shed. They are constructing new shed to relocate materials. They have said that they will demolish the single story industrial and utility building after new shed is completed. On 13-Feb-2018: Factory management has demolished the utility building. On 30-Jul-2018: Corrected from previous follow up inspection. Factory management has demolished those buildings. On 07-Mar-2022: This issue was corrected in previous follow-up inspection. Those buildings were demolished. Issue remains corrected. On 14-Jan-2025: Corrected previously. Factory has demolished single storey industrial & utility building and constructed new structure in that place. | Within 6 months | Corrected

## Fire
Date
02-Feb-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A YARN DYEING LTD., Kaichabari, West Side of DEPZ,Savar,Dhaka, Savar, Dhaka
Date of Inspection |  | 2014-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boiler & generator shared the same room, and we're not separated from each other by fire rated construction. | Separate the boiler & generator rooms by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations |  | Aug 30 2015 | On 13/10/2016: Corrected. On 12/12/2016: Corrected. On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Issue reopened. It reflects on issue 32. On 30/07/2018: Refer to issue #32. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | The generator room had unprotected window openings facing another (non-factory) building approximately 5 feet away | Separate the generator room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations |  | Jun 30 2015 | On 25/01/2016: Corrected. On 03/04/2016: Corrected. On 07/08/2016: Corrected. On 13/10/2016: Corrected. On 12/12/2016: Corrected. On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Issue reopened. It reflects on issue 32. On 30/07/2018: Refer to issue #32. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Areas used for combustible storage are not separated by firerated construction. Fabric Store room, Packing Section, 4th floor waste store room. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction, Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. |  | Apr 30 2016 | On 22-02-2017: Corrected. Factory has demolished the roof top store room & unarranged storage was not found during follow up inspection. On 21/05/2017: Corrected as per previous follow up. Note: factory will ensure that factory is maintaining the storage limit as per Accord recommendation. On 20/09/2017: Corrected as per previous follow up. On 11/03/2018: Corrected as per previous follow up. On 30/07/2018: Corrected. On 07/03/2019: Corrected. Maintaining. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | The exit stairs are not separated from work areas or other spaces on each floor by fire rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons,provide automatic closing devices tied to the fire alarm system |  | Apr 30 2016 | On 21/05/2017: Partially corrected. Fire doors installation including interfacing is almost done. Stair landing is obstructed by non rated door at south exit stair on all the floor. On 20/09/2017: Stair landing is obstruct by non-rated doors. Interfacing work is not fully completed yet. Factory was using external sources for keeping the doors open in few places. On 11/03/2018: Progress done. Testing and commissioning will check the interfacing of FA system. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. Note: Functionality of fire door shall be maintained properly and if any field modification is required then it shall be permitted by manufacturer and listing authority. | Within 3 months | Corrected
Initial Inspection |  | 5 | Exit capacity is not adequate for the occupant load on 3rd floor | Reduce the occupant load on the 3rd floor immediately. In the future provide adequate egress width by either: - Addition of an exit stair or - Upgrade of the existing North exit stair to provide sufficient combined width for the occupants of 3rd floor |  | Apr 10 2016 | On 12/12/2016: Corrected. Reduced. On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 6 | Egress doors / gates with locking features are provided at all exit stair openings and central stair discharge | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Jun 30 2015 | On 12/12/2016: Corrected. On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Refer to issue #33 On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | Sliding doors are provided at all exit stair doors and central stair discharge. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 |  | Aug 30 2015 | On 12/12/2016: Corrected. On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Refer to issue #33 On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 8 | Waste bins were located in the central exit stair | Remove all storage from exit stairs and egress paths |  | Jun 30 2015 | On 12/12/2016: Corrected. On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. Removed. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 9 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72 |  | Apr 30 2016 | 12/06/2019 (J-H T&C): Not Approved. For details follow the full report. On 31-8-2021: N/A. Special Inspection. On 11/10/2021: T&C VI found that, the fire alarm system is not approved. Requires corrective action and should not be accepted until all items have been properly addressed and or resolved as per standard. See detailed T&C VI Report. On 07/03/2022: Installation and commissioning work is almost completed. Factory shall inform the RSC after completion of activities. On 19-Nov-2023: T&CVI has been conducted along with follow-up inspection and found that the system is requires on-site Final Verification. See the T&CVI report. On 13-Feb-2024: Final verification inspection (FVI) has been conducted along with follow-up inspection and found that the system is approved. See the detailed FVI report. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the fire alarm system were not in accordance with NFPA 72 | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. |  | Mar 30 2016 | On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants | Replace the single-station smoke alarms with automatic smoke detectors tied into the fire alarm system. Configure the fire alarm system to initiate occupant notification upon activation of any two smoke detectors in addition to the manual fire alarm stations |  | Apr 30 2016 | On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Corrected as per previous follow-up. On 11/03/2018:Corrected as per previous follow-up. On 30/07/2018: Refer to issue #9. On 07/03/2019: Corrected as per previous follow up. It is an integrated part of fire alarm system. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 12 | Exit signage not illuminated within fabric store was not working. | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs |  | Mar 30 2016 | On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 13 | New Finding: The building has an occupied floor greater than 10 meter (33 feet) and its not provided with standpipe system as per NFPA 14 & 20. | Provide standpipe and hose system as per NFPA 14 & 20. |  | Apr 30 2016 | On 07/03/2019: During follow up inspection (testing & commissioning) updated as built drawing and hydraulic calculation was not available on site. Factory shall submit updated as built drawing to Accord prior testing & commissioning (T&C) & ensure availability on-site during T & C. Protection system (standpipe) shall be deigned and install as per NFPA 14 & 20 and Accord standard. 12/06/2019 (J-H T&C): Not Approved. For details follow the full report. On 31-8-2021: N/A. Special Inspection. On 11/10/2021: T&C VI found that, the fire fighting system is not approved. Requires corrective action and should not be accepted until all items have been properly addressed and or resolved as per standard. See detailed T&C VI Report. On 07/03/2022: Installation and commissioning work is almost completed. Factory shall inform the RSC after completion of activities. On 19-Nov-2023: T&CVI has been conducted along with follow-up inspection and found that the system is requires T&CVI. See the T&CVI report. RPO Comments on 18 Dec 2023: The factory is determined as ready for T&CVI for SUPS as of 30 Nov 2023. On 13-Feb-2024: T&CVI has been conducted along with follow-up inspection and found that the system is approved. See detailed T&CVI report. | Within 6 months | Corrected
Follow Up Inspection |  | 14 | New Finding: Chemical storage area is not separated by fire-rated construction having non rated door and unsealed penetrations and openings in exit stair. | Separate the chemical storage room by 2-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. Keep 16-points MSDS of all chemicals in the storage area. ** As per BNBC, chemical storage room will be Type-1 construction. |  | Aug 30 2015 | On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected as per previous follow up. Factory shall relocate chemicals and machine oils from side of boiler room as construction of boiler room is still going on. On 07/03/2019: Corrected as per last follow up. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 15 | New Finding: Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. |  | Apr 10 2016 | On 21/05/2017: Corrected. On 20/09/2017: In progress. Unseal penetration found. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 16 | New Finding: Storage was located in the exit stair. | Remove all storage from exit stairs. |  | Apr 10 2016 | On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. Removed. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 17 | New Finding: Width of aisles is less than 0.9m (36-in.). | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). |  | Apr 30 2016 | On 21/05/2017: Corrected as per previous follow up. Note: factory will ensure the unobstructed 36 inch aisles on each and every floor. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Re-opened. Width of aisles has been found less than 36" in several places. Aisles has been blocked with DB and building column in almost every floor. On 07/03/2019: Corrected. Factory has re-arranged aisles mark. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 18 | New Finding: Storage was located in the exit way. | Remove all storage from exit way. |  | Dec 30 2015 | On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 19 | New Finding: Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. |  | Oct 31 2015 | On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. |  | Feb 10 2016 | On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. |  | Feb 10 2016 | On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 22 | New Finding: Exit way to in side of compressor room. | Separate the exit way from compressor room (ceiling, floor, wall etc.) by 1- hr fire-resistance rated construction and shall terminate at an exit discharge. |  | Apr 30 2016 | On 20/09/2017: Corrected. On 11/03/2018: Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Storage area is not separated by fire rated construction. | Separate the storage area (ceiling, floor, wall etc.) by 1- hr fire-resistance rated construction and shall terminate at an exit discharge. |  | Apr 30 2016 | On 22-02-2017: Corrected. On 21/05/2017: Corrected. On 20/09/2017: In progress. Fire doors were not closing properly during the time of inspection. On 11/03/2018: Same condition found. On 30/07/2018: Corrected. Storage area has been shifted to another building. On 07/03/2019: Corrected as per last follow up. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Dining room is not separated by fire rated construction. | Separate the dining room (ceiling, floor, wall etc.) by 1- hr fire-resistance rated construction and shall terminate at an exit discharge. |  | Apr 30 2016 | On 20/09/2017: Corrected. Dinning has been fully shifted. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected as per previous follow up. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 01 Month | Corrected
Follow Up Inspection |  | 25 | New Finding(3rd Follow-up): Directional signs are not provided where direction of the path of travel to an exit has changed. Location: On all floors. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. |  | Apr 30 2016 | On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding(3rd Follow-up): Handrails are not provided on both side in the exit stair. Location: Central exit stair. | Provide handrails on both side of exit stair having a minimum height 34 in. |  | Apr 30 2016 | On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. Provided. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding(3rd Follow-up): The external stair of South exit & North exit is not having a fire separation from the building beyond 10 feet of its span as required as per clause 6.3.1.3. | Provide a fire-resistive rated assembly between the exterior exit stairs and the building up to 10 ft. beyond the end of the stair to achieve the required separation. The rated assembly should be approved and/or designed by a qualified fire protection engineer. Enclose any openings (windows, etc.) with required fire rated construction within that 10 ft. wall section. |  | Apr 30 2016 | On 22-02-2017: Corrected On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018: Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding(3rd Follow-up): Stair name or designation is not mentioned. Occupant load is not also mentioned in Bangla & English. | Install signage adjacent to each stair door indicating the stair name and the occupant load level at the noted locations. |  | Apr 30 2016 | On 22-02-2016: Corrected On 21/05/2017: Corrected. On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected as per previous follow up. Note: Factory shall update stair designation sign. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding in 4th Follow-up: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. |  | Sep 7 2016 | On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding in 4th Follow-up: Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. |  | Sep 7 2016 | On 20/09/2017: Corrected. On 11/03/2018:Corrected. On 30/07/2018: Corrected. On 07/03/2019: Corrected. Removed. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding in 4th Follow-up: The exit discharge path is less than 10 ft wide and is not separated from the building interior. Location: North stair discharge path. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way (only include this if feasible). |  | Nov 13 2016 | On 21/05/2017: Corrected. Note: Factory will ensure that the exit discharge has been separated in proper way. On 20/09/2017: Corrected as per previous follow-up. On 11/03/2018: Corrected as per previous follow-up. On 30/07/2018: Corrected. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding in 9th Follow-up: The boiler and generator room is not separated by fire rated construction (openings, non-rated doors, penetrations) | Separate the boiler and generator room by a minimum 2-hr fire rated construction from the surroundings. Seal and/or protected all openings to maintain fire separations. |  | Oct 20 2017 | On 11/03/2018: Progress done but not yet finished On 30/07/2018: Corrected. Generator room is fully separated with boiler room. On 07/03/2019: Corrected. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 33 | New Finding: Glass sliding type doors and non-compliant locking features have been provided along means of egress. | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. |  | Aug 6 2018 | On 30/07/2018: NEW FINDING On 07/03/2019: Corrected. During follow up inspection non-compliant doors/gates & non-compliant locking features were not found in egress routes. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 week | Corrected
Follow Up Inspection |  | 34 | New Finding: Exit access corridor are not provided with 1 hr fire resistance rating or approved NFPA 13 sprinkler system. | Provide exit access corridors with 1 hr fire resistance rating Or Provide approved sprinkler system as per NFPA 13 . |  | Sep 30 2018 | On 30/07/2018: NEW FINDING On 07/03/2019: Corrected. During follow up inspection it was observed that factory has re-arranged egress routes and corridor not found. On 31-8-2021: N/A. Special Inspection. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 35 | New Finding (On 07/03/2019): Liquefied or compressed gas cylinders were located within the factory near boiler room on the ground floor. | The storage or use of liquefied or compressed flammable gas cylinders shall be prohibited within the factory building. |  | Apr 7 2019 | On 08/05/2019 the factory is asking timeline till 30/06/2019, which is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 07/03/2019: NEW FINDING On 31-8-2021: Corrected. Factory is supplied gas from Titas Gas Transmission & Distribution. On 07/03/2022: Corrected. On 19-Nov-2023: Corrected. On 13-Feb-2024: Corrected. | Within 1 month | Corrected

## Electrical
Date
02-Feb-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A YARN DYEING LTD., Kaichabari, West Side of DEPZ,Savar,Dhaka, Savar, Dhaka
Date of Inspection |  | 2014-03-24
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Cables laid on floor without protection in boiler room. | Install cable trays supported from the ceiling to provide power from distribution panel to load or construct cable trench or steel pipe to laid cable in trench or pass through pipe on floor respectively. | Completed | Jun 30 2015 | On 01/07/15: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Oil spilled in generator room floor. | Generator room floor must be kept free from oil spillage to avoid fire hazard. Establish a routine cleaning program to keep the generator room neat and clean. | Completed | Jun 30 2015 | On 01/07/15: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Lint, dust and debris found in uncovered cable trench. | Provide metallic cover or RC slab on cable to avoid physical damage to the cables from falling objects and to keep the trench free from lint, dust and debris. | Completed | Jun 30 2015 | On 25/01/16: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Cables encased in flexible pipe not supported and protected. | Use rigid PVC pipe (use steel pipe on floor) or cable to support and protect the cables entering and leaving the panel. Support the conduits at regular intervals. | Completed | Feb 28 2016 | On 03/04/16: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 5 | Panel enclosure including its door not connected to earth. | Provide earth connection to metallic panel enclosure including its door by using green cables preferably earthling braid so that the metallic door remains at zero potential all the time. | Completed | Jun 30 2015 | On 01/07/15: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 6 | Cable laid directly on floor without protection. | Use steel pipe to ensure the mechanical protection of the cables laid on floor otherwise cable insulation may damage due to falling object or stepping of occupants onto it. | Completed | Jun 30 2015 | On 25/01/16: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 7 | Cables terminated to bus bar inside panel without using cable lugs/sockets. | Use proper sized cable lugs to terminate the cables to bus bar. Punch the lugs by proper hand puncher or hydraulic puncher. Use chromium plated nut, bolt and washer to fix the lugs (cables) to bus bar tightly. | Completed | Jun 30 2015 | On 01/07/15: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 8 | Barrier/separators between different phases are not installed. | Install separators/barriers between different phases of MCCB to avert flashover. Standard separators provided by the MCCB manufacturer must be used. | Completed | Jun 30 2015 | On 01/07/15: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 9 | Wirings in flexible PVC conduit entering and leaving panels not firmly fixed. | Extend the cable tray up to the distribution panel and encased the cables inside it. Install base plate of the panel and make hole into it then fit cable glands (required sized) for cable entry and exit to the panel and seal all the unused openings. | Completed | Mar 5 2016 | On 03/04/16: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Cables arranged inside the panel haphazardly. | Arrange the main incoming cable inside panel by avoiding acute bend and install slotted PVC channel to route and arrange cables inside panel. | Completed | Aug 31 2015 | On 01/07/15: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | Excessive dust and lint deposit inside distribution panel. | Install the base plate of the panel as well as seal all the unused openings of the panel to make the distribution panel dust and vermin proof. | Completed | Sep 30 2015 | On 01/07/15: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | Panel base plate not installed to allow cable entry. | Install base plate of the panel and make hole into it then fit cable gland (required sized) for cable entry and exit to the panel and seal all the unused openings by suitable means to make the panel dust and vermin proof. | Completed | Feb 29 2016 | On 03/04/16: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 13 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | Completed | May 15 2016 | On 25/01/16: Not corrected.Timeline:05/03/16 On 03/04/16: Not Corrected. New timeline: May 15, 2016. On 07/08/2016: Not corrected On 13/10/2016: Not Corrected On 12/12/2016: Not Corrected. On 22/02/2017: Not corrected. On 21/05/2017: Corrected | Within 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Lightning Protections System (LPS) is inadequate for the factory. | Redesign/modify LPS for your factory to increase safety. | Completed | May 30 2016 | On 25/01/16: Not corrected and time extension is 05/03/16 On 03/04/16: Not Corrected. New timeline: 30/05/2016. On 07/08/2016: Not corrected. LPS installation is going on. On 13/10/2016: Corrected | Within 3 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Earth Pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Completed | Aug 31 2015 | On 25/01/16: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Insulation resistance test of electrical cables is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Completed | Aug 31 2015 | On 25/01/16: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | Completed | Mar 5 2016 | On 03/04/16: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Hot spots at terminations inside panel. Thermo graphic inspection record is unavailable. | Arrange periodic inspection & thermal scan at least twice in a year to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, correct such points immediately. | Completed | Apr 30 2016 | On 25/01/16: Not Corrected. On 03/04/16: Not Corrected. New timeline:30/04/2016. On 07/08/2016: Not corrected. On 13/10/2016: Not corrected Thermographic scan report is available but Hot point found at several points. On 12/12/2016: Corrected. No such points found. | Within 2 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals | Completed | May 15 2016 | On 25/01/16: Not corrected and time extension 05/03/16 On 03/04/16: Not Corrected. New timeline: May 15, 2016. On 07/08/2016: Not corrected On 13/10/2016: Not Corrected On 12/12/2016: Not Corrected. On 22/02/2017: Corrected | Within 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded | Completed | Aug 25 2015 | On 25/01/16: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Multiple cables terminated at MCCB terminals/ Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. | Completed | May 15 2016 | On 25/01/16: Not corrected and time extension is 05/03/16 On 03/04/16: Not Corrected. New timeline: May 15, 2016. On 07/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 22 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Completed | May 15 2016 | On 25/01/16: Not corrected and time extension is 29/02/16 On 03/04/16: Not Corrected. New timeline: May 15, 2016. On 07/08/2016: Not corrected On 13/10/2016: Corrected | Within 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). Again, the ballast of tube light is installed inside the cable duct with other cable. | Clean all the cable channels/ducts; then cover them (you may use checkered/perforated plate at the bottom). And after each maintenance, keep record. Again, remove or separate the ballast from other electrical cables so that cables cannot receive heat from. | Completed | May 15 2016 | On 25/01/16: Not corrected and new timeline is 05/03/16. On 03/04/16: No lint/dust & ballast of tube light was found inside cable duct/channel but not get any cover of cable duct. New timeline is May 15, 2016. On 07/08/2016: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: MCB is installed at wrong place (inside cable duct) without any enclosure. | Need to provide electrical graded enclosure | Completed | Feb 29 2016 | On 03/04/16: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Completed | Apr 5 2016 | On 03/04/16: Corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Exhaust fans are used direct from MCB. | Use Direct On Line (DOL) switch to stop auto start after power failure. | Completed | Mar 5 2016 | On 03/04/16: Corrected. | Within 1 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Completed | Mar 5 2016 | On 03/04/16: Corrected. | Within 1 Months | Corrected
Follow Up Inspection |  | 28 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. | Completed | May 15 2016 | On 03/04/16: Not Corrected. New timeline is May 15, 2016. On 07/08/2016: Not corrected On 13/10/2016: Corrected | Within 1 Months | Corrected
Follow Up Inspection |  | 29 | New Finding: Generator output cables (laid on floor) are not protected and supported. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. | Completed | May 15 2016 | On 07/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Exposed and heated steam line is close to cable channel. | Wires close/attached to steam line/heat source must be protected from external heat. In unavoidable case provide proper insulation for the heat source/steam line. Normally power cable should keep 0.9m apart from hot area. | Completed | May 15 2016 | On 07/08/2016: Not corrected On 13/10/2016: Corrected | Within 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Three phase MCCB connected to control two phases or less. | Check and redesign the requirements to control the circuits. If three phase control is not required, then replace with suitable control devices (Switch of Security Light). | Completed | May 15 2016 | On 07/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Power Cables are hanging without support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Completed | Oct 20 2016 | On 13/10/2016: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Field information has less reflection in existing SLD. | Electrical SLD must be amended properly; all the required information must be mentioned there; and it shall be updated when you do significant amount of changes of your electrical system. | Completed | Mar 31 2017 | On 22/02/2017: Not corrected. Time extension is given till 31/03/2017. On 21/05/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Unprotected cables terminated at sockets | Proper protection must be ensured for unprotected cables termination. | Completed | Apr 20 2018 | On 30/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Air terminal are not fixed properly with base plate and nut-bolt & washers are rusted at several points of Lightning Protection System. | Air Terminals shall be installed properly and rusted nut-bolt must be replaced. | Completed | Sep 2 2018 | On 07/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Power cables entering or exiting from Distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). Any arrangement that creates trip hazard must be removed. | Corrected | Mar 10 2020 | On 07-Mar-2022: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Inadequate sized earth cable connected to generator frame. | Two separate earth connection & one separate and distinct Neutral connection must be provided over generator. Generator body must have earth connection with half of phase conductor or follow manufacturer/suppliers recommendation. | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables(P,N.E) used in the system according to SLD. | All power cable identification done . Corrected | Feb 10 2020 | On 07-Mar-2022: Not Corrected. On 19-Nov-2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Battery cases are kept on temporary support (Brick). | Use non-flammable case/shelf to store battery | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: HT Cable dropping from 11kV OH line is not firmly supported to the pole. | HT cable dropping from 11kV pole must be firmly fixed to the pole with supports and clamps and protected by steel/PVC rigid conduit up to minimum of 2 meters above ground level. | We installed support , Corrected | Feb 10 2020 | On 07-Mar-2022: Not Corrected. Still work is pending inside substation room. On 19-Nov-2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Maintenance movement is obstacle due to uneven height of cable trench in utility area (transformer room). | Work place around transformer (or other electrical installation) must be on same height. Adequate working clearance (1.07m around) and ventilation is required. | Corrected | Mar 10 2020 | On 07-Mar-2022: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Transformer Breather oil cup is empty | Transformer breather oil cup must be filled not more than 70% of its capacity. | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. Old transformer is changed with dry type. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: MCCB/MCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. | all MCCB set up as pre requirements and updated SLD Corrected | Feb 10 2020 | On 07-Mar-2022: Not Corrected. Still work is going on. On 19-Nov-2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Loop connection has been used powering multiple circuits through MCB/MCCBs. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity) | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Multiple cables connected/terminated at the bus bar using single cable lug. | Each power cable must be terminated at any point using single cable lug. | Corrected | Feb 10 2020 | On 07-Mar-2022: Corrected. | 1 Month | Corrected

## Boiler
Date
02-Feb-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | 4A YARN DYEING LTD., Kaichabari, West Side of DEPZ,Savar,Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2022-04-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 11935 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Emergency stop push switches installed on the boiler control panel and outside the boiler room | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 11935 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The Low Low Water Level (LLWL) marked beside the gauge glass on a separate arrangement | Mar 4 2026 | Comments on 01-Feb-2026: Markings should be properly done on a separate arrangement, with the levels clearly marked and written for clear understanding. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 3 | BB 11935 | Necessary technical documents (water treatment report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | All technical documents available | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work status could not be assessed, as no image was provided. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 11935 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Fuel line openings in boiler room diverted outside of the boiler room and also some point sealed off with a bond plug/blind flange to prevent fuel leakage. | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 11935 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Unused steam line terminated | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 11935 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | New pressure gauge installed | Feb 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 14163 | Valves were observed between the boiler and the water level limiter sensor. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. Any modification shall be consulted with the manufacturer. | Valve have been removed from water level limiter | Jan 11 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 14163 | Valves were observed between the boiler and the pressure controller. | The measuring and sensing devices related to boiler safety shall be mounted directly with the boiler without any valves in between. | valve have been removed from steam pressure controller | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 14163 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The Low Low Water Level (LLWL) marked beside the gauge glass on a separate arrangement | Mar 4 2026 | Comments on 01-Feb-2026: Markings should be properly done on a separate arrangement, with the levels clearly marked and written for clear understanding. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 14163 | Unused steam line connection was not terminated properly. | Any unused & unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | Unused steam line terminated | Jan 18 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 11935 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve. | From manufacture there are no drain line for water level gauge glass. For water level check we may use blow down line | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 12 | BB 11935 | Salt and scale formation (1~2 mm) was observed on the waterside on inside water tube, top and bottom endplate of the boiler. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | water side of the boiler water tube cleaned | Feb 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 13 | BB 14163 | Carbon deposition was found in the (smoke tubes). | The furnace and inside of the fire tubes should be cleaned periodically to prevent excessive soot build-up. The fuel burner should be adjusted according to the manufacturer's guidelines. | Smoke tubes habe been cleaned | Mar 4 2026 | Comments on 01-Feb-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification