## Structural
Date
03-Jan-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.M Design Ltd., Dia khali , Beron, Zirabo , Ashulia,Savar,Dhaka, Savar, Dhaka
Date of Inspection |  | 2014-05-03
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Sensitivity of cantilever areas to loading | Building Engineer to assess capacities of cantilever slabs and develop and implement loading plans for these areas as necessary. | DONE | May 7 2016 | Previous timeline: 08.05.16 DEA along with load plan has been developed by factory management. DEA has been accepted by Accord. During DEA verification inspection, it was observed that the cantilever portions were loaded. Factory management is advised to reduce the loads within 2 days On 16.10.17: During inspection cantilever portions were found occupied with loading below the allowable limit of accepted load plan. On 18-Aug-2019: Load plans were found posted and floor loading was found below the allowable limit of accepted final load plan. Issue remains corrected. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. Accepted load plan(42 psf) was posted. Loading was found within 42 psf. Issue remains corrected. On 18-Feb-2024: This issue was corrected from previous inspection. Accepted floor load plans were found posted and floor loading was found below the allowable limit (42 psf). | 6-weeks | Corrected
Initial Inspection |  | 2 | Sensitivity of cantilever areas to loading | Building Engineer to implement loading plans specific for cantilever areas. (to be incorporated in Item 2 actions) | DONE | May 7 2016 | Previous timeline: 08.05.16 DEA along with load plan has been developed by factory management. DEA has been accepted by Accord. During DEA verification inspection, it was observed that the cantilever portions were loaded. Factory management is advised to reduce the loads within 2 days On 16.10.17: During inspection cantilever portions were found occupied with loading below the allowable limit of accepted load plan. On 18-Aug-2019: Load plans were found posted and floor loading was found below the allowable limit of accepted final load plan. Issue remains corrected. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. Accepted load plan(42 psf) was posted. Loading was found within 42 psf. Issue remains corrected. On 18-Feb-2024: This issue was corrected from previous inspection. Accepted floor load plans were found posted and floor loading was found below the allowable limit (42 psf). | 6-weeks | Corrected
Initial Inspection |  | 3 | Concentrated areas of high loading | Building Engineer to develop loads plans for all buildings, accounting for usage, floor build ups, solid partition walls and areas of concentrated loading. Factory management to implement load plans. | DONE | May 7 2016 | Previous timeline: 25.02.16. During DEA verification, it was observed that the loading on 1st floor area exceeds 42psf. According to approved load plan by Accord, there was no provision for storage at the area which was observed to be overloaded. The factory is advised to reduce and relocate the loads within 2days. On 16.10.2017: During inspection, accepted load plan was posted on each floor and floor loading was below the allowable limit of posted load plan. On 18-Aug-2019: Load plans were found posted and floor loading was found below the allowable limit of accepted final load plan. Issue remains corrected. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. Accepted load plan(42 psf) was posted. Loading was found within 42 psf. Issue remains corrected. On 18-Feb-2024: This issue was corrected from previous inspection. Accepted floor load plans were found posted and floor loading was found below the allowable limit (42 psf). | 6-months | Corrected
Initial Inspection |  | 4 | No stiffening edge beam to assumed one way spanning slab GL 6/7 parallel to GL G | Building Engineer to confirm one-way spanning slab parallel to GL G (as assumed). IF slab is designed/constructed as a cantilever about GL F a verification of the slab design is required. | Done | May 8 2015 | During DEA verification inspection, some discrepancy was observed between as built condition and drawing. The factory has revised the drawing which has been accepted by Accord. On 16.10.2017: Corrected from previous inspection. On 18-Aug-2019: Issue was found corrected from previous follow up report. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. This issue was covered in accepted EA report. On 18-Feb-2024: This issue was corrected from previous inspection. | 6-weeks | Corrected
Initial Inspection |  | 5 | No stiffening edge beam to assumed one way spanning slab GL 6/7 parallel to GL G | Building Engineer to monitor façade cracking due to unstiffened slab edge and restrict floor use with loading plans as defined in item 1 | Done | Feb 28 2016 | During DEA verification inspection, some discrepancy was observed between as built condition and drawing. The factory has revised the drawing which has been accepted by Accord. On 16.10.2017: Corrected from previous inspection. On 18-Aug-2019: Cracks were repaired already. During a walk through session, cracks were found at facade wall which had been repaired. Factory has provided crack investigation report which declared that cracks were non-structural. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. Cracks in facade were found repaired. As per investigation report, cracks were non-structural. Loading on slab was found below 42 psf. On 18-Feb-2024: This issue was corrected from previous inspection. | 6-months | Corrected
Initial Inspection |  | 6 | Discrepancies between structural drawings and as built structure | As built structural drawings to be generated/updated for all buildings on factory complex. As built drawings to account for structural framing as observed on site. | Done | Mar 10 2016 | During DEA verification inspection, some discrepancy was observed between as built condition and drawing. The factory has revised the drawing which has been accepted by Accord. On 16.10.2017: Corrected from previous inspection. On 18-Aug-2019: A set of as-built drawing has been prepared along with DEA which was accepted on 5th August 2015. Issue remains corrected. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. As-built drawings along with DEA was accepted by Accord on 5th Aug 2015. Issue remains corrected. On 18-Feb-2024: This issue was corrected from previous inspection. | 6-months | Corrected
Initial Inspection |  | 7 | Discrepancies between structural drawings and as built structure | As built drawings to be revised, as necessary, as future modifications are made to the building. Any strengthening works, as required, to be included on the as built drawings. | Done | Feb 10 2016 | During DEA verification inspection, some discrepancy was observed between as built condition and drawing. The factory has revised the drawing which has been accepted by Accord. On 16.10.2017: Corrected from previous inspection. On 18-Aug-2019: A set of as-built drawing has been prepared along with DEA which was accepted on 5th August 2015. As per accepted DEA, no remediation work is required. Issue remains corrected. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. On 18-Feb-2024: This issue was corrected from previous inspection. | 6-months | Corrected
Initial Inspection |  | 8 | Minor hairline cracks observed in structural elements | Building Engineer to identify areas of structural cracking throughout building. | We have ingaged consultant M/s Shaheedullah & New Associates Ltd. to repair cracks | Feb 28 2016 | During DEA verification inspection, it was observed that the cracks have been repaired by the factory management. On 16.10.2017: Corrected from previous inspection. No cracks observed during inspection On 18-Aug-2019: Cracks were repaired already. During a walk through session, cracks were found at facade wall which had been repaired. Factory has provided crack investigation report which declared that cracks were non-structural. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. Cracks were repaired. As per crack investigation report, cracks were non-structural. On 18-Feb-2024: This issue was corrected from previous inspection. During inspection, no cracks were observed. As per crack investigation report, cracks were non-structural. | 6-months | Corrected
Initial Inspection |  | 9 | Minor hairline cracks observed in structural elements | Building Engineer to continue to monitor size, length and location of structural cracking throughout. | We have ingaged consultant M/s Shaheedullah & New Associates Ltd. to repair cracks | Feb 28 2016 | During DEA verification inspection, it was observed that the cracks have been repaired by the factory management. It is advised that the management monitor the appearance of cracks. On 16.10.2017: Corrected from previous inspection. No cracks observed during inspection On 18-Aug-2019: Cracks were repaired already. During a walk through session, cracks were found at facade wall which had been repaired. Factory has provided crack investigation report which declared that cracks were non-structural. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. Cracks were repaired. As per crack investigation report, cracks were non-structural. On 18-Feb-2024: This issue was corrected from previous inspection. During inspection, no cracks were observed. As per crack investigation report, cracks were non-structural. | 6-months | Corrected
Initial Inspection |  | 10 | Future vertical extension | Prior to future extension commencing, Building Engineer to verify column capacities exceed future design loading, accounting for actual loading throughout existing building. Loading plans to be updated as required. | Done | Feb 18 2016 | DEA report, load plan has been prepared by factory considering that no vertical extension will be done. DEA has been accepted by Accord. On 16.10.2017: Corrected from previous inspection. Factory management submitted a letter stating that no vertical extension will be done in future. On 18-Aug-2019: Issue was found corrected from previous follow up inspection. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. No vertical extension was commenced. Currently the building is four storied. On 18-Feb-2024: This issue was corrected from previous inspection. The building was found 4 storied. | 6-months | Corrected
Initial Inspection |  | 11 | Non-engineered structures | Building Engineer to review the adequacy of non-engineered structures throughout complex. Particular attention should be paid to the stability of these structures and the holding down connection details. | DEA Approved on 5/8/2015 by ACCORD. We have engaged consultant M/s Shaheedullah & New Associates Ltd. to construct & Complete retrofitting works of Non-engineered structures. | Feb 28 2016 | Adequacy and stability of non-engineered structures throughout complex has been covered in DEA. DEA has been accepted by Accord. On 16.10.2017: Corrected from previous inspection. On 18-Aug-2019: DEA was accepted on 5th Aug 2015. As per accepted DEA, no remediation work is required. Issue remains corrected. Issue remains corrected. On 19-Jun-2022: This issue was corrected in previous follow-up inspection. No remediation work was required as per accepted DEA. On 18-Feb-2024: This issue was corrected from previous inspection. DEA of the was accepted from ACCORD on 5th Aug 2015. As per recommendation of DEA factory has completed all remedial works for Building 1 (Penthouse roof shed) and Building 2 (Utility & dinning roof shed). | 6-months | Corrected
Follow Up Inspection |  | 12 | New Finding-1: Stagnant water on rooftop. | Drainage system is required to be investigated, Apply waterproofing with sufficient slope. | Already applied waterproofing with sufficient slope. | Jul 31 2022 | On 19-Jun-2022: Stagnant water was observed on rooftop. Drainage system is required to be investigated, factory authority is required to apply waterproofing with sufficient slope. On 18-Feb-2024: Drainage system was found improved by the factory. No water stagnant was observed on rooftop. | (within 6 weeks) | Corrected

## Fire
Date
03-Jan-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.M Design Ltd., Dia khali , Beron, Zirabo , Ashulia,Savar,Dhaka, Savar, Dhaka
Date of Inspection |  | 2014-05-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boiler room on the eastern end of the site was not separated form the discharge path of the north eastern exit by means of fire-rated construction (unprotected openings and non rated door). | Separate the boiler room from the working areas and egress routes by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Done | Jun 10 2016 | On 22/08/2016: In progress. Proper fire separation has not been observed for boiler room. On 31/10/2016: Corrected. Boiler room has been located far away from exit discharge path. On 02-01-17: Corrected. Boiler room has been located far away from exit discharge path. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3months | Corrected
Initial Inspection |  | 2 | The dedicated storage areas on the 1st floor(Bonded warehouse)and ground floor(Finished goods area)were not separated by fire-rated construction (unprotected openings and non rated doors). | Provide dedicated storage rooms separated by minimum1-hr fire-rated construction. | Done | Jun 10 2016 | On 22/08/2016: Partially corrected. The factory has installed fire doors in storage area. But during follow-up inspection fire door has been found remaining open. The factory has informed that they will install automatic door closer interfacing with FACP system. On 31/10/2016: Corrected. Door holding device has been installed on Fire door. On 02-01-17: Corrected as per last follow-up inspection. Note that, Door closer is found missing in ground floor. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3months | Corrected
Initial Inspection |  | 3 | All exits are open on all floors due to unprotected openings(doors were present but fire rating could not be verified). | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors areself-closing and positivelatching and that they areprovided with fire exit (panic)hardware where servingproduction floors.If fire doors are required to beheld open for functionalreasons, provide automatic-closing devices tied to the firealarm system. | Done | Jun 10 2016 | On 22/08/2016: In progress. The factory has installed fire doors and installation of automatic door closer interfacing with FACP system is going on. Door coordinator has been found missing in double leaf-door. The factory has opened L/C for the required door coordinator. On 31/10/2016: Fire door installation has been completed and door coordinator device is missing on southwest exit stair case. On 02-01-17: Fire door installation has been completed as per last follow-up inspection. Few doors are found damaged and 2 door leaf are found missing due to damage. The factory has opened LC for replacing those damaged fire doors. LC has been opened for door coordinator device. On 06-04-17: Action has been taken but not finished yet. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in enclosures of the southern and north western exit stairs. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Done | Jun 10 2016 | On 22/08/2016: It was found same as it was before. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. Sealed. On 03/06/2018: Refer to issue 27. On 13/01/2019: Refer to issue 27. | Within 3months | Corrected
Initial Inspection |  | 5 | The discharge path to the assembly point from the north eastern exit is less than 10 ft wide andis not separated fromthe building interior(unprotected opening and non rated doors). | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way. | Done | May 10 2016 | On 22/08/2016: Partially corrected. Still few openings have been observed. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 6 | Egress doors / gates with locking features are provided at all building exits on the ground floor. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Apr 19 2016 | On 22/08/2016: Corrected. Non-compliant locking feature has not been observed during follow-up inspection. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | The combined exitcapacity of all the stairs(575 persons) is notadequate for theoccupant loads on the2nd and 3rd floors (678and 686 persons). | Reduce occupant load to not more than available exit capacity (575 persons). If possible add new exit stairs in the future to increase capacity. | Done | Feb 18 2016 | On 22/08/2016: Corrected. Occupant load has been reduced by the factory. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected based on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Sliding doors areprovided at the allbuilding exits on theground floor. | Replace all gates / sliding doors along the means of egress with side-hinged,swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Feb 18 2016 | On 22/08/2016: Corrected. Non-compliant gate has not been observed during follow-up inspection. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 1month | Corrected
Initial Inspection |  | 9 | The width of secondary discharge path from the dining area is less than 36-in. | Provide minimum path widths of 36-in. | Done | May 18 2016 | On 22/08/2016: Corrected. Mentioned exit discharge path has not been used by the factory and they have provided another exit instead of mentioned exit. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3months | Corrected
Initial Inspection |  | 10 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Installation Complete.Testing & Commissioning documents is ready for submission. | Jun 10 2016 | On 25/07/2017: Completed. Factory has installed automatic fire alarm system according to Accord reviewed drawing/design. During inspection the system's performance testing and commissioning has been done and the system was found performed well. On 03/06/2018: Corrected based on previous follow up. As built design shall be updated and proper, interfacing shall working properly, power extender shall be listed and specification shall support FACP, voltage drop and battery calculation shall be proper, device addressing shall be marked and matched with as built design, spacing and coverage shall be as per standard, audibility shall be sufficiently increased, MCP shall activate sounders as per standard. System shall completely comply with NFPA 72. On 13/01/2019: Old panels have been replaced with new one. Remediation of the identified shortcomings is in progress. On 08/03/2022: Approved. For details follow the full T&C report. On 25-Mar-2024: Corrected on last T&CVI. During the inspection system has been found functional, magnetic door holder has been found interfaced with FADS however FACP was unable to identify the pre alarm from initiating devices. Factory shall ensure that maintenance of the system has been done periodically. | Within 9months | Corrected
Initial Inspection |  | 11 | The building is equipped with single-stationsmoke alarms. Smokealarm activation soundsonly a local alarm anddoes not provideautomatic fire alarmnotification ofoccupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the building, tied into the fire alarm system, in accordance with NFPA 72. | Done | Jun 10 2016 | On 22/08/2016: It is an integrated part of fire alarm system On 31/10/2016: Partially corrected. Pending for testing and commissioning. On 02-01-17: Partially corrected. Pending for testing and commissioning. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Not removed yet. Refer to issue 25. On 13/01/2019: Not removed yet. On 25-Mar-2024: Corrected. Not found. | Within 1month | Corrected
Initial Inspection |  | 12 | Inspection, testing, andmaintenance of the firealarm system is not inaccordance with NFPA72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Done | Jun 10 2016 | On 22/08/2016: It is an integrated part of fire alarm system. On 31/10/2016: Corrected. Factory is maintaining as per Accord standard for their existing system. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3months | Corrected
Initial Inspection |  | 13 | Exit sign not provided at exit points of the north western and north eastern stair wells. | Provide exit signs above all exits to the exterior and all doors to the exit stairs. | Done | Feb 18 2016 | On 22/08/2016: Corrected. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 1month | Corrected
Initial Inspection |  | 14 | Inspection, testing, and maintenance records for the emergency lighting were not in accordance to the ACCORD standards. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Done | Apr 19 2016 | On 22/08/2016: Corrected. The factory has maintained a checklist for emergency lighting system as per ACCORD standard.\ On 31/10/2016: Corrected. Factory is maintaining as per Accord standard for their existing system. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3months | Corrected
Follow Up Inspection |  | 15 | New finding (1st Follow-up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: In all the floor of factory building. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Factory increased some emergency lights in 1st floor and in the ground floor along with increased the illumination by changing light to higher watts. | May 10 2016 | On 22/08/2016: Corrected. Adequate illumination for emergency lighting system has been observed during follow-up inspection. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Issue re open. Emergency light has been found inadequate on 1st Floor. RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1month | Pending Verification
Follow Up Inspection |  | 16 | New finding (1st Follow-up): Manual on-off switch is provided for emergency lights in all the staircases. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Done | Feb 18 2016 | On 22/08/2016: Corrected. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 1month | Corrected
Follow Up Inspection |  | 17 | New finding (1st Follow-up): The width of aisle is less than 36 inch. In ground floor finishing area. | Provide minimum 36 inch clearance for the aisles with proper marking at ground floor and keep the aisles free from the storage materials. | Factory removed excess garments from the ground floor finishing area and kept ailses clear. | Feb 18 2016 | On 22/08/2016: Corrected. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Re-opened as aisles not provided in some areas and some aisles found blocked by storage at ground floor. In other floors some aisles found obstructed by building column and worker have to work in the aisles. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Issue Re-opened as aisles with clear width of 36 inch not provided in some areas (Jhut Godown). RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1month | Pending Verification
Follow Up Inspection |  | 18 | New finding (1st Follow-up): A compressor is installed in the production floor without fire rated separation on the North-East corner of the main factory building. | Relocate the compressor or separate the compressor area with minimum 2-hrs fire resistive rated construction and door. | Done | Feb 18 2016 | On 22/08/2016: Corrected . On 31/10/2016: Corrected. On 02-01-17: Corrected as per last follow-up inspection. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3 month | Corrected
Follow Up Inspection |  | 19 | New finding (1st Follow-up): Time section, combustible materials, IPS, and pumps are stored and installed in the south-west staircase and Combustible materials are stored in the egress paths on the 1st floor of the main factory building. | Remove all the combustible materials from the noted locations and keep all the staircases and egress paths from any kind of stored materials. | Done | Apr 28 2016 | On 22/08/2016: Partially corrected. The factory has removed all storage except water pump. On 31/10/2016: Corrected. Time section has been shifted to another location. On 02-01-17: Corrected as per last follow-up inspection. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Re-opened as combustible storage is observed in stair, aisles, exit access corridor, egress paths. On 13/01/2019: Corrected. On 25-Mar-2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 20 | New finding (1st Follow-up): RMS room located in the south side main egress path is not separated by fire rated construction (openings, non rated door etc.). | Separate the RMS room by 2-hr. fire rated constrcution. Seal all penetrations and openings to maintain required fire separation. | Done | Jun 10 2016 | On 22/08/2016: In progress. RMS room has been found not separated with newly constructed fire pump room. On 31/10/2016: Corrected. RMS room has been located far away from production building. On 02-01-17: Corrected. RMS room has been located far away from production building. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. Not applicable. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 3 month | Corrected
Follow Up Inspection |  | 21 | New finding (1st Follow-up): The existing factory building has an occupiable floor greater than 10 m (33 ft) and is not provided with standpipe system as per NFPA14. | Provide a standpipe system throughout the building in accordance with NFPA 14. | Factory already completed the installation of standpipe system throughout the building accordance with NFPA 14. Waiting for T&C procedure. | Jun 18 2016 | On 03/06/2018: Re-opened as non listed standpipe system with non listed fire pump set is installed as well as system is not installed as per NFPA 14 and NFPA 20. On 13/01/2019: Construction for new fire pump room and reservoir has been started in a new place. On 23/03/2020: Pending T&CVI Documents submission. On 8/03/2022: Approved. For details follow the full T&C report. On 25-Mar-2024: Corrected. | Design within 2 months, installation within 4 months | Corrected
Follow Up Inspection |  | 22 | New Finding (4th Follow Up): Areas used for in-process storage of combustible materials are open to the surrounding occupancy | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Factory rearranged the combustible materials and also kept as per guideline. | Oct 22 2016 | On 22/08/2016: New Finding On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. On 03/06/2018: Re-opened as open storage area is observed throughout the ground floor. On 13/01/2019: Area for in process storage has not been found according to standard on 1st floor. On 25-Mar-2024: Same as previous follow up. RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 23 | New Finding (4th Follow Up): Building did not have occupant load signs at required locations. | Provide occupant load signs at required locations. | Done | Aug 29 2016 | On 22/08/2016: New Finding. On 31/10/2016: Corrected. On 02-01-17: Corrected. On 06-04-17: Corrected. On 25/07/2017: Corrected. Some modifications are still required. On 03/06/2018: Corrected based on previous follow ups. Appropriate occupant load sign shall be provided at all stairs. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 24 | New Finding: Directional signs are not provided where direction of the path of travel to an exit has change. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | Done | Feb 2 2017 | On 06-04-17: In progress. On 25/07/2017: Corrected. On 03/06/2018: Corrected as on previous follow ups. On 13/01/2019: Corrected as on previous follow ups. On 25-Mar-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding: The fire pump room is not provided with adequate fire separation. | Provide fire pump room with 2 hr rated fire separation when not sprinklered and 1 hr rated fire separation when provided with automatic sprinklers, in accordance with NFPA 20. | Done | Aug 3 2018 | On 15/08/2018 the factory is asking timeline till 15/10/2018, which is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 13/01/2019: Corrected. Separation has been provided. On 25-Mar-2024: Corrected. | Within 2 months | Corrected
Follow Up Inspection |  | 26 | New Finding: Smoke seal is not provided at any fire door and door interfacing is not working properly. | Provide proper smoke seal, interface all fire doors with FACP and ensure it work properly. | Done | Jul 3 2018 | On 15/08/2018 the factory is asking timeline till 31/08/2018, which is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 13/01/2019: Corrected. On 25-Mar-2024: Corrected. Note: Factory shall ensure that smoke seal has been installed properly on each fire rated door. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New Finding: Electrical distribution board installation within the stair enclosures wall violates the rating requirements of stair separation wall. | Re-install the distribution boards at the surface of stair enclosure walls after filling the gaps to maintain the required wall width and fire separations. | Factory fixed the stair separation by build the brick wall with the surface of the distribution board. | Jul 3 2018 | On 15/08/2018 the factory is asking timeline till 31/08/2018, which is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 13/01/2019: Rectification done only on ground floor but not on the upper floors. On 25-Mar-2024: Progress has been observed but not corrected yet. Electrical Distribution Board has been separated from stair enclosure by 5 inch RCC wall on all floor except Ground floor where separation has not been ensured yet. Factory shall complete the separation work immediately. RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 28 | New Finding: Dead-end distance exceeds 15 m (50 ft) limit at 1st floor office area. | Reconfigure the egress arrangement to reduce the maximum dead-end distance to not more than 15 m (50 ft) in accordance with ACCORD standard 6.13.3. | Done | Jul 3 2018 | On 15/08/2018 the factory is asking timeline till 31/08/2018, which is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 13/01/2019: Corrected. On 25-Mar-2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 29 | New Finding (11th FUI): The dedicated storage areas on the 1st floor were not separated by fire-rated construction (3 inch brickwall has been constructed). | Provide dedicated storage rooms separated by minimum1-hr fire-rated construction. | Separation ensured by build 5 inch brick wall. | Apr 25 2024 | On 25-Mar-2024: New Finding. RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 30 | New Finding (11th FUI): Unsealed penetrations and openings due to PVC pipes of toilet block are located in the fire rated floor/ceiling assemblies. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | Sealing work is completed. | Apr 25 2024 | On 25-Mar-2024: New Finding. RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 31 | New Finding (11th FUI): Fire door accessories (door coordinators, door closer) in various location have been found non-functional so fire separation is not being maintained. Locations: Stair 1,2 and 3 of main production building. | Factory shall ensure that the maintenance work shall be done for the door hardware and accessories on a regular basis as per NFPA 80 and manufacturer's published guideline. Repair/ replace the hardware and accessories which are not functional or under unauthorized maintenance. Doors shall not be tied up with rope or blocked by obstacles. Keep the fire rated doors close all time, if for functional reason require to keep open then interfacing facility with functional FACP shall be ensured. | Maintenance work was done for all the fire doors, and will do the maintenace regularly. | Apr 25 2024 | On 25-Mar-2024: New Finding. RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 32 | New Finding (11th FUI): Non compliant stair is provided for FACP Room. | Provide the stair in accordance to RSC Technical Guidelines (Standard) Section 6.5.6.2 & 6.9 | Fully Compliant stair ensured by some minor reparing of existing stair. | Apr 25 2024 | On 25-Mar-2024: New Finding. RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification

## Electrical
Date
03-Jan-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.M Design Ltd., Dia khali , Beron, Zirabo , Ashulia,Savar,Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2014-05-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Cables dropping from OH line are not supported. | Steel or PVC conduit must be installed for the cable support to prevent damages and stress to the cables. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 12 Weeks | Corrected
Initial Inspection |  | 2 | Cables terminating to the distribution boards are not supported. | Steel or PVC conduit or cable tray must be installed for the cable support to prevent damages and stress to the cables. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 12 Weeks | Corrected
Initial Inspection |  | 3 | The cable entry/ exit point is not sealed. | Make circular hole at the top plate of panels and provide cable gland according to the respective cable size for cable entry and exit. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 3 Weeks | Corrected
Initial Inspection |  | 4 | Cable passing through wall is not protected. | Cables passing through permanent walls must be protected in steel pipes and remaining holes around the pipe must be sealed. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 12 Weeks | Corrected
Initial Inspection |  | 5 | Excessive lint and dust deposit in cable duct. | Remove lint and dust from the cable duct and cover it with non-combustible material; make a periodical cleaning program. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 12 Weeks | Corrected
Initial Inspection |  | 6 | Panel doors not connected with earth bond. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 3 Weeks | Corrected
Initial Inspection |  | 7 | Cables are laid on concrete floor without mechanical guard. | Install cable tray with metallic cover to provide mechanical support to cables laid haphazardly on the floor. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 3 Weeks | Corrected
Initial Inspection |  | 8 | Multiple cables terminating to MCCB in panel. | Multiple cables connecting at a MCCB terminal must be removed. Individual circuit breaker must be used for each load according to the respective cable-size. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 3 Weeks | Corrected
Initial Inspection |  | 9 | Barrier/separators between different phases of MCCB are not installed. | Install graded separators between different phases of MCCB. | Done | Apr 30 2015 | Already corrected at first follow-up inspection and found same at 3rd follow-up inspection. | Within 3 Weeks | Corrected
Initial Inspection |  | 10 | Flexible PVC conduit wiring is not supported. | Use steel pipe or PVC pipe (not flexible) or cable tray to support the cables. | Done | Apr 30 2015 | Already corrected at second follow-up inspection and found same at 3rd follow-up inspection. | Within 12 Weeks | Corrected
Follow Up Inspection |  | 11 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Done | May 31 2016 | On 19/04/2016: The design is acknowledged. However, the drawing is not as-built. New timeline has been given till May 31, 2016 to complete the task. On 22/08/2016: Not corrected On 31/10/2016: Corrected On 13/01/2019: All floor level newly installed BBT information shall be included. All circuit shall have proper identification as per circuit directory. Circuit identification shall be made in such a way that it can specify circuit location, and can make adequate discrimination from other circuits. Means of identification may be done by providing separate color coding, marking tape, tagging, or other approved means. | Within 3 Months | Corrected
Follow Up Inspection |  | 12 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Done | May 31 2016 | On 18/02/2016: Already corrected at second follow-up inspection. On 13/01/2019: OCPD shall be sized as per load. | Within 2 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Earth busbar size is inadequate/undersize in panel. | Used adequate earth busbar to be rated to safely conduct the maximum fault current of phase to ground fault with negligible voltage drop. | Done | Mar 31 2016 | On 18/02/2016: This issue is not corrected. New timeline to resolve the issue is 31-03-16. On 19/04/2016: This issue is corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Done | Mar 31 2016 | On 18/02/2016: This issue is not corrected. New timeline to resolve the issue is 31-03-16. On 19/04/2016: This issue is corrected. | Within 2 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Wiring has done using flexible PVC cable around vertical boiler surface. | Wires close/attached to boiler must be protected from external heat. In unavoidable case use metal type flexible pipe. Again Power cable should keep 0.9 m apart from hot area. | Done | Apr 30 2015 | Already corrected at second follow-up inspection and found same at 3rd follow-up inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Lightning Protection System (LPS) has not installed yet. | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | Done | Mar 31 2016 | On 18/02/2016: This issue is not corrected. New timeline to resolve the issue is 31-03-16. On 19/04/2016: Not corrected. On 22/08/2016: Not corrected. Some area is still unprotected lightning protection system. On 31/10/2016: Corrected. | Within 3 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Thermographic scanning of the entire electrical system has not been tested and recorded. | Thermographic scanning for the entire electrical system must be performed on a bi-annual basis and recorded. | Done | Dec 30 2015 | Already corrected at second follow-up inspection and found same at 3rd follow-up inspection. Last thermo graphic inspection was done on November 11, 2016. | Within 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding: Insulation resistance test of electrical equipment is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Done | Dec 30 2015 | Already corrected at second follow-up inspection and found same at 3rd follow-up inspection. Last insulation resistance test was done on November 13, 2016. | Within 2 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Earth pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Done | Dec 30 2015 | Already corrected at second follow-up inspection and found same at 3rd follow-up inspection. Last earth resistance test was done on November 13, 2016. Need maintenance of 2 pits. | Within 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. | Done | Dec 30 2015 | Already corrected at second follow-up inspection and found same at 3rd follow-up inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Maintenance records do not detail out all the electrical equipment/ machinery. | Maintenance Manager or Safety Officer must keep accurate records and ensure that they reflect actual factory day to day operations. | Done | Dec 30 2015 | Already corrected at second follow-up inspection and found same at 3rd follow-up inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Circuit is drawn from bus bar of MDB-1 without Circuit breaker or any protective means. | For distribution board, along with the main circuit breaker all outgoing circuits shall have individual outgoing circuit breaker. | Done | May 31 2016 | On 22/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Power cable is buried in the concrete floor. | Construct a cable trench or any other means for distributing power cables. Then cover it by checkered plate. The cable shall not be directly squeezed by concrete. | Done | May 31 2016 | On 22/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Panel base plates removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. | Done | May 31 2016 | On 22/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: Multiple cables connected in the bus bar. | Each cable must be connected in the bus bar through single lugs. | Done | May 31 2016 | On 22/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals. | Done | May 31 2016 | On 22/08/2016: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Hot spots have been observed at some points. | Thermography survey must be done at least twice in a year. Hot spots must be removed as soon as possible. | Done | Sep 9 2016 | On 31/10/2016: Corrected. Hot Spots have been removed. | 2 Weeks | Corrected
Follow Up Inspection |  | 28 | New Finding: Periodicity of thermography survey is not continued. | Thermography survey must be done and recorded at least twice in a year. |  | Jan 30 2019 | On 09/10/2023: Corrected. | 15 Days | Corrected
Follow Up Inspection |  | 29 | New Finding: Individual protection is not provided for machines such as Sewing and Manual Cutter exceeding 0.376 kW rating. | Every electric motor having a rating exceeding 0.376 kW shall be provided with individual control equipment incorporating means of protection against overcurrent. | Every electric motor having a rating exceeding 0.376 kW, and for those we installed a single phase MCB as individual control equipment incorporating means of protection against over current. | Dec 12 2023 | 18/02/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 30 | New Finding: Combustible material attached with cable channels/BBTs. | Cable channels/BBTs must be free from combustible material. | We removed all kind of combustible materials which was attached with the BBTs. | Nov 12 2023 | On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | All manually operated machines are connected with earth connection. | Feb 22 2024 | RPO Comments on 15-DEC-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 01/06/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Large exhaust fans are controlled directly by circuit breakers. | Induction motor-driven fans, which have high inrush current, should not be operated directly using an MCB (Miniature Circuit Breaker). Instead, a Direct-On-Line (DoL) type control switch must be used. | We have installed latching (ON-OFF) circuit for large exhaust fans control panel. | Aug 1 2025 | RPO Comments on 30-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 21/12/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Protective device is not installed/adjusted per load demand. | Protective devices must be installed or adjusted according to the connected load current. If adjustment is not feasible, replacement is necessary. Each motor load exceeding 376 W requires separate protection, adhering to nameplate data for selecting the appropriate protective device. | We have adjusted 10Nos MCCB and replaced 5 Nos MCB | Aug 1 2025 | RPO Comments on 30-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 21/12/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Lightning Protection System (LPS) is not maintained properly. Issues include missing air terminals, inaccessible earthing pits, calculation/risk index missing for some structures etc. | Regularly scheduled maintenance procedures must be conducted to ensure the continued effectiveness and reliability of the Lightning Protection System (LPS), preserving its ability to protect against lightning strikes. | We have completed repair & Installation of the missing air terminals. The Earthing pits are now accessible and Calculation/risk index for all missing structures are now ready. | Sep 1 2025 | RPO Comments on 30-Oct-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 21/12/2025: Corrected. | 3 Months | Corrected

## Boiler
Date
03-Jan-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.M Design Ltd., Dia khali , Beron, Zirabo , Ashulia,Savar,Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2022-02-14
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 7012 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Emergency stop push switches has been installed on the boiler control panel and outside of the boiler room near the entrance door. | Aug 21 2025 | Comments on 06-Aug-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 7012 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have consulted with our local boiler Supplier. The Low Low Water Level (LLWL) will be marked beside the gauge glass with there cosultation. | Aug 21 2025 | Comments on 06-Aug-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 3 | BB 7012 | Necessary technical documents (Piping & Instrumentation diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of boiler. | We have consulted with our local boiler supplier. And communicated with boiler menufecturer Hurst Boiler & Welding Co. Inc. (USA) for manufacturing drawings & calculations, , electrical wiring diagram. And the Supplier will provide Piping & Instrumentation diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report with there cosultation. Boiler operational & maintenance logbook has been kept by boiler operator. | Aug 21 2025 | Comments on 06-Aug-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 4 | BB 7012 | Boiler Safety Valve outlet line is not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support & drainage system. | Boiler Safety Valve outlet line has been directed outside of the boiler room with proper support & drainage system. | Aug 21 2025 | Comments on 06-Aug-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 7012 | Steam line connection is not terminated properly. | Any unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator(s). | All unprotective steam line has been terminated in an appropriate manner that does not create any possibility of burn hazard for the operators. | Aug 21 2025 | Comments on 06-Aug-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 7012 | Boiler steam pipelines were found with improper insulation. | Proper insulation to boiler steam pipelines shall be provided. | Proper insulation to boiler steam pipelines has been provided. | Jul 21 2025 | Comments on 06-Aug-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 7012 | Inconsistency was observed between the nameplate data & the CIoB provided certificate copy for the boiler evaporation capacity. | Information provided in the nameplate and in the CIoB provided certificate shall be consistent. Any alteration shall be approved from the CIoB and a copy to be preserved on site. | We communicated with CIoB and applied for amendment of CIoB provided certificate as per manufacturer the nameplate. | Jul 21 2025 | Comments on 5-May-2025: The remediation timeline is over and the factory management did not give any updated timeline. The remediation work shall be done following provided guidelines and applicable standard within 4-Sep-2025 | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 8 | BB 7012 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | All fuel line openings in boiler room has been sealed off with a bond plug to prevent fuel leakage. | Jul 6 2025 | Comments on 06-Aug-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 7012 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - should be provided. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder - that does not pose fall hazard - will be provided. Construction in progress . | Aug 21 2025 | Comments on 06-Aug-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 7012 | The water level gauge glass was not protected. | The water level gauge glass should be properly protected with guard rods or covered by suitable protection housing. | We have consulted with our local boiler supplier. The water level gauge glass will be properly protected with guard rods or covered by suitable protection housing with their cosultation.. | Aug 21 2025 | Comments on 06-Aug-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 11 | BB 7012 | Steam leakage was observed in the boiler water gauge glass globe valve. | The steam leakage shall be repaired to prevent burn hazard. | The steam leakage has been repaired immediately to prevent burn hazard. | Jul 21 2025 | Comments on 06-Aug-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 12 | BB 7012 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We have already collected quotation from the suppliers. Waiting for approval by our top management. | Jul 21 2025 | Comments on 5-May-2025: The remediation timeline is over and the factory management did not give any updated timeline. The remediation work shall be done following provided guidelines and applicable standard within 4-Sep-2025 | 1 MONTH | In Progress