## Structural
Date
29-Jul-2023 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Dragon Sweaters Bangladesh Ltd, 25/2 Dit Road, Malibagh, Chowdhury Para, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2013-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Verify concrete strengths in all columns | Maintain current use of the floors and don´t change use or increase occupation, either of which could increase loading. | Corrected : Received Status Corrected from Accord team in 3rd followup report. | Mar 22 2016 | On 22/03/2016: On All floor uses are same as it was found in time of initial inspection. On 23/10/2017: Corrected in previous follow-up. Floor usage was observed as per drawing posted in stair. On 18/02/2018: Corrected in previous follow-up. Floor usage was observed as per drawing posted in stair. On 13/09/2018: This issue was corrected from previous inspection. Load plan was produced as part of DEA and accepted from ACCORD on 4th February 2018. During inspection load plan was found posted and load was observed below 42psf. On 02/10/2018: Corrected in previous follow up inspection. Before retrofitting load plan was found posted to each floor and loading was observed below 42 psf. On 16/04/2019: This issue was corrected as per 1st follow up inspection. On 23-Sep-2019: This issue is corrected in 1s follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. During inspection floor usage was found below 42 psf. On 26-Aug-2021: Corrected from previous inspection. During inspection live load was found below 42 psf at every floor as per accepted load plan. On 04-Jan-2022: Corrected previously. During inspection, live load was found below the accepted load limit (42 psf for all floor plates & 63 psf for dining and prayer room). On 28-Jul-2022: This issue was corrected from previous inspection. During inspection live load was found below 42 psf at every floor as per accepted load plan. On 12-Oct-2022: Corrected previously. Loading was found below the accepted load plan (2kPa/42psf) on all floors. | Immediate | Corrected
Initial Inspection |  | 2 | Verify concrete strengths in all columns | Factory Engineer to review design, loads and columns stresses for all floors. | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22/03/2016: DEA report was submitted to ACCORD, where some documents were missing such as as-built structural drawings, Before and after load plan, scan report etc. All documents must be submitted within final time line. On 23/10/2017: Core location was observed but unable to verify as DEA is not accepted. Re-submission of DEA is required. . The date of last submission was 27-Sep-2017. Review mail was sent on 16-Oct-2017. On 18/02/2018: The DEA was accepted from ACCORD on 04-feb-2018. Core test location was observed. Original core test report was found during inspection. On 13/09/2018: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. Core test location was observed. Original core test report was found during inspection On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. DEA was reviewed and accepted from Accord on 4th Feb 2018. On 26-Aug-2021: Corrected from previous inspection. DEA of this factory was reviewed and accepted from Accord on 4th Feb 2018. On 04-Jan-2022: Corrected previously. Factory has got DEA acceptance from ACCORD on 04-Feb-2018. On 28-Jul-2022: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. On 12-Oct-2022: Corrected previously. DEA of the factory has been accepted from ACCORD on 04-feb-2018. | Immediate | Corrected
Initial Inspection |  | 3 | Verify concrete strengths in all columns | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22-Mar-16: No load plan has been produced or implemented. It must be produced and submitted to the ACCORD within 06/04/2016. On 23-Oct-17: Re-submission of DEA is required. . The date of last submission was 27-Sep-2017. Review mail was sent on 16-Oct-2017. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. Load plan had been produced as part of DEA. During inspection, before retrofitting load plan was observed. On 13/09/2018: This issue was corrected from previous inspection. Load plan was produced as part of DEA and accepted from ACCORD on 4th February 2018. During inspection before retrofitting load plan was found posted and load was observed below 42psf. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. As per DEA recommendation retrofitting works were started. During inspection before retrofitting load plan was found posted to each floor and loading was observed below 42 psf. So, factory is required to maintain before retrofitting load plan till the completion of retrofitting work. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. Load plan was produced as part of DEA which was accepted from ACCORD on 04/02/2018. However, load was found below 2 kPa on all floors. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. Load was produced and accepted as a part of DEA. During inspection live load was found below 42 psf at every floor level. On 26-Aug-2021: Corrected from previous inspection. Live load plan had been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and live load was found below 42 psf as per accepted load plan. On 04-Jan-2022: Corrected previously. Load plan was produced as part of DEA which was accepted by ACCORD on 04-Feb-2018. Load plan was found posted on each floor during inspection & live load was found below the accepted load limit (42 psf for all floor plates & 63 psf for dining and prayer room). On 28-Jul-2022: This issue was corrected from previous inspection. Live load plan had been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and live load was found below 42 psf as per accepted load plan. On 12-Oct-2022: Corrected previously. DEA of the factory accepted and the load plan has been produced. Load plan found posted on every floor and loading was found below the load plan (2kPa/42psf). | Within 4 months | Corrected
Initial Inspection |  | 4 | Verify concrete strengths in all columns | A Detail Engineering Assessment of Factory to be commenced, see attached Scope | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22-Mar-16: DEA report was submitted to ACCORD, where some documents were missing such as as-built structural drawings, Before and after load plan, scan report etc. All documents must be submitted within final time line. On 23/10/2017: Re-submission of DEA is required. The date of last submission was 27/09/2017. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. On 13-Sept-2018: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. DEA of the factory was accepted from ACCORD on 04/02/2018. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. DEA was reviewed and accepted from Accord on 4th Feb 2018. On 26-Aug-2021: Corrected from previous inspection. DEA of this factory was reviewed and accepted from Accord on 4th Feb 2018. On 04-Jan-2022: Corrected previously. Factory has got DEA acceptance from ACCORD on 04-Feb-2018. On 28-Jul-2022: This issue was corrected as per 3rd follow up inspection. The DEA was accepted from ACCORD on 04-feb-2018. On 12-Oct-2022: Corrected previously. DEA of the factory has been accepted from ACCORD on 04-feb-2018. | Within 4 months | Corrected
Initial Inspection |  | 5 | Verify concrete strengths in all columns | Detail Engineering Assessment to be completed. | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22-Mar-16: DEA report was submitted to ACCORD, where some documents were missing such as as-built structural drawings, Before and after load plan, scan report etc. All documents must be submitted within final time line. On 23-Oct-17: Re-submission of DEA is required. The date of last submission was 27-Sep-2017. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. According to DEA recommendation, retrofitting is required for some columns. On 13/09/2018: This issue was corrected from previous inspection. As per DEA recommendation, some column need to be retrofitted. During inspection remedial work was found just started, where remediation timeline was 4th July 2018. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. As per DEA recommendation retrofitting works were required to be completed within 04/07/2018 but during inspection retrofitting works were found just started. See item no-16. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. DEA of the factory was accepted from ACCORD on 04/02/2018. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. DEA was reviewed and accepted from Accord on 4th Feb 2018. On 26-Aug-2021: Corrected from previous inspection. DEA of this factory was reviewed and accepted from Accord on 4th Feb 2018. On 04-Jan-2022: Corrected previously. Factory has got DEA acceptance from ACCORD on 04-Feb-2018. On 28-Jul-2022: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. As per DEA recommendation retrofitting was found completed. On 12-Oct-2022: Corrected previously. The DEA of the factory has been accepted. As per the accepted DEA, all the retrofitting works have been completed. | Within 6 months | Corrected
Initial Inspection |  | 6 | Verify concrete strengths in all columns | Continue to implement load plan. | Completed : For your kind information Already we have completed 100%Retrofitting work . Also note that, We have designated load monitoring manager who is full time engaged in load management to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans.we have posted floor load plan & maintain register about it. | Apr 21 2016 | On 22-Mar-16: No load plan has been produced or implemented. It must be produced and submitted to the ACCORD within 06/04/2016. It must implemented after being reviewed by ACCORD. On 23-Oct-17: Load plan will be produced as part of DEA. Re-submission of DEA is required. . The date of last submission was 27-Sep-2017. On 18/02/2018: The DEA was accepted from ACCORD on 04-feb-2018. According to DEA recommendation, retrofitting is required for some columns. Factory was maintaining the before retrofitting load plan. Final load plan can be implemented after completion of the retrofitting work. On 13/09/2018: Load plan was produced as part of DEA and accepted from ACCORD on 4th February 2018. During inspection before retrofitting load plan was found posted and load was observed below 42psf. During inspection remedial work was found just started. Final load plan can be implemented after completion of the retrofitting work. On 02/10/2018: Factory management got DEA acceptance on 04/02/2018. As per DEA recommendation retrofitting works were required to be completed within 04/07/2018 but during inspection retrofitting works were found just started. During inspection before retrofitting load plan was found posted to each floor and loading was observed below 42 psf. So, factory is required to maintain before retrofitting load plan till the completion of retrofitting work. On 16/04/2019: DEA of the factory was accepted from ACCORD on 04/02/2018. As per recommendation of accepted DEA, factory building required column strengthening. Factory was required to complete all the remediation works within 04/07/2018. But till date factory has not completed retrofitting works. Factory shall follow final load plan after completing all the remediation works. However, load was found below 2 kPa on all floors. On 23-Sep-2019: DEA of the factory got accepted from Accord on 04-02-2018. As per accepted DEA, factory was required to complete retrofitting works for 7 no's footings and 126 no's columns. During inspection it was found that 5 no's footing were completed, 11 no's columns were completed, 9 no's columns were partially completed. Final timeline for retrofitting works was 4-07-2018. After completing retrofitting works factory will follow final load plan. Load was found below 42 psf. On 12-Jan-2020: During inspection live load was found below 42 psf at every floor. Final load plan is required to be maintained after completing the retrofitting works. On 26-Aug-2021: Factory has completed all retrofitting work as per accepted drawing. During inspection accepted load plan was found posted at every floor and live load was found below 42 psf as per accepted load plan. However, material test report of retrofitting works was not available during inspection. This issue is required to be finalized after confirmation of the test result of the retrofitting materials. On 04-Jan-2022: Load plan was produced as part of DEA which was accepted by ACCORD on 04-Feb-2018. Load plan was found posted on each floor during inspection & live load was found below the accepted load limit (42 psf for all floor plates & 63 psf for dining and prayer room). According to the DEA recommendation, factory has completed all kinds of retrofitting works. On 28-Jul-2022: This issue was corrected from previous inspection. Load plan was produced as part of DEA which was accepted by ACCORD on 04-Feb-2018. Load plan was found posted on each floor during inspection & live load was found below the accepted load limit (42 psf for all floor plates & 63 psf for dining and prayer room). According to the DEA recommendation, factory has completed all kinds of retrofitting works. On 12-Oct-2022: Corrected previously. DEA of the factory accepted and the load plan has been produced. Load plan found posted on every floor and loading was found below the load plan (2kPa/42psf). | Within 6 months | Corrected
Initial Inspection |  | 7 | Verify concrete strengths in all columns | Verify in situ concrete stresses either by cores or existing cylinder strength data for cores from 4 columns. | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22-Mar-16: Marks of core sampling for core test has been observed during inspection. Test reports has been submitted along with DEA report. On 23-Oct-17: Core test location was observed. Resubmission of DEA is required. . The date of last submission was 27-Sep-2017.Review mail was sent on 16-Oct-2017. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. Core test location was observed. Original core test report was found during inspection. On 13-Sept-2018: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. Core test location was observed. Original core test report was found during inspection. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. During inspection original core test report was kept onsite. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. On 26-Aug-2021: Corrected from previous inspection. Cores were taken and this issue was covered under DEA. On 04-Jan-2022: Corrected previously. Core test report was found on site which was incorporated in DEA. On 28-Jul-2022: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. Cores were taken and this issue was covered under DEA. On 12-Oct-2022: Corrected previously. | Within 6 months | Corrected
Initial Inspection |  | 8 | Stability System and Foundations | Request that Detail Engineering Assessment of Factory to be commenced and in particular Stability and foundation aspects to be investigated in detail, see attached Scope | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22-Mar-16: Foundations must be investigated in detail as a part of DEA and report be attached with DEA. On 23-Oct-17: This issue will be covered in DEA. Resubmission of DEA is required. . The date of last submission was 27-Sep-2017.Review mail was sent on 16-Oct-2017. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. This issue was covered in the DEA. On 13-Sept-2018: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. DEA of the factory was accepted from ACCORD on 04/02/2018. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. DEA was reviewed and accepted from Accord on 4th Feb 2018. On 26-Aug-2021: Corrected from previous inspection. DEA of this factory was reviewed and accepted from Accord on 4th Feb 2018. On 04-Jan-2022: Corrected previously. Factory has got DEA acceptance from ACCORD on 04-Feb-2018. On 28-Jul-2022: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. On 12-Oct-2022: Corrected previously. DEA of the factory has been accepted from ACCORD on 04-feb-2018. | Within 4 months | Corrected
Initial Inspection |  | 9 | Stability System and Foundations | Detail Engineering Assessment to be completed | Corrected | Apr 21 2016 | On 22-Mar-16: DEA report was submitted to ACCORD, where some documents were missing such as as-built structural drawings, Before and after load plan, scan report etc. All documents must be submitted within final time line. On 23-Oct-17: Re-submission of DEA is required. . The date of last submission was 27-Sep-2017.Review mail was sent on 16-Oct-2017 . On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. Core test location was observed. Original core test report was found during inspection. On 13/09/2018: This issue was corrected from previous inspection. As per DEA recommendation, some column need to be retrofitted. During inspection remedial work was found just started, where remediation timeline was 4th July 2018. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. As per DEA recommendation retrofitting works were required to be completed within 04/07/2018 but during inspection retrofitting works were found just started. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. DEA of the factory was accepted from ACCORD on 04/02/2018. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. DEA was reviewed and accepted from Accord on 4th Feb 2018. On 26-Aug-2021: Corrected from previous inspection. DEA of this factory was reviewed and accepted from Accord on 4th Feb 2018. On 04-Jan-2022: Corrected previously. Factory has got DEA acceptance from ACCORD on 04-Feb-2018. On 28-Jul-2022: This issue was corrected from previous inspection. The DEA was accepted from ACCORD on 04-feb-2018. As per DEA recommendation retrofitting was found completed. On 12-Oct-2022: Corrected previously. The DEA of the factory has been accepted. As per the accepted DEA, all the retrofitting works have been completed. | Within 6 months | Corrected
Initial Inspection |  | 10 | Stability System and Foundations | Continue to implement load plan. | Completed : For your kind information Already we have completed 100%Retrofitting work . Also note that, We have designated load monitoring manager who is full time engaged in load management to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans.we have posted floor load plan & maintain register about it. | Apr 21 2016 | On 22-Mar-16: Load plan must be implemented after getting acceptance of DEA. Meanwhile follow the instructions of initial inspection report. On 23-Oct-17: Load plan will be produced as part of DEA. Re-submission of DEA is required. . The date of last submission was 27-Sep-2017.Review mail was sent on 16-Oct-2017. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. According to DEA recommendation, retrofitting is required for some columns. Factory was maintaining the before retrofitting load plan. Final load plan can be implemented after completion of the retrofitting work. On 13-Sept-2018: Load plan was produced as part of DEA and accepted from ACCORD on 4th February 2018. During inspection before retrofitting load plan was found posted and load was observed below 42psf. During inspection remedial work was found just started. Final load plan can be implemented after completion of the retrofitting work. On 02/10/2018: Factory management got DEA acceptance on 04/02/2018. As per DEA recommendation retrofitting works were required to be completed within 04/07/2018 but during inspection retrofitting works were found just started. During inspection before retrofitting load plan was found posted to each floor and loading was observed below 42 psf. So, factory is required to maintain before retrofitting load plan till the completion of retrofitting work. On 16/04/2019: DEA of the factory was accepted from ACCORD on 04/02/2018. As per recommendation of accepted DEA, factory building required column strengthening. Factory was required to complete all the remediation works within 04/07/2018. But till date factory has not completed retrofitting works. Factory shall follow final load plan after completing all the remediation works. However, load was found below 2 kPa on all floors. On 23-Sep-2019: DEA of the factory got accepted from Accord on 04-02-2018. As per accepted DEA, factory was required to complete retrofitting works for 7 no's footings and 126 no's columns. During inspection it was found that 5 no's footing were completed, 11 no's columns were completed, 9 no's columns were partially completed. Final timeline for retrofitting works was 4-07-2018. After completing retrofitting works factory will follow final load plan. Load was found below 42 psf. On 12-Jan-2020: During inspection live load was found below 42 psf at every floor. Final load plan is required to be maintained after completing the retrofitting works. On 26-Aug-2021: Factory has completed all retrofitting work as per accepted drawing. During inspection accepted load plan was found posted at every floor and live load was found below 42 psf as per accepted load plan. However, material test report of retrofitting works was not available during inspection. This issue is required to be finalized after confirmation of the test result of the retrofitting materials. On 04-Jan-2022: Load plan was produced as part of DEA which was accepted by ACCORD on 04-Feb-2018. Load plan was found posted on each floor during inspection & live load was found below the accepted load limit (42 psf for all floor plates & 63 psf for dining and prayer room). According to the DEA recommendation, factory has completed all kinds of retrofitting works. On 28-Jul-2022: This issue was corrected from previous inspection. Load plan was produced as part of DEA which was accepted by ACCORD on 04-Feb-2018. Load plan was found posted on each floor during inspection & live load was found below the accepted load limit (42 psf for all floor plates & 63 psf for dining and prayer room). According to the DEA recommendation, factory has completed all kinds of retrofitting works. On 12-Oct-2022: Corrected previously. DEA of the factory accepted and the load plan has been produced. Load plan found posted on every floor and loading was found below the load plan (2kPa/42psf). | Within 6 months | Corrected
Initial Inspection |  | 11 | Cracks in façade and parapets. Loose façade elements can fall onto the street. | Building engineer to check and make a proposal for façade repair of cracks in north top corner and on parapets. | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22/03/2016: Cracks have been found repaired but no documents regarding crack repair method or statement was available at time of inspection. On 23/10/2017: Most of the cracks were found repaired. Some cracks were still observed during inspection. No crack repair procedure document or crack investigation report was found during inspection. On 18/02/2018: The DEA was accepted from ACCORD on 04-feb-2018. According to DEA report, the cracks are non-structural. Most cracks were found repaired. Factory is required to monitor the cracks in case of further occurrence. On 13/09/2018: This issue was corrected from previous inspection. According to DEA report, the cracks are non-structural. During inspection, cracks were found repaired. Factory is required to monitor the cracks in case of further occurrence. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. During inspection, cracks were found repaired. and a crack investigation report also provided where cracks were recommended as non-structural. Factory is required to monitor the cracks in a regular manner. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. DEA of the factory was accepted from ACCORD on 04/02/2018. According to DEA report, the cracks are non-structural. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. No crack was found. On 12-Jan-2020: Corrected from previous inspection. As per accepted DEA all cracks are non structural. On 26-Aug-2021: Corrected from previous inspection. Assessment of crack was covered in DEA report and as per the assessment all cracks in facade are declared as non structural by the consultant. On 04-Jan-2022: Corrected previously. This issue was included in DEA & according to DEA report, the cracks are non-structural. No crack was observed during inspection. Factory is required to monitor the cracks in case of further occurrence. On 28-Jul-2022: This issue was corrected from previous inspection. No crack was observed during inspection. Factory is required to monitor the cracks in case of further occurrence. On 12-Oct-2022: Corrected previously. Crack was not observed during the inspection. The factory is required to monitor the cracks in case of further occurrence. | Within 6 months | Corrected
Initial Inspection |  | 12 | Cracks in façade and parapets. Loose façade elements can fall onto the street. | Building engineer to provide a method statement for the on-going maintenance of the external elevations. | Corrected : Received Status Corrected From last followup report on dated 18 Feb-2018. | Apr 21 2016 | On 22-Mar-16: Cracks have been found repaired but no documents regarding crack repair method or statement was available at time of inspection. On 23-Oct-17: Most of the cracks were found repaired. Some cracks were still observed during inspection. No crack repair procedure document or crack investigation report was found during inspection. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. According to DEA report, the cracks are non-structural. Most cracks were found repaired. Factory is required to monitor the cracks for further occurrence. On 13-Sept-2018: This issue was corrected from previous inspection. According to DEA report, the cracks are non-structural. During inspection, cracks were found repaired. Factory is required to monitor the cracks in case of further occurrence. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. During inspection, cracks were found repaired. and a crack investigation report also provided where cracks were recommended as non-structural. Factory is required to monitor the cracks in a regular manner. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. DEA of the factory was accepted from ACCORD on 04/02/2018. According to DEA report, the cracks are non-structural. During inspection, cracks were found repaired. Factory is required to monitor cracks in a regularly. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. As per accepted DEA all cracks are non structural. On 26-Aug-2021: Corrected from previous inspection. Assessment of crack was covered in DEA report and as per the assessment all cracks in facade are declared as non structural by the consultant. On 04-Jan-2022: Corrected previously. This issue was included in DEA & according to DEA report, the cracks are non-structural. No crack was observed during inspection. Factory is required to monitor the cracks in case of further occurrence. On 28-Jul-2022: This issue was corrected from previous inspection. This issue was included in DEA & according to DEA report, the cracks are non-structural. No crack was observed during inspection. Factory is required to monitor the cracks in case of further occurrence. On 12-Oct-2022: Corrected previously. Crack was not observed during the inspection. The factory is required to monitor the cracks in case of further occurrence. | Within 6 months | Corrected
Initial Inspection |  | 13 | Structural drawings do not match current arrangement of the structure | Building engineer to check, collect information and produce accurate and complete as-built documentation soonest | Corrected | Apr 21 2016 | On 22-Mar-16: Cracks have been found repaired but no documents regarding crack repair method or statement was available at time of inspection. On 23-Oct-17: As-built drawings will be produced as art of DEA. Re-submission of DEA is required. The date of last submission was 27-Sep-2017. Review mail was sent on 16-Oct-2017. No crack repair procedure document or crack investigation report was found during inspection. On 18-Feb-2018: The DEA was accepted from ACCORD on 04-feb-2018. No mismatch was found during inspection. On 13-Sept-2018: This issue was corrected from previous inspection. As-built drawing was produced as part of DEA and accepted from ACCORD on 4th February 2018. During verification inspection on 18th February 2018, no mismatch was found in between as built drawing and onsite condition. On 02/10/2018: Corrected in previous follow up inspection. Factory management got DEA acceptance on 04/02/2018. Mismatch was not found in between as built drawing and onsite condition. On 16/04/2019: This issue was corrected as per 3rd follow up inspection. As-built drawings were prepared as part of DEA which was accepted from ACCORD on 04/02/2018. On 23-Sep-2019: This issue is corrected in 3rd follow-up inspection. On 12-Jan-2020: Corrected from previous inspection. As-built drawings were prepared as part of DEA. On 26-Aug-2021: Corrected from previous inspection. As-built drawing was produced and accepted from Accord on 04/02/2018 as a part of DEA which was verified on 16th April 2019 during a verification inspection. On 04-Jan-2022: Corrected previously. As-built drawing was found on-site during inspection. On 28-Jul-2022: This issue was corrected from previous inspection. As-built drawing was produced and accepted from Accord on 04-Feb-2018. On 12-Oct-2022: Corrected previously. As built drawings were prepared as part of DEA. | Within 6 months | Corrected
Initial Inspection |  | 14 | Water accumulation and leaking with potential to cause corrosion and lasting damage to roof slab | Leaks in water tanks to be repaired. | Corrected | Apr 21 2016 | On 22-Mar-16: No sign of repair work and water leakage was not found. On 23-Oct-17: water ponding was found in some part of roof top during inspection. Repairing work is going on. Tile placing work is going on as water proofing in roof top. On 18-Feb-2018: Water ponding was observed. Tile placing works is not completed for all area. On 13-Sept-2018: During inspection, water ponding was found on rooftop. Dampness was found on roof floor. Water proofing works was not completed. Factory is required to complete water proofing work and repair all dampness effected area on roof floor. On 02/10/2018: During inspection, water ponding was found on rooftop. Water proofing works was not completed. Factory is required to complete water proofing work. On 16/04/2019: During inspection, water ponding was found on rooftop. Factory is required to provide proper water proofing on rooftop. On 23-Sep-2019: Water ponding was found on rooftop. Factory is required to take remedial action. On 12-Jan-2020: Plastic water tanks have been removed from the roof and any leakage was not found in the RC water reservoir. As per previous comments, water ponding was found on the roof. The factory is required to develop drainage system on the room storage. On 26-Aug-2021: Factory has relocated all plastic water tank from which the water was leaking previously. On 04-Jan-2022: Corrected previously. No plastic tank was found during inspection. On 28-Jul-2022: This issue was corrected from previous inspection. Factory has relocated all plastic water tank from which the water was leaking previously. On 12-Oct-2022: Corrected previously. The factory has relocated the plastic water tanks. | Within 6 months | Corrected
Follow Up Inspection |  | 15 | New Finding-1: Crack was observed on ground floor column at Grid I-6. | Engage a consultant to thoroughly investigate the crack and produced investigation report along with the repair methodology | Corrected | Sep 22 2018 | On 13-Sept-2018: During inspection, crack was found on ground floor at grid I-6. Factory is required to investigate the crack and do needful as required. On 02/10/2018: Factory management had involved a consultant to repair the cracked column. During inspection props were found installed as per crack investigation report but repairmen work wasn't started. On 16/04/2019: Factory has started retrofitting works for the column. As per recommendation of crack investigation report factory required to complete retrofitting of the column up to 3rd floor. During inspection the remediation works were found up to 1st floor. On 23-Sep-2019: No investigation report was found. Factory has started retrofitting works to this column. As per accepted drawing, retrofitting was required up to 7th floor roof. Retrofitting was found completed up to 3rd floor roof. On 12-Jan-2020: As per accepted DEA and crack investigation report this column was required to be retrofitting up to 7th floor roof but factory has completed retrofitting up to 5th floor. Factory is required to complete the retrofitting of the column up to 7th floor drawing. On 26-Aug-2021: Factory has completed retrofitting work in that cracked column as per accepted retrofitting drawing. On 04-Jan-2022: Corrected previously. No crack was observed in the ground floor column (at grid I6). On 28-Jul-2022: This issue was corrected from previous inspection. Factory has completed retrofitting work in that cracked column as per accepted retrofitting drawing. On 12-Oct-2022: Corrected previously. The factory has retrofitted the column as per the accepted retrofitting drawing. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 16 | New Finding-2: Column to be over stressed under normal limit. | Remediation is required to be applied as per DEA recommendation | Completed but Pending Verification: For your kind information Already we have completed 100%Retrofitting work . We will submit all test report very soon. | Nov 17 2018 | On 02/10/2018: Factory management got DEA acceptance on 04/02/2018. As per DEA recommendation retrofitting works were required to be completed within 04/07/2018 but during inspection retrofitting works were found just started. So factory is required to complete the remedial work as soon as possible. On 16/04/2019: During inspection, retrofitting works were found on going. As per recommendation of accepted DEA, factory building required column strengthening. Factory was required to complete all the remediation works within 04/07/2018. But till date factory has not completed all the retrofitting works. On 23-Sep-2019: Factory has started retrofitting works to this column. As per accepted drawing, retrofitting was required up to 7th floor roof. Retrofitting was found completed up to 3rd floor roof. On 12-Jan-2020: As per accepted DEA factory was required to complete all retrofitting works within 4th July 2018 but during inspection retrofitting work was found on going and factory has completed approximately 30% of the retrofitting works. Factory is required complete all retrofitting works. submitted. On 26-Aug-2021: Factory has completed all retrofitting works as per accepted retrofitting drawing. However, material test report of retrofitting work was not available during inspection. Factory is required to prepare material test report (both concrete & rebar) of the retrofitting work. On 04-Jan-2022: This issue was covered by DEA which was accepted by ACCORD on 04-Jul-2018. According to the DEA recommendation, factory has completed all kinds of retrofitting works but the strength of the materials of retrofitting works not verified till the date of inspection. Factory is required to prepare material test report (both concrete & rebar) of the retrofitting work. On 28-Jul-2022: Factory has completed all retrofitting works as per accepted retrofitting drawing. However, material test report of retrofitting work was not available during inspection. Factory is required to prepare material test report (both concrete & rebar) of the retrofitting work. On 12-Oct-2022: No action has been taken yet. The factory is required to prepare material test report (both concrete & rebar) of the retrofitting work. | (Immediate – Now) | In Progress
Follow Up Inspection |  | 17 | New Finding-3: Water ponding on 17th floor and roof slab | Improve drainage system to prevent water clogging | We are working toImprove drainage system to prevent water clogging. | Oct 15 2021 | On 26-Aug-2021: During inspection water ponding was found on 17th floor and roof slab. Factory is required to improve drainage system to prevent water clogging. On 04-Jan-2022: Factory has taken proper measure on 17th floor and roof slab to avoid water ponding. But during inspection, on 16th floor water clogging was observed. Factory is required to improve drainage system to prevent water clogging. On 28-Jul-2022: During inspection no water clogging was observed at roof floor. Factory has taken proper measure regarding this issue. On 12-Oct-2022: Corrected previously. Roof drainage system was observed as improved. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 18 | New Finding-4: Corrosion on steel stair at roof level | Replace corroded members and provide rust proof paint on steel members | We will do this as per your guideline. | Oct 15 2021 | On 26-Aug-2021: During inspection corrosion was found on steel stair at roof level. Factory is required to replace the corroded members and provide rust proof paint on steel members. On 04-Jan-2022: Till the date of inspection factory did not take any action regarding this issue. Factory is required to replace the corroded members and provide rust proof paint on steel members. On 28-Jul-2022: Factory has provided extra steel member to steel stair as a support, also provided rust proof paint on steel member. On 12-Oct-2022: Corrected previously. rust proofing applied to the steel stairs. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 19 | New Finding-5: Dampness observed at Ground floor column & adjacent beam (Grid- K-6) | Factory Engineer is required to investigate the reason and to take proper remedial actions. | In Progress | Feb 25 2022 | .On 04-Jan-2022: During inspection, dampness was observed on the ground floor column and beam at grid -K6. Factory is required to investigate the reason and to take proper measure to repair the dampness. On 28-Jul-2022: During inspection, no dampness was observed on the ground floor column and beam at grid -K6. Factory has repaired the dampness area by providing new plaster at column and beam. On 12-Oct-2022: Corrected previously. The factory has repaired the damped area. However regular monitoring is required in the specific area. | (within 6 weeks) | Corrected

## Fire
Date
29-Jul-2023 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Dragon Sweaters Bangladesh Ltd, 25/2 Dit Road, Malibagh, Chowdhury Para, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2013-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The main exit stair and rear exit stair are separated from the work areas, and other spaces, on each floor by non-fire-rated construction. The stairs open directly into areas used for storage on some floors. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system | Completed but Pending Verification: Already we have installed 2 hour rated fire door to safe the exit rout. In basement floor where the cargo lift open we also install fire rated door. . After finishing installation of fire alarm system we will provided automatic-closing devices tied to the fire alarm system.During this time We ensure that the door is closed all time. | Apr 30 2016 | On 10/03/2020: The factory has installed fire-rated doors but still unsealed penetrations were observed due to sanitary pipe and electric cable. Fire doors were kept open without using any automatic hold open devices. On 26/08/2021: In progress, Remediation work on going through the entire site.Remediation work must be completed as per recommended timeline. On 04.01.2022: No progressive action has been taken since last follow up inspection. Installed fire doors were opened through external sources. On 12/10/2022: Fire door coordinators, door closer, Positive latching system, magnetic door holders in various location have been found non-functional & Few fire doors were observed kept opened by unauthorized manner also interfacing with FADS have not been found functional. So, fire separation is not being maintained. | Within 3 months | Pending Verification
Initial Inspection |  | 2 | The main exit stair discharges inside the building on the ground floor. | Provide minimum 2-hr fire separation between the exit stair discharge lobby and all ground floor areas including the canteen, boiler and generator rooms, and utility spaces. | Corrected | Apr 30 2016 | On 07/11/2017: Corrected as per previous follow up. Note: Factory shall ensure that installed doors (boiler, generator & canteen rooms) are closed until door interface with FACP by electro-magnetic door holder device at required location. On 04/07/2018: Corrected as per previous follow up. Current condition is as it was. On 06/03/2019: Corrected as per previous follow ups. On 10/03/2020: Corrected as per previous follow ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. Note: The factory shall keep free the ground floor inside discharge area. On 12/10/2022: Corrected as per previous FUI. | Within 3 months | Corrected
Initial Inspection |  | 3 | The rear exit stair discharges inside the building at the basement. Basement areas used for combustible storage are not separated from the exit discharge path. A secondary discharge door leads directly outside at ground level; however, access away from the building is heavily obstructed by housing construction behind the building. | If feasible, utilize the exterior discharge door at ground level and provide a minimum 32-in. discharge path leading away from the building to the street. If direct exit discharge is not feasible, provide minimum 2-hr fire separation between the stair discharge path and all storage areas on the basement. Provide vestibules with minimum 1.5-hr fire doors to protect any openings in the fire separation walls. | Corrected | Apr 30 2016 | On 07/11/2017: Corrected as per previous follow up. Note: Factory shall ensure that installed doors (boiler, generator & canteen rooms) are closed until door interface with FACP by electro-magnetic door holder device at required location and egress path obstacle free. On 04/07/2018: Corrected On 06/03/2019: Refer to issue no. 33. On 10/03/2020: Corrected as per previous follow ups. Refer to isssue no.33 On 26/08/2021: Corrected as per previous follow up.Refer to issue no. 33 On 04.01.2022: Refer to issue no. 33 On 12/10/2022: Refer to the issue no-33. | Within 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in the exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected | Sep 14 2015 | On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Refer to issue no. 34 On 10/03/2020: Corrected as per previous follow ups. Refer to issue no. 34 On 26/08/2021: Corrected as per previous follow up.Refer to issue no. 34 On 04.01.2022: Refer to issue no. 34 On 12/10/2022: Refer to the issue no-34. | Within 6 months | Corrected
Initial Inspection |  | 5 | Areas used for combustible storage on production floors and are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction on all production floors where transient storage is required for operations. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4 m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Apr 3 2016 | On 07/11/2017: Corrected. During follow up inspection such storage areas (WIP) were not observed. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 6 months | Corrected
Initial Inspection |  | 6 | Unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies where the electrical service rises from floor-to-floor (behind elevators) | Provide a minimum 2-hr fire-rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation | Corrected | Sep 14 2015 | On 17/07/2017: Corrected as per last follow-up. On 07/11/2017: Corrected as per previous follow up. On 04/07/2018: Corrected On 06/03/2019: Corrected as per previous follow ups. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 6 months | Corrected
Initial Inspection |  | 7 | The boiler, generator and transformer rooms on the ground floor are not separated by fire-rated construction (openings, non-rated doors, penetrations) | Separate each of the rooms by minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Corrected | Apr 30 2016 | On 04/07/2018: Corrected On 06/03/2019: Corrected as per previous follow up. Note: Factory shall ensure that installed doors (boiler, generator & canteen rooms) are closed until door interface with FACP by electro-magnetic door holder device On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 6 months | Corrected
Initial Inspection |  | 8 | The elevator hoistway opens directly into the main exit stair enclosure. The machine room on Level 16 is not separated by fire-rated construction | Provide a minimum 2-hr fire separation of the elevator machine room from the exit stair | Corrected | Apr 30 2016 | On 17/07/2017: Corrected. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 6 months | Corrected
Initial Inspection |  | 9 | Collapsible (concertina) gates with locks are provided along means of egress, including the rear exit stair leading to the basement, along the basement stair discharge path, and at exterior exit doors. Note - all gates were open and unlocked during the inspection. | Remove all collapsible gates at exit stairs and along the means of egress. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 | Corrected | Apr 30 2016 | On 17/07/2017: Corrected. On 07/11/2017: Corrected. During follow up inspection non-compliant doors/gates were not found in egress routes. On 04/07/2018: Corrected On 06/03/2019: Refer to issue no. 35. On 10/03/2020: Corrected as per previous follow ups. Refer to issue no. 35 On 26/08/2021: Corrected as per previous follow up. Refer to issue no. 35 On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 3 months | Corrected
Initial Inspection |  | 10 | Several egress doors have locking features. While most egress doors were observed to be unlocked, a designated egress door was locked at the rear of the finishing room on Level 16. | Maintain all designated egress doors unlocked and operable at all times. Remove all non-compliant locking features from egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Apr 20 2014 | On 09-04-2017: Corrected. On 17/07/2017: Corrected. On 07/11/2017: Corrected. During follow up inspection non-compliant locking features were not found in egress routes exit doors/gates. On 04/07/2018: CorrectedOn 06/03/2019: Refer to issue no. 36. On 10/03/2020: Corrected as per previous follow ups. Refers to issue no. 36 On 26/08/2021: Corrected as per previous follow up.Refers to issue no. 36 On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 3 months | Corrected
Initial Inspection |  | 11 | The day-care room located on Level 3 does not have direct access into an exit stair | Provide a minimum 2-hr fire-rated exit corridor between the day-care room and exit stair. | Corrected | Apr 20 2014 | On 04-04-2017: Corrected. On 17/07/2017: Corrected. Relocated on ground floor. On 07/11/2017: Corrected as per last follow up. On 04/07/2018: Corrected On 06/03/2019: Refer to issue no. 37. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 6 months | Corrected
Initial Inspection |  | 12 | One of the two designated exits serving the canteen is via an exterior overhead door that has an approximate 30-in. drop-off to the outside. | Replace the overhead door with side-swinging egress doors and provide exterior steps to eliminate the drop-off. Alternatively, provide a second remotely located egress door for the canteen by replacing the sliding door near the boiler room with side-swinging egress doors and appropriate signage. | Corrected | Apr 20 2014 | On 17/07/2017: Corrected. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow-up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 6 months | Corrected
Initial Inspection |  | 13 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | In Progress: Activation of Fire Alarm is automically triggered by Smoke alarms as recommended. 55% of all works have been duly completed. The balance work is in-progress . | Jun 1 2016 | On 10/03/2020: No significant progress observed since last follow-up. On 26/08/2021: In progress; No significant progress has been noticed since the last follow-up although the factory has hired new consultants to complete the pending works. On 04.01.2022: The fire alarm and detection system installation was on-going. However, there was no significant progress observed since last follow up inspection. On 12/10/2022: No progress has been observed since last Inspection. During inspection observed conventional panel in shut off condition. | Within 3 months | In Progress
Initial Inspection |  | 14 | Activation of the fire alarm system by a manual fire alarm station provides automatic occupant notification only on the floor of alarm and not throughout the building. Activation of the fire alarm system throughout the building is capable via a manual switch in the main stair and from the main fire panel on the ground floor. | Configure the fire alarm system to initiate automatic occupant notification on all floor levels to facilitate whole-building evacuation upon any manual fire alarm station activation | In Progress: Activation of Fire Alarm is automically triggered by Smoke alarms as recommended. 55% of all works have been duly completed. The balance work is in-progress . | Jun 1 2016 | On 10/03/2020: No significant progress observed since last follow-up. On 26/08/2021: In progress; No significant progress has been noticed since the last follow-up although the factory has hired new consultants to complete the pending works. On 04.01.2022: The fire alarm and detection system installation was on-going. However, there was no significant progress observed since last follow up inspection. On 12/10/2022: No progress has been observed since last Inspection. During inspection observed conventional panel in shut off condition. | Within 3 months | In Progress
Initial Inspection |  | 15 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Replace the single-station smoke alarms with automatic smoke detectors tied into the fire alarm system. Configure the fire alarm system to initiate occupant notification upon activation of any two smoke detectors in addition to the manual fire alarm stations. | In Progress: Activation of Fire Alarm is automically triggered by Smoke alarms as recommended. 55% of all works have been duly completed. The balance work is in-progress . | Jun 1 2016 | On 10/03/2020: No significant progress observed since last follow-up. On 26/08/2021: In progress; No significant progress has been noticed since the last follow-up although the factory has hired new consultants to complete the pending works. On 04.01.2022: The fire alarm and detection system installation was on-going. However, there was no significant progress observed since last follow up inspection. On 12/10/2022: No progress has been observed since last Inspection. During inspection observed conventional panel in shut off condition. | Within 3 months | In Progress
Initial Inspection |  | 16 | The fire alarm system is not regularly tested and maintained | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72 | Corrected | Jan 4 2016 | On 07/11/2017: Corrected as per previous follow up. Factory management is maintaining and keeping existing fire alarm system maintenance records on-site. Note: Factory shall update maintenance checklist after complete new alarm system. On 04/07/2018: Corrected On 06/03/2019: Corrected as per previous follow ups. Note: Factory shall update maintenance checklist after complete new alarm system. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 12/10/2022: Corrected as per previous FUI. | Within 3 months | Corrected
Initial Inspection |  | 17 | The high-rise building is not provided with automatic sprinkler protection. The large occupant loads, heavy fuel loading, and anticipated extended egress times warrant sprinkler protection. | Provide automatic sprinkler protection throughout the building in accordance with NFPA 13. | In Progress: we have started to install of Sprinkler system & Installation work is running Level# 15,14,13,12,11,10,9,8&7 piping work has been completed for the above mentioned floors, Further, fixing of pipes are in progress . | Jun 1 2016 | On 10/03/2020: No significant progress observed since last follow-up. On 26/08/2021: No significant progress observed since last follow-up to present site condition except few pipe seen without sprinkler head. On 04.01.2022: There was no significant progress observed since last follow up inspection. On 12/10/2022: No progress has been observed since last Inspection. Till now existing non-compliant standpipe system served the factory premises. |  | In Progress
Initial Inspection |  | 18 | Emergency lighting is provided on the floors and in the exit stairs. The adequacy of the system was not fully tested; however several units did not function properly in the test mode. Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated for all floor levels along egress routes. A manual on-off switch is also provided on the emergency lighting units, several of which were observed in the off position. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. Remove the manual switches from the units to prevent them from being switched off. | Corrected | Apr 30 2016 | On 17/07/2017: Corrected as per previous follow-up. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. Note: The factory shall provide emerency light on the all underconstruction floors. On 12/10/2022: Refer to the issue no-25. | Within 6 months | Corrected
Follow Up Inspection |  | 19 | New Finding: The width of egress aisles is less than 36-inch in sixth to fifteenth floor. | Provide minimum aisle widths of 36-inch. | Corrected | Mar 30 2016 | On 17/07/2017: Corrected as per previous follow-ups. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 20 | New Finding: The exit discharge path serving rear west exit is less than 10 ft wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. | Corrected | Mar 30 2016 | On 07/11/2017: It was found same as it was last follow up. On 04/07/2018: Corrected On 06/03/2019: This issue is reflected in issue no. 33. On 10/03/2020: Refer to issue no. 33 On 26/08/2021: This issue is reflected in issue no. 33. On 04.01.2022: This issue is reflected in the issue no. 33. On 12/10/2022: Refer to the issue no-33. | Within 3 months | Corrected
Follow Up Inspection |  | 21 | New Finding: Steam line, CCTV cable located in the rear exit stairs in all floor | Remove steam line, CCTV cable from the exit stair and egress path | Corrected | Apr 30 2016 | On 17/07/2017: Corrected. On 07/11/2017: Corrected as per previous follow up. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 1 month | Corrected
Follow Up Inspection |  | 22 | New Finding: Parapets or guards are provided in occupiable roof less than 42 inch. | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | Corrected | Apr 30 2016 | On 17/07/2017: Corrected. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 3 months | Corrected
Follow Up Inspection |  | 23 | New finding ( 3rd follow up): Storage was located inthe exit stair. | Remove all storage from exitstairs and egress paths. | Corrected | Apr 30 2016 | On 04-04-2017: Corrected. On 17/07/2017: In progress. Storages (combustible finish goods, Cylinder gas) were found at exit stairs during the time of inspection. On 07/11/2017: Corrected. Factory has removed storages (LPG cylinders) from exit stair enclosure. On 04/07/2018: Corrected On 06/03/2019: Not corrected. During follow-up inspection found improper. Issue is re-opened. On 10/03/2020: Corrected. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding (6th Follow-up): Exit sign not provided at exit. Location: Secondary exit of main stair at different floors. | Lighted exit signs shall be placed at entrance to an exit. Additional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. | Complete But Pending Varefication : We placed Additional exit signs at the entrance to an exit throughout the facility where needed. Pls See the picture. | Dec 28 2016 | On 28/11/2016: New Finding On 04-04-2017: Corrected. On 17/07/2017: Corrected. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. Note: All exit sign shall be illuminated at all required places. On 12/10/2022: Issue reopened. During inspection exit signs were not illuminated at several locations. | Within 1 month | Pending Verification
Follow Up Inspection |  | 25 | New Finding (6th Follow-up): Emergency lights not illuminated during testing (burned out, broken, etc.). Location: Several places in all floors. | Regularly inspect all emergency lighting system as per Accord standard and replace/install lights as needed to illuminate signs. | Complete But Pending Varefication : Already we have replaced lights as needed to illuminate signs Sent the picture to you. And We have started to inspect all emergency lighting systems as per Accord standards and will continue it. | Dec 28 2016 | On 28/11/2016: New Finding On 04-04-2017: Corrected. On 17/07/2017: Corrected. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Issue reopened. Adequate illumination level was not observed during inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 26 | New Finding (6th Follow-up): Lighted exit signs were not provided with either battery backup or uninterruptable power supply systems. Location: North West (rear) stair exit at all floors. | Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated. | Complete But Pending Varefication :We have IPS Battery backup for exit signs and uninterruptable power supply systems which shall be continuously illuminated. | Dec 15 2016 | On 28/11/2016: New Finding On 09-04-2017: Not corrected yet. On 17/07/2017: Corrected. IPS back-up lights were provided. On 07/11/2017: Corrected as per last follow up. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Issue reopened. During inspection exit signs were not illuminated at several locations. | Immediate | Pending Verification
Follow Up Inspection |  | 27 | New Finding (6th Follow-up): Electrical panels are located inside the exit stair enclosure. Location: At 16th, 15th and 1st floor main stair . | Remove all electrical panels from exit stairs. | Corrected | Dec 28 2016 | On 28/11/2016: New Finding On 09-04-2017: Partially corrected . Electrical panel has been found in 15th floor. On 17/07/2017: Corrected. Removed. On 07/11/2017: Corrected as per last follow up. On 04/07/2018: Corrected On 06/03/2019: Corrected. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding (6th Follow-up): Fire pump room is not separated from production area by Fire rated construction. Location: Ground floor . | Fire pump room shall be separated from other occupancies by a minimum 2-hr fire rated assemblies (wall, floor, slab etc.). | Complete But Pending Varefication : For yor kind information as per our drawing pump will be positive sucktion & our water reserver in basement. our existing fire pump room is situated at ground floor. But our New fire pump will be installed at basement floor & designated place is ready for that. | Dec 28 2016 | On 06/03/2019: Remediation has not started yet. 10-Dec-2019: Time extension to complete the remediation work till 30 March 2020 are not accepted. Follow Accord recommended timeline. On 10/03/2020: No remedial action has been taken yet. On 26/08/2021: No remedial action has been taken yet as per site condition. On 04.01.2022: There was no progress observed since last follow up inspection. On 12/10/2022: No progress has been observed since last Inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 29 | New Finding (6th Follow-up): Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Complete But Pending Verification: We have started to inspect all Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Already Sent the picture to you. And will Keep written records on-site. | Dec 15 2016 | On 17/07/2017: Factory is maintaining a checklist by their own way. On 07/11/2017: Corrected. On 04/07/2018: Corrected On 06/03/2019: Maintaining. On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow up. On 04.01.2022: Corrected. On 12/10/2022: Issue reopened. During inspection observed system are not maintaining as per standard. | Immediate | Pending Verification
Follow Up Inspection |  | 30 | New Finding (7th Follow up): Penetrations through floor/ceiling assemblies are found unsealed. Location: South corner (glass wall) & ceiling. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | Complete But Pending Verification: We have sealed all penetration. For your information sprinkler pipe work and Reconstruction, works are both in progress which require regular penetrations works and we sealed it at once. | May 5 2017 | On 10/03/2020: No progress since last FUI. On 26/08/2021: No progress since last FUI.Many perforated wall has been seen as per site condition. On 04.01.2022: There was no progress observed since last follow up inspection. On 12/10/2022: During inspection penetrations through floor/ceiling assemblies were found unsealed at utility riser in west exit enclosure. | Within 1 month | Pending Verification
Follow Up Inspection |  | 31 | New Finding in 8th Follow-up: Unsealed penetrations and openings are located in the exit stair enclosures. Location: Stair-2, 16th floor. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separations. | Corrected | Aug 17 2017 | New Finding On 07/11/2017: Corrected. Sealed. On 04/07/2018: Corrected On 06/03/2019: Corrected. (Said location was found sealed.) On 10/03/2020: Corrected as per previous follow-ups. On 26/08/2021: Corrected as per previous follow-up. On 04.01.2022: Corrected. On 12/10/2022: Refer to the issue no-34. | Within 1 month | Corrected
Follow Up Inspection |  | 32 | New Finding from 10th FUI: Exits are not remotely located from each other at several floors | Modify exit arrangement or Provide additional exit(s) or Provide automatic sprinkler system throughout the building as per NFPA 13 | In Progress: we have started to install of Sprinkler system & Installation work is running Level# 15,14,13,12,11,10,9,8&7 piping work has been completed for the above mentioned floors, Further, fixing of pipes are in progress . | Sep 4 2018 | On 10/03/2020: No significant progress observed since last follow-up. On 26/08/2021: No significant progress observed since last follow-up to present site condition except few pipe seen without sprinkler head. On 04.01.2022: There was no significant progress observed since last follow up inspection. On 12/10/2022: No progress has been observed since last Inspection. | Within 2 months | In Progress
Follow Up Inspection |  | 33 | New Finding (11th Follow up): The rear exit stair discharges inside the building at the basement. Basement areas used for combustible storage are not separated from the exit discharge path. A secondary discharge door leads directly outside at ground level; however, access away from the building is heavily obstructed by housing construction behind the building. | If feasible, utilize the exterior discharge door at ground level and provide a minimum 32-in. discharge path leading away from the building to the street. If direct exit discharge is not feasible, provide minimum 2-hr fire separation between the stair discharge path and all storage areas on the basement. Provide vestibules with minimum 1.5-hr fire doors to protect any openings in the fire separation walls. | Completed but Pending Verification:Fire Door duly installed and direct exit discharge ensured leading to the street as desired. Further a 2 hour fire seperation between the stair discharge and all storage areas on the basement has been created. This has been done by constructing a 10" inch wall cordoning the staircase from the warehouse, with a 2 hour fire rated UL certified Door. (Pls see the pic file) | Apr 5 2019 | On 06/03/2019: New Finding. On 10/03/2020: Not corrected yet. Exit discharge is still unsafe and not easily accessible. On 26/08/2021: Not Corrected yet. Exit discharge is still unsafe and not easily accessible as per site condition. On 04.01.2022: There was no significant progress observed since last follow up inspection. On 12/10/2022: Exit discharge is still unsafe and not easily accessible as per site condition. | Within 1 month | Pending Verification
Follow Up Inspection |  | 34 | New Finding (11th Follow up): Unsealed penetrations and openings are located in the exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Complete But Pending Verification: We have sealed all penetration. | Apr 5 2019 | On 10/03/2020: Unsealed penetrations were observed due to sanitary pipe and electric cable. On 26/08/2021: Unsealed penetrations were observed due to the underconstruction work. On 04.01.2022: There was no progress observed since last follow up inspection. On 12/10/2022: During inspection found same as it was before. Penetrations were found unsealed at utility riser in west exit enclosure. | Within 1 month | Pending Verification
Follow Up Inspection |  | 35 | New Finding (11th Follow up): Non-compliant doors/gates were found in egress routes (exit doors/gates). Location: Basement | Remove all non-compliant doors/gates along the means of egress. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 | Corrected | Mar 8 2019 | On 06/03/2019: New Finding. On 10/03/2020: Corrected. On 26/08/2021: Corrected as per previous follow-up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Immediate | Corrected
Follow Up Inspection |  | 36 | New Finding (11th Follow up): Non-compliant locking features were not found in egress routes (exit doors/gates). Location: Basement | Maintain all designated egress doors unlocked and operable at all times. Remove all non-compliant locking features from egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Mar 8 2019 | On 06/03/2019: New Finding. On 10/03/2020: Corrected. On 26/08/2021: Corrected as per previous follow-up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Immediate | Corrected
Follow Up Inspection |  | 37 | New Finding (11th Follow up): The day-care room located on Level 3 and not having direct access into an exit stair, which does not meet ACCORD standard 3.4.2.1.1. | Day-care shall be located on the ground floor with a maximum travel distance of 9 m (30 ft), or, Located one story above level of exit discharge with direct access to an exit enclosure. | Corrected | Apr 5 2019 | On 06/03/2019: New Finding. 10-Dec-2019: Time extension to complete the remediation work till 20 Dec 2019 are not accepted. Follow Accord recommended timeline. On 10/03/2020: Corrected. On 26/08/2021: Corrected as per previous follow-up. On 04.01.2022: Corrected. On 12/10/2022: Corrected as per previous FUI. | Within 1 month | Corrected
Follow Up Inspection |  | 38 | NEW FINDING (15th FUI): Flammable liquid gas cylinder found at 15th floor kitchen area. | The storage or use of liquefied or compressed flammable gas cylinders shall be prohibited within the factory building according to RSC Technical Guidelines (Standard) 3.4.2.1.11. If factory wants to keep it then must have to follow below rules: The room within the factory building housing only gas canisters shall be enclosed in a 2-hour fire resistant, non-combustible construction, inclusive of providing fire doors and protection of all openings, penetrations & ducts to maintain the 2-hour fire resistance / fire separation. | Complete But Pending Verification: We stopped at once all activities at15 floor kitchen area until we fixed the alternative way. | Nov 12 2022 | On 12/10/2022: New Finding. | Within 1 month | Pending Verification

## Electrical
Date
29-Jul-2023 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Dragon Sweaters Bangladesh Ltd, 25/2 Dit Road, Malibagh, Chowdhury Para, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2013-11-02
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The 11kV Service cable delivering power to 1000kVA power transformer is laid on concrete floor | Cable shall be drawn in trenches with protective cover or directly buried in ground. | We have made a concrete trench and buried the cable inside this. | Sep 15 2014 | Already corrected at previous follow-up inspection. | Within 6 months | Corrected
Initial Inspection |  | 2 | HT service cable bent sharply while entering HT breaker panel | Laying cable in proper trench will provide sufficient bending radius while entering HT panel. It will ease stress on the terminations. | We have made a concrete trench and buried the cable inside this. | Sep 15 2014 | Already corrected at previous follow-up inspection. | Within 6 months | Corrected
Initial Inspection |  | 3 | HT cable raiser (cable ladder) is not utilized. Cable termination is not proper. | Cable diameter is too large to take proper bend. a) Providing sufficiently deep cable trench will allow cable to climb the ladder. b) Ladder/raiser shall be provided with lamps of proper size. c) Longer Cable outer insulation (cover) should be removed to provide flexibility and reduce stress on the transformer bushing | we have placed a ladder and fixed the HT Cable properly on ground floor | Oct 12 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 4 | HT cable termination: leakage current collector bond not connected to earth directly. | The leakage current collector bond should be directly connected to the main earth strip and shall not be bonded together with other earth conductors. The joints may be done using proper splicing/jointing method | We have completed | Oct 20 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 5 | LT cable is directly connected to the bushing without cable support. This will put stress on the bushing and its oil seal. Oil leakage is seen on around the bushings which is the result of stress on oil seal. | Cable support similar to that on the HV side should be installed at a distance far enough from the transformer to allow safe bending for connections. (Optional: single cable with larger cross-sectional area may be used between transformer LV bushing to LV breaker). | We have placed a cable support with ladder to allow safe bending for connections | Aug 24 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 6 | LV breaker is directly mounted on the wall without protective covers | 1250A, LV MCCB shall be installed with enclosure and phase bearer on both load and line sides. (Suggest that the MCCB be replaced with LV breaker with O/C, E/F, Overload, Under voltage facilities). | We have placed a enclosure to protect the MCCB | Oct 20 2014 | Already corrected at previous follow-up inspection. | Within 6 months | Corrected
Initial Inspection |  | 7 | LV cables connecting to LV MCCB is not firmly fixed. The cables are not armored and shall be protected from possible mechanical damage. | a) Cable shall be terminated (through the enclosure panel base/gland plate) to reduce/avoid stress at the termination points). Cables shall be protected from physical damage | We have placed a ladder to lay the cable. A steel plated cover placed to protect the cable. | Aug 24 2014 | Already corrected at previous follow-up inspection. | Within 6 months | Corrected
Initial Inspection |  | 8 | The transformer/ substation room does not have enough space for operation and maintenance. Short of safe working distance in front and back of the panel as per BNBC & NFPA Code | The partition between the Transformer and HT Switchboard shall be provided with metal door (specification to be obtained as per fire safety requirement). Surroundings shall be kept clean from combustibles | We have completed | Dec 20 2015 | Already corrected at previous follow-up inspection. | Within 6 months | Corrected
Initial Inspection |  | 9 | The Cross-section of transformer earth conductor is too small and not connected directly to the main earth strip. | Transformer should be earthed independently at two different points and should be directly connected to main earth strip. It is not mandatory as per BNBC, but would be necessity | We have arranged the proper Earth connection for the transformer. | Oct 27 2014 | Already corrected at previous follow-up inspection. | Within 6 months | Corrected
Initial Inspection |  | 10 | Transformer is covered with dust and cob-webs. Including the transformer room/floor. | Shall be scheduled to clean on monthly basis, taking proper precautionary procedures. | We are cleaning regular basis and maintaining cleaning Log | Jan 14 2015 | Already corrected at previous follow-up inspection. | Regularly | Corrected
Initial Inspection |  | 11 | Oil leakages from both HT & LT bushings are seen. Leakages may deteriorate the insulation property of the oil inside transformer. | Shall schedule with necessary permission with the Utility company stop leakages and test the oil inside. The cables termination shall be rearranged with supports (see E-5). Oil level gauge is empty5. LT cables termination at the transformer indicate signs of overheating (melting insulation) | We have completed | Apr 30 2016 | On 14/07/2016: Not corrected. On 08/09/2016: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | Silica gel in Breather is mostly white in color and half filled. The moisture/dust sealing cup is not filled with transformer oil. | Silica gel in breather shall be changed and sealing cup shall be filled with transformer oil as per the filling marks provided on the equipment. | We are changed the silica gel | Oct 27 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 13 | Cables in Generator panels are terminated directly without installing cable glands. The cable gland plates are removed from the panel base. Cables run over diesel tank (one of the generators) which is very risky in case of sparks/heating in cables. | Cables terminating at generator terminals shall be protected and supported in ladder or riser. Cables on floor may be installed inside cable trench. | Used cable glands in generator panel | Jun 15 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Initial Inspection |  | 14 | Cable is run under wooden covers (fabricated wooden box) on the floor | Cables may be run in cable trenches or in cable trays with non- combustible tray covers to prevent from mechanical damages. | We have made a concrete trench replacing wooden cover and buried the cable inside this and covered that with steel plate. | Sep 15 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 15 | Boiler is under installation and yet to be commissioned. Cables are laid without proper protections. Control panel doors are not installed properly. | Cables may be run in cable trays and/or trenches. Boiler control panel may be installed, inspected and commissioned by competent person(s). | We need more time until 15.04.14 | Sep 15 2014 | Already corrected at previous follow-up inspection. | Required | Corrected
Initial Inspection |  | 16 | Electric cables and wires (Including communication cables) are run through sanitary shaft. | Electric cables, Communication cables and sanitary pipes shall be separated to avoid accidents and to prevent cables from damage. | We have separated all types of cables from sanitary pipes using steel plated box. | Oct 12 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 17 | Power cables delivering power to different floors are tied up on insulators at the floor level where connection to SDB is made, without cable supports. | Cables shall be supported on cable raiser, raceway or cable trays, to avoid mechanical stress on the cables. Covered cable tray/raiser shall be used (conduits/pipes shall be avoided as the cables are vertically drawn) to support cables. | We have fixed the steel ladder/tray to avoid the stress on the cables. | Aug 24 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 18 | Cables and wires are not supported. Cable/wire identification is not provided. Routes are not defined. | Cables/wires are installed with supports and protection. Cables/wires are drawn without specific route (hanging from every possible ways). Cable are not marked (ID/tag). | Cables installed with support (ladder) and marked as well. | Jun 7 2015 | Already corrected at previous follow-up inspection. | Dec 31 2014 | Corrected
Initial Inspection |  | 19 | Cables connecting to SDB at various floor levels are drawn though walls without supports and sealing at the entry point through the wall. | Cables shall be supported by cable trays and shall be connected to the main tray running vertical (See E-17) with proper size “Tee” and corners. The gap/space left unused after cable enter through walls shall be sealed with fire stopping materials. | Cables has given support by cable tray at the entry point | Jul 5 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Initial Inspection |  | 20 | Cable entry/exit are from the back of the panel. Cable termination is difficult and not safe for the operators. Cable insulation at the entry point is prone to damage. | Cable entry may be designed from top or bottom of the panel to allow proper fixing of cable ends with glands. Entry from bottom or top will allow proper dressing within the panel (bending & Clipping) | We are fixing the entry and exit hole of the cable with a proper gland will be finish by 15/03/2014 | Sep 2 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 21 | Panels are congested with wires/cables and switches. | Proper size panels shall be selected | We have replaced. | Sep 15 2014 | Already corrected at previous follow-up inspection. | Within 6 months | Corrected
Initial Inspection |  | 22 | Main Dist. Board and LT panels are housed in the Basement without proper cable trench/tray. The panels are not fixed/grouted firmly to the ground/floor. | Separate electrical utility shaft with firmly fixed cable tray with covers, Tee, Cross, corners and bents shall be used. All cables connecting between switch boards and major equipment shall be identified (cable tags). | We have completed that with proper stand | Sep 15 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 23 | MCCBs are mounted on wooden planks and directly on the wall without protective covers. | Distribution systems shall be redesigned to reduce concentration of switches/devices in one place. E.g., provide Main MDB in ground floor, downstream MDB in every 4-5 floors. Each floor with SDB and for high concentration load centers, provide additional Sub-SDBs | We have completed | Oct 20 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 24 | Connections in the panels are not safe: a) Multiple cables are connected on one terminal (sometimes sharing cable lug/ferrule). b) Cable terminals not provided with spring washers when bolted. c) Cables & wires are spliced and taped. d) No gland plates/cable glands. e) Not enough space between live parts and to the grounded parts. | Suggested to redesign & replace the panels. a) Every cable terminal shall be connected separately with individual lugs. b) Main cable terminals (and large cables) connected with nuts & bolts shall be provided with spring washers. c) Cables shall not be spliced or joined in between10. d) Additional panels may be provided to provide more space (replacing with larger panels may be an option). | a) Every cable connected separately with individual lugs. b) Main cable terminals (and large cables) connected with nuts c) There is no spliced or joined | Mar 4 2015 | Already corrected at previous follow-up inspection. | Dec 31 2014 | Corrected
Initial Inspection |  | 25 | Cables connecting to motors and equipment are not terminated with glands and rigid supports. | All equipment shall be connected with proper size of cable/wires and shall be firmly terminated. Cable ends should be fixed with cable glands. Cables shall be supported on riser / trays. | All equipment connected with proper size of cable/wires and firmly terminated with cable gland | Mar 4 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Initial Inspection |  | 26 | Earth connection is not continuous and earth conductors used are smaller. | Earth conductor shall complete loop from the main earth to the end equipment. Earth conductors used shall be of proper size and shall not be tapped in between. All equipment including panels shall be earthed | Finished | Sep 15 2014 | Already corrected at previous follow-up inspection. | Within 3 months | Corrected
Initial Inspection |  | 27 | General wiring in various floors used for lighting, supply to swing m/c, spinner, knitting, cutter, etc. run without standard systems. a) Cable/wires run in metal ducts are not covered and transferred to other system without proper jointing systems. b) Wirings are run haphazardly on walls, ceiling and floors. c) Various wiring systems are used in one floor or for a circuit. d) Cut (on one side) flexible PVC covers are used to cover wires and cables used for wiring | a) Metal ducts (channels) used shall have protective covers. Tee, Cross and bend shall be used when changing cable/wire route. b) Wirings shall follow dedicated and protected route on wall, floor and ceiling with proper wiring systems. It shall be chosen for safety of operators, workers and shall not be source of fire. c) Open flexible PVC conduit used to cover the bunch of wires/cables shall be replaced with cable trays/ducts | Proper wiring, covered bunch of wires by metal tray /duct | Jun 15 2015 | Already corrected at previous follow-up inspection. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 28 | New Finding: HT service cable is not protected near the base, above ground level and it is not properly supported. | HT cable shall be protected in steel pipe of required size from the ground level to protect from physical damage. | HT Cable has fixed with metal shit cover to protect | Mar 4 2015 | Already corrected at previous follow-up inspection. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 29 | New Finding: Panel doors not connected with earth bond. | All metal panel doors shall have earth connection by at least 4 rm earth cable. | Metal doors have given earth connection | Jun 7 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 30 | New Finding: Generator frame connected to only one earth point. | Generator shall be connected to earth securely at least at two points. Ensure the earthing cable size is not less than 35rm. | Earthing connection at two points has made for both generators | Oct 25 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 31 | New Finding: Machines (Boiler) are not connected with earth | Connect all the electrical machines with earth by proper sized earth type cable | Earth connection has given to all machine( boiler, pump) | Oct 25 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 32 | New Finding: Power cables entering to or exiting from Distribution board/panel are not properly fixed. | Power cables entering to or exiting from distribution board/panel shall be fixed through Panel base plate using cable glands (metal/PVC). | Completed: we did it on 20/03/2016 and Received Status Corrected from Accord team in 3rd follow-up report. | Mar 20 2016 | Already corrected at previous follow-up inspection. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 33 | New Finding: Change Over Switch contacts covered with bearing grease. | Clean the change over switch and use sufficient amount of electrical graded grease | Our electrician clean the Change over regular basis. Now they are using electric grease. | Jul 5 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 34 | New Finding: Cable duct/ channels are filled with fluffs (Lint/dust) | Clean all the cable channels/ducts; periodically. Provide cover made of non-combustible material on the channel for preventing ingress of dust and debris in future. . | Corrected: we did it on 20/03/2016 and Received Status Corrected from Accord team in 3rd follow-up report. | Mar 20 2016 | Already corrected at previous follow-up inspection. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 35 | New Finding: Battery cases are kept in wooden case. Battery terminals are filled with rust and left open. | Use non-combustible case/shelf to store battery. Clean battery terminals and Use insulated rubber cap to cover all the battery terminals | Already we replaced the wooden shelf with non combustible metal shelf to store battery | Jun 7 2015 | Already corrected at previous follow-up inspection. | Dec 15 2014 | Corrected
Follow Up Inspection |  | 36 | New Finding: Lightning protections system (LPS) is inadequate for the factory | Redesign/modify LPS for your factory to increase safety; Factory have to submit LPS design to Accord before starting | In progress: Alliance has reviewed the LPS Drawing. Now our engineers are doing the site assessment and analysis and there after installation will start. | May 30 2016 | On 14/07/2016: Not corrected. Few modification needed. On 08/09/2016: Corrected. | Feb 28 2015 | Corrected
Follow Up Inspection |  | 37 | New Finding: Inadequate working space around panels and access to the panel is inconvenient. | Ensure at least 1 meter working clearance in front each panel | Already cleared in front of panel | Jun 15 2015 | Already corrected at previous follow-up inspection. | 41973 | Corrected
Follow Up Inspection |  | 38 | New Finding: High Tension (HT) power cable is covered by sand in the cable trench | If it is designed to keep HT cable under sand, its OK; otherwise remove sand from cable trench avoiding physical damage of HT cable | Completed: we did it on 09/03/2016 and Received Status Corrected from Accord team in 3rd follow-up report. | Mar 9 2016 | Already corrected at previous follow-up inspection. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 39 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Corrected | Apr 30 2016 | On 14/07/2016: Not corrected. On 08/09/2016: Not corrected. On 28/11/2016: Not corrected. On 04/04/2017: Not Corrected. SLD is not as built. On 17/07/2017: Corrected | Feb 28 2015 | Corrected
Follow Up Inspection |  | 40 | New Finding: Transformer Oil Test report is absent. | Check the transformer oil condition by performing oil test twice in a year and keep the record in a report form. | Completed: Test done on 02/03/2016 and report received on 21/03/2016. Received Status Corrected from Accord team in 3rd follow-up report. | Mar 2 2016 | Already corrected at previous follow-up inspection. | Feb 28 2015 | Corrected
Follow Up Inspection |  | 41 | New Finding: Earth Pits are not identifiable & Earth resistance record is unavailable | Identify each earth pit and mark it for periodic maintenance purpose. All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Completed: report received on 18/03/2016. Received Status Corrected from Accord team in 3rd follow-up report. | Mar 6 2016 | Already corrected at previous follow-up inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Insulation resistance test of electrical cable is not performed | Insulation resistant test of all the cables shall be performed once every 2 year cycle and recorded (this shall require a complete power shut off) | Completed: report received on 18/03/2016. Received Status Corrected from Accord team in 3rd follow-up report. | Mar 6 2016 | Already corrected at previous follow-up inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: Thermal inspection record is unavailable. | Thermal inspection is needed to be conducted and recorded bi-annually. Record/Ask for the calibration certificate of the scanner. | Completed: report initiated on 13/03/2016. Received Status Corrected from Accord team in 3rd follow-up report. | Mar 13 2016 | Already corrected at previous follow-up inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers shall be initiated and recorded | Completed: we have started training from 09/03/2016 and completed on 10/03/2016. Received Status Corrected from Accord team in 3rd follow-up report. | Mar 10 2016 | Already corrected at previous follow-up inspection. | Within 2 Months | Corrected
Follow Up Inspection |  | 45 | New Finding: Oil spillage is seen on the floor of generator room. | Generator room should be kept neat & clean. | Completed: We have corrected earlier and Received Status Corrected from Accord team in 3rd follow-up report. | Mar 9 2016 | Already corrected at previous follow-up inspection. | Within 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Sub station room has inadequate ventilation & inadequate illumination | Ensure/Arrange cross ventilation sub station room; You may use fire damper if you have to keep any opening on the corridors/egress path/exit & Ensure adequate illumination in the sub station room thus any maintenance can be done comfortably (150 lux should be maintained) | We have completed | Apr 30 2016 | Time extension mentioned by the factory is accepted. ACCORD expects the issue to be closed as recommended within this timeline. On 14/07/2016: corrected | Within 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: (1)Distribution board/panel & Cable duct/channels are filled with fluffs (lint/dust) (2)HT cable is buried in the concrete. | (1)Keep always clean inside all the distribution boards/panels. Seal them properly and ensure adequate ventilation. (2)Clean all the cable channels/ducts; then cover them (you may use checkered/perforated plate ). But ensure that you have options for further maintenance work. (3)Remove the concrete from HT cable & provide adequate support if needed. | Completed but Pending Verification: We have clean all side of distribution boards & cable channels & also we have removed concrete from HT cable & provided adequate support. | Oct 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/10/2016. On 28/11/2016: Not corrected. On 04/04/2017: Not Corrected On 17/07/2017: Not Corrected On 07/11/2017: Not Corrected. On 04/07/2018: Not Corrected. On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. Factory has started structural renovation work. They are also working to solve this issue. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Lot of cable channels were open and full of fluffs. | 2 Months | Pending Verification
Follow Up Inspection |  | 48 | New Finding: (1)Phase barrier/ separator has not installed. (2)Power bus bar/MCCB are installed congested; and power cables touch opposite phased bus bar. | (1)Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. (2)Ensure that no power cable touches bare bus bar. Use insulated bus bar (just covering existing bus bar by heat shrink). | Completed but Pending Verification: We ensure that, no power cable touch the bus bar & use lugs properly. | Oct 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/10/2016. On 28/11/2016: Not corrected. On 04/04/2017: Not Corrected On 17/07/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: (1)Inadequate sized earth cable connected to generator & transformer frame. (2)Neutral earthing is not separated from body earthing of the electrical system. | (1)Two separate earth connection & one separate and distinct neutral connection shall be provided over generator & transformer. Earth connection shall be half of phase conductor /follow manufacturer/ suppliers recommendation. (2)Need to improve the earthing system for the whole electrical system so that neutral earthing is separated from body earthing of the electrical system. | Corrected | Oct 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/10/2016. On 28/11/2016: Not corrected. On 04/04/2017: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 50 | New Finding: Loop connection has used powering multiple MCBs/MCCBs. Earth cables are terminated at bus bar/ MCB loosely/without lugs. | (1)Eliminate loop cables; use single cable for each MCBs/MCCBs. You may use bus bar to avoid multiple termination. (2)Terminate each power cable at single terminal and use proper sized cable lug. | Completed but Pending Verification: we use properly bus bar with lugs. ( see picture in photo evidence file) | Oct 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/10/2016. On 28/11/2016: Not corrected. On 04/04/2017: Not Corrected On 17/07/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: (1)Panel/Distribution boxes are not readily accessible. (2)Cable trench cover makes obstacle in the working clearance area (around 1.07m of the equipment) | (1)Take necessary initiative thus every panel/distribution board can be easily accessible. (2)Relocate the floor mounted cable trench; or construct a slope at both side of that trench. So that trench cover cant make obstacle in the working clearance area (around 1.07m of the equipment) | We have completed | Sep 24 2016 | On 08/09/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 52 | New Finding: Electrical elements are installed without proper support/improper way. | Electrical elements shall be fixed properly & remove the combustible materials. | We have completed | Sep 24 2016 | On 08/09/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: (1)Phases are imbalanced. (2)Hot spots at terminations inside panel. Thermo graphic inspection record is unavailable. | (1)In three phase outgoing circuits all the phases shall be balanced. Calculate each phase's load and redistribute loads to make phases balanced. (2)Arrange periodic inspection & thermal scan at least twice in a year to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, quickly correct such points. | Corrected | Sep 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/09/2016. On 28/11/2016: Not corrected. On 04/04/2017: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 54 | New Finding: (1) No permanent identification found at the panel boards & instruction for CPR is absent. No/Inadequate rubber (insulation) mat on the working are of distribution board/Panel. (2) Panel/ distribution board has inadequate illumination | (1)All distribution boards shall be marked permanently, as the case may be, provided a unique ID number (e.g. MDB-1). (2)CPR instruction shall be hanged near all electrical installations (LT panel, MDB, DB, etc.) at visible location (3)Put electrical insulation (rubber mat) on the working area of each electrical installation. (4)Ensure adequate illumination in front of panel/distribution board thus any maintenance can be done comfortably (150 lux should be maintained) | Completed but Pending Verification: we marking permanently all MDB/DB/Panel /LT board properly & provide rubber mat in all electrical installation & Clean in front place.( see picture in photo evidence file) | Oct 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/10/2016. On 28/11/2016: Not corrected. On 04/04/2017: Not Corrected On 17/07/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: (1)Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize/absent. (2)Panel door has no earth connection. (3)Manually operated machines/motors have no earth connection | (1)Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). (2)All metal panel doors shall have earth connection with a 4 rm earth cable. (3)Connect and ensure all the manually operated machines/motors with earth. | Completed but Pending Verification: we have completed earthing on all machine, panel door etc..( see picture in photo evidence file) | Oct 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/10/2016. On 28/11/2016: Not corrected. On 04/04/2017: Not Corrected On 17/07/2017: Not Corrected On 07/11/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: (1)Cables are hanging without proper support. (2)Cables are laid on floor without any support. | (1)Use ladder type cable tray to support cables at any where to keep cable out of tension or arrange adequate support. (2)Provide cable tray inside cable drain and cover it by checkered plate. | We have completed | Aug 24 2016 | On 08/09/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: (1)Safety program is initiated but has no influence. (2)Uninsulated electrical tools are used for breakdown and preventive maintenance. (3)Battery terminals are left open. | (1)Electrical safety training and awareness program for the electrical personal and workers shall be conducted and recorded. After the training, there should be exam to evaluate the influence of the training program. (2)Insulate all the electrical tools used by the electricians/technicians. (3)Lead acid battery terminals shall be covered/capped. | Corrected | Oct 30 2016 | On 08/09/2016: Not corrected. Time extension is given till 30/10/2016. On 28/11/2016: Not corrected. On 04/04/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: LPS down conductors are disconnected & loose bonding found at several points. Air terminals aren't installed at desired height at some places | Missing down conductors shall be reinstalled & tightening all the bonding's shall be done as per standard. Increase air terminals height where necessary. | Completed but Pending Verification: we have reinstalled & tightening & also increase air terminals height. ( see pic in photo file) | Jan 10 2017 | On 04/04/2017: Not Corrected. On 17/07/2017: Not Corrected On 07/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. Cable trench cover makes obstacle in the working clearance area (around 1.07m of the equipment) | Each electrical distribution board/panel shall be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. Relocate the floor mounted cable trench; or construct a slope at both side of that trench. So that trench cover cant make obstacle in the working clearance area (around 1.07m of the equipment | Completed but Pending Verification: Already we have removed some DB/panel board & reinstall it acceptable Height & ensure distance from work area. ( see pic in photo file) | Jan 10 2017 | On 04/04/2017: Not Corrected On 17/07/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: (I)Power Cables are hanging without proper support. (ii)Electrical elements are installed without proper support. | (I)Power cables shall be supported by cable tray (ladder- where needed). Outdoor arrangement shall be covered. (ii)Ensure adequate support while installing electrical elements. | Completed but Pending Verification: Already we have given proper support in all electrical element. | Jan 10 2017 | On 04/04/2017: Not Corrected On 17/07/2017: Not Corrected On 07/11/2017: Not Corrected. On 04/07/2018: Not Corrected. On 04/07/2018: Not Corrected. On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. Renovation work is going on but not completed for whole factory. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Few power cables were hanging but a lot of electrical installations were not supported properly. | 1 Month | Pending Verification
Follow Up Inspection |  | 61 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct) | Heat source (or steam line) shall be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Completed but Pending Verification: we covered properly the steam line pipe by insulator. ( see pic in photo file) | Jan 10 2017 | On 04/04/2017: Not Corrected On 17/07/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Compressor frame and motor has no ECC connection, mechanical guard is missing and unfixed wheels | Provide ECC connection. Fix the compressor to the floor & arrange mechanical guard to the moving parts | Corrected | Jan 10 2017 | On 04/04/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: MCCBs are not adjusted per load demand. Cables in service are joined (splicing) between terminations & kept exposed. | All the MCCBs shall be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. Splicing in the power cables shall be avoided; in unavoidable cases splicing, shall be made following proper guidance. | Completed but Pending Verification: We adjust cable current load & avoid all splicing.( see pic in photo file) | Jan 10 2017 | On 04/04/2017: Not Corrected On 17/07/2017: Not Corrected On 07/11/2017: Not Corrected. On 04/07/2018: Not Corrected. On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. Renovation work is going on but not completed for whole factory. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Found in lot of places. No progress found. | 1 Month | Pending Verification
Follow Up Inspection |  | 64 | New Finding: Oil leakage from transformer has been observed. | Oil leakage from transformer shall be stopped and top of transformer shall also be kept clean | Corrected | Oct 1 2017 | On 04/04/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Distribution Board's top/ bottom is left open (typical issue) | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs; but an adequate ventilation system shall also be ensured. Seal the unwanted gland holes & other openings. | Completed but Pending Verification: Already we have properly sealed all of the electrical distribution board/panel to avoid ingression of fluffs. | Jan 10 2017 | On 04/04/2017: Not Corrected On 17/07/2017: Not Corrected On 07/11/2017: Not Corrected. On 04/07/2018: Not Corrected. On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. Some panels found sealed. They are working to seal the rest of the panels. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Found in few panels. Progress observed. | 1 Month | Pending Verification
Follow Up Inspection |  | 66 | New Finding: Mechanical Guard is not provided where necessary. | Arrange mechanical guard to the rotating parts. | Corrected | Jan 10 2017 | On 04/04/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Wooden support used for electrical installation/element. | Replace wooden support and it is preferable to fix each electrical devices with non-combustible support. | Corrected | Aug 30 2017 | On 07/11/2017: Corrected. That wooden support had been removed. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel shall be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | Corrected | Dec 15 2017 | On 04/07/2018: Not Corrected. On 06/03/2019: Not Corrected. On 26/08/2021: Corrected. Factory has removed such panels. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Circuit is drawn from bus bar without any protective means. Protection of circuit has been bypassed. | Each electrical circuit shall be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). Every circuit shall have protection by means of circuit breaker or fuse. Replace circuit breaker/fuse in case of faulty. | Completed but Pending Verification: We have corrected this as per requirement. | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. No progress observed. | 1 Month | Pending Verification
Follow Up Inspection |  | 70 | New Finding: Magnetic ballast found inside the cable channel/duct. | Magnetic ballast shall not be kept inside of cable channel/duct. | Corrected | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Corrected. Ballast has been removed from channel. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables shall be removed as soon as possible. | Completed but Pending Verification: Already we have checked & removed all unterminated live power cable. | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Found in production floors as there were lot of renovation work was running. | 1 Month | Pending Verification
Follow Up Inspection |  | 72 | New Finding: Lighting fitting/fixtures are not properly supported from the structure/ supporting stand(pipe/conduits, brackets fabricated from structural steel, steel chains or similar materials) | The support of lighting fitting/ fixtures shall have adequate strength to carry the weight of light fixtures. | Completed but Pending Verification: Already we have given proper support of lighting fitting. | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Found in floors in lot of places. No progress found. | 1 Month | Pending Verification
Follow Up Inspection |  | 73 | New Finding: Access to the HT switchgear is not convenient. | HT switchgear shall have easy access. High voltage equipment with exposed live parts or wiring terminal installed in a low voltage vault/room shall be effectively separated from the space occupied by low voltage equipment by a suitable partition, screen or fence. | Completed but Pending Verification: Now this area is easy accessible ( Pls see the picture file) | Aug 10 2018 | On updated CAP for the month of Sep 2018 factory asked time extension to complete the remediation work till 30 Sep 2018 but time extension are not accepted. On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. No progress observed. | 1 Month | Pending Verification
Follow Up Inspection |  | 74 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) shall have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Completed but Pending Verification: We have Completed to give manually machine earth connection. | Aug 10 2018 | On updated CAP for the month of Sep 2018 factory asked time extension to complete the remediation work till 30 Oct 2018 but time extension are not accepted. On updated CAP for the month of Oct 2018 factory asked time extension to complete the remediation work till 30 Nov 2018 but time extension are not accepted. Remediation work shall be done as per Accord given timeline. On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct) | Heat source (or steam line) shall be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Completed but Pending Verification: we have provided adequate insulator in steam line & other heat source where was missing. | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Found in few places. No progress observed. | 1 Month | Pending Verification
Follow Up Inspection |  | 76 | New Finding: Neutral identification does not match with the phase of the circuit. Circuit directory cannot specify circuit location and does not have discrimination from other circuits by naming. | All circuit shall have proper identification as per circuit directory. Circuit identification shall be made in a such a way that it can specify circuit location, and can make adequate discrimination from other circuits. Means of identification may be done by providing separate color coding, marking tape, tagging, or other approved means. | Completed but Pending Verification: we have done this issue by marking & tagging all circuit breaker & cable according to color code. | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. No progress found. | 1 Month | Pending Verification
Follow Up Inspection |  | 77 | New Finding: Floor around control panel is wet. (Typical shock hazard) | A dry platform shall be in front of panel for maintenance purpose. Panel access shall be restricted to qualified people with proper equipment(e.g. rubber boot). | Completed but Pending Verification. To ensure dry platform Cleaning work has done & we provide rubber mat in front of panel board. | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 78 | New Finding: Sub station room has inadequate illumination | Adequate illumination in the sub station room shall be ensured thus any maintenance can be done comfortably (around 150 lux) | Corrected | Aug 10 2018 | On 06/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: Transformer Silica gel is discolored | Silica gel shall be changed; or reuse can be done, if color regains after sundry. | Corrected | Aug 10 2018 | On 06/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Periodicity of Transformer Oil Test (dielectric strength test) survey is not continued. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Corrected | Aug 10 2018 | On 06/03/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Safety program is initiated but has no influence in the factory | Electrical safety training and awareness program for the electrical personal and workers shall be conducted and recorded. Training shall have an impact on the safety attitude of the personnel. | Completed but Pending Verification: Electrical safety training and awareness program for the electrical personal and workers on monthly basis is our regular practice. After 11th verification we have started this program with more effective way. | Aug 10 2018 | On 06/03/2019: Not Corrected. On 26/08/2021: Not Corrected. Safety training has no influence on the attitude of the personnel. On 04-Jan-2022: Not Corrected. No training record found during inspection. On 13/11/2022: Not Corrected. Safety personnel are not maintaining PPE during work.. No progress observed. | 1 Month | Pending Verification
Follow Up Inspection |  | 82 | New Finding: Field information has less reflection in existing SLD | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord. Electrical SLD shall be updated properly when electrical system is modified. | In Progress : For your kind information, we are changing our Factory layout and for this, we need to change the electrical diagram. Our Electric Engner working g for this.. We need some time to complete this issue. | Apr 15 2019 | On 26/08/2021: Not Corrected. They are working on it. (RCH) 03-Nov-2021: Time extension till 30 Nov 21 are not accepted. Remediation work must be completed as per recommended timeline. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. SLD is not as built. No progress observed. | 1 Month | In Progress
Follow Up Inspection |  | 83 | New Finding: i) Materials are used for LPS is not as per acknowledged Standard; iii) Air Terminals are not installed at desire height. | Factory has to redesign Lightning Protection system (LPS) for the whole premises (where necessary and the Risk index is more than 40) and install the system with appropriate materials according to the acknowledged standard. | Complete But Pending Verification: Already we change & reinstall new Materials ii) As per the acknowledged Standard, we have completed the work for Air Terminals. | Apr 15 2019 | On 26/08/2021: Not Corrected. Air terminal found missing. Metal's are not bonded. (RCH) 03-Nov-2021: Time extension till 30 Nov 21 are not accepted. Remediation work must be completed as per recommended timeline. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. Few air terminals are missing and few are broken. LPS not maintained properly. | 1 Month | Pending Verification
Follow Up Inspection |  | 84 | New Finding: Inadequate working space around transformer for performing maintenance work | Minimum working space (1.07m) around the transformer (and related electrical installations) shall be maintained | Completed but Pending Verification: Now working around space above 40 up inch in the transformer. | Apr 15 2019 | On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Not Corrected. No progress observed. | 1 Month | Pending Verification
Follow Up Inspection |  | 85 | New Finding: Hot Spots were observed at several points. | Hot spots shall be eliminated from entire electrical system and shall be always carried forward. | Completed but Pending Verification: Pls See the pic. | Apr 15 2019 | On 26/08/2021: Not Corrected. On 04-Jan-2022: Not Corrected. No report found during inspection. On 13/11/2022: Corrected. No major hotspot found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 86 | New Finding: Insulation resistance test report not covered all system. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) Shall be performed once in every 2 years’ cycle and recorded (this shall require a complete power shut off). | Completed but Pending Verification: After follow up Inspection we have done Insulation resistance test. As per auditor guideline | Apr 15 2019 | On 26/08/2021: Not Corrected. All the cables are not included in IR test report. They are working on it. On 04-Jan-2022: Not Corrected. No report found during inspection. On 13/11/2022: Not Corrected. Still some cables need to add in the report. | 1 Month | Pending Verification
Follow Up Inspection |  | 87 | New Finding: Large exhaust fans are controlled directly by MCB | Induction motor driven fans (which has high inrush current) shall not be operated directly using MCB; Direct-On-Line (DoL) type control switch shall be used. | Corrected | Apr 15 2019 | On 26/08/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 88 | New Finding: Power Cable left unprotected on floor. | Power cable shall be distributed through cable trench/ladder. Cable trench shall be covered properly. | Completed but Pending Verification: Already we have given proper support. | Apr 15 2019 | On 26/08/2021: Not Corrected. They are working on it. On 04-Jan-2022: Not Corrected. On 13/11/2022: Corrected. No such cable found during inspection. | 1 Month | Corrected