## Structural
Date
03-Feb-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.T.S. Apparels Limited, 414, Kochakuri, Talirchala,, Mouchak,Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-03-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Columns appear to be stressed in excess of normal design limits – Building Engineer to verify concrete stresses and in-situ concrete strength. | Factory Engineer to review design, loads and columns stresses. | Done | Apr 15 2017 | On 4 Aug 2016 : Core has been taken. DEA has been submitted to Alliance on 4th Feb, 2016. DEA not accepted yet On 16/10/2017:Core test has been done .DEA has been accepted by ALLIANCE on August 2 ,2017 .Core test report was found during inspection .Retrofitting works were completed . On 18-April-2018: This issue was corrected from previous inspection. DEA has been accepted from ALLIANCE on August 2 ,2017. As per accepted DEA recommendation retrofitting works were completed. On 08-May-19: Corrected from previous inspection. The DEA was accepted from ALLIANCE on 02-Aug-2017. On 20-Dec-2020: Corrected from previous follow up inspection of Accord. This issue had been covered in DEA report. Factory management got DEA re-acceptance for main building from RSC on 02-July-2020. As per accepted DEA recommendation retrofitting works were completed. On 23-Sep-2024: Corrected previously. This issue has been covered in DEA which was re-accepted from RSC on 02-July-2020 for Main Factory Building. On 03-Jul-2025: Corrected previously. | (within 6 weeks) | Corrected
Initial Inspection |  | 2 | Columns appear to be stressed in excess of normal design limits – Building Engineer to verify concrete stresses and in-situ concrete strength. | Verify in-situ concrete stresses either by 100mm diameter cores or existing cylinder strength data for cores from 4 columns. | Done | Jan 10 2015 | On 4 Aug 2016 : Core has been taken and relevant document has been incorporated in DEA. Core cutting location count be verified on site due to paint on column. On 16/10/2017:Corrected in previous follow-up inspection .Core test has been done .DEA has been accepted by ALLIANCE on August 2 ,2017 . On 18-April-2018: This issue was corrected from previous inspection. Core has been taken and relevant document has been incorporated in DEA. On 08-May-19: Corrected from previous inspection. On 20-Dec-2020: Corrected from previous follow up inspection of Accord. This issue had been covered in DEA report. Factory management got DEA re-acceptance for main building from RSC on 02-July-2020. During inspection core test reports were found kept onsite. On 23-Sep-2024: Corrected previously. Core has been taken as part of DEA which was re-accepted from RSC on 02-Jul-2020. During inspection, core test report was available. On 03-Jul-2025: Corrected previously. | (within 6 months) | Corrected
Initial Inspection |  | 3 | Columns appear to be stressed in excess of normal design limits – Building Engineer to verify concrete stresses and in-situ concrete strength. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Done | Apr 15 2017 | On 4 Aug 2016 : Load plan has been produced and incorporated in DEA. Load plan found posted and maintained accordingly. Factory is required to post approved load plan after receiving DEA approval and maintain accordingly. On 16/10/2017:Load plan is produced as a part of DEA. DEA has been accepted by ALLIANCE on August 2 ,2017.During inspection ,Load was found below 42psf .Load plan was found as posted on every floor . On 18-April-2018: This issue was corrected from previous inspection. Load plan is produced as a part of DEA. DEA has been accepted by ALLIANCE on August 2 ,2017.During inspection , load was found below 42psf . Load plan was posted on every floor. On 08-May-19: Corrected from previous inspection. The load plan was been produced as part of DEA. Load plan was found posted. Load was found below allowable limit (63 / 42 psf) On 20-Dec-2020: Corrected from previous follow up inspection of Accord. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance for main building from RSC on 02-July-2020. As per accepted DEA recommendation retrofitting works were completed. During inspection load plan was found posted to each floor & overall loading was found within the allowable accepted loading limit (max.- 63 psf for store area). On 23-Sep-2024: Corrected previously. Load plan has been prepared as part of DEA which was re-accepted from RSC on 02-Jul-2020. During inspection, load plan was found posted in each floor and loading was found within allowable limit (63 psf) of accepted load plan. On 03-Jul-2025: Corrected previously. Floor loading was found within the allowable limit of the accepted load plan (2 kPa in Part-1; 3 kPa in Part-2). | (within 6 months) | Corrected
Initial Inspection |  | 4 | Design Check required for the loading from the plastic water tanks at roof level and for the location of the fusing machine at 3rd Floor Level. | Locations of loading noted to be surveyed and capacity of floor structure to be assessed by the Building Engineer to confirm that the floor slab is designed to carry these loads. | Done | Apr 15 2017 | On 4 Aug 2016: Plastic water tank has been removed. RCC water tank has been provided as per submitted DEA. Fusing machine loading has been considered in floor loading. DEA has been submitted to Alliance and is under review. On 16/10/2017:This issue is covered in DEA .DEA has been accepted by Alliance on August 2, 2017 .Retrofitting works were completed . On 18-April-2018: This issue was corrected from previous inspection. Load plan is produced as a part of DEA. DEA has been accepted by ALLIANCE on August 2 ,2017. During inspection , load was found below 42psf . Load plan was posted on every floor. On 08-May-19: Corrected from previous inspection. The load plan was been produced as part of DEA. Load plan was found posted. Load was found below allowable limit (63 / 42 psf) On 20-Dec-2020: Corrected from previous follow up inspection of Accord. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance for main building from RSC on 02-July-2020. As per accepted DEA recommendation retrofitting works were completed. During inspection load plan was found posted to each floor & overall loading was found within the allowable accepted loading limit (max.- 63 psf for store area). On 23-Sep-2024: Corrected previously. Factory has completed all the retrofitting works as per recommendation of accepted DEA and retrofitting completion certificate was available. On 03-Jul-2025: Corrected previously. Retrofitting work was completed. Floor loading was found within the allowable limit of the accepted load plan (2 kPa in Part-1; 3 kPa in Part-2). | (within 6 months) | Corrected
Initial Inspection |  | 5 | Design Check required for the loading from the plastic water tanks at roof level and for the location of the fusing machine at 3rd Floor Level. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Done | Apr 15 2017 | On 4 Aug 2016 : Load plan has been produced and incorporated in DEA. Load plan found posted and maintained accordingly. DEA is under review in Alliance. On 16/10/2017: DEA has been accepted by ALLIANCE on August 2 ,2017. Load plan was found as posted. Load plan was produced .Load was found below 42psf .All plastic tanks have been removed. On 18-April-2018: This issue was corrected from previous inspection. Load plan is produced as a part of DEA. DEA has been accepted by ALLIANCE on August 2 ,2017.During inspection ,Load was found below 42psf . Load plan was found as posted on every floor . All plastic water tanks have been removed. On 08-May-19: Corrected from previous inspection. The load plan was been produced as part of DEA. Load plan was found posted. Load was found below allowable limit (63 / 42 psf) On 20-Dec-2020: Corrected from previous follow up inspection of Accord. Load plan had been prepared as a part of DEA. Factory management got DEA re-acceptance for main building from RSC on 02-July-2020. As per accepted DEA recommendation retrofitting works were completed. During inspection load plan was found posted to each floor & overall loading was found within the allowable accepted loading limit (max.- 63 psf for store area). On 23-Sep-2024: Corrected previously. Load plan has been prepared as part of DEA which was re-accepted from RSC on 02-Jul-2020. During inspection, load plan was found posted in each floor and loading was found within allowable limit (63 psf) of accepted load plan. On 03-Jul-2025: Corrected previously. Load plan was found posted on the floors and loading was found within the allowable limit of the accepted load plan (2 kPa in Part-1; 3 kPa in Part-2). | (within 6 months) | Corrected
Initial Inspection |  | 6 | Design check required for the single storey buildings to confirm their adequacy to support wind loading (pressure / suction and uplift) | Building Engineer to provide detailed calculations for the single storey structures and the associated light steel roofs. These should confirm their ability to withstand all wind loading pressure, suctions and uplift forces. | Revised DEA submitted to the Accord on 06th February 2020 for review. Accord reviewed the DEA on 27th February 2020 & asked for some correction & resubmit the DEA to Accord with in 8th March 2020.After completion the correction work we have re-submitted to revised DEA to Accord on 09th March 2020 & got approval from Accord on 02 July 2020. | Apr 15 2017 | On 6/10/2019 Factory asked for extended timeline till: 30/10/2019 Timeline extension request is not accepted. On 4 Aug 2016 : Single story structure has been included in DEA. DEA is submitted to Alliance and is under review now. On 16/10/2017: DEA has been accepted by ALLIANCE on August 2 ,2017 .As per DEA verification inspection ,discrepancy was observed between accepted drawing and actual as-built condition for the single storey buildings. Factory is required to update as built drawing as per actual site condition. On 18-April-2018: Factory has carried out DEA report and accepted from ALLIANCE on August 2 ,2017 .As per DEA verification inspection ,discrepancy was observed between accepted drawing and actual as-built condition for the single storey buildings. Factory is required to submit all document immediately as per DEA verification report requirement. On 08-May-19: As per CCVV inspection of ALLIANCE, factory is required to revise the DEA correcting the issues highlighted by ALLIANCE. Factory is required to submit the revised DEA with relevant drawing and documents to ACCORD for review as soon as possible. On 20-Dec-2020: Factory management got DEA acceptance from Alliance for these structures on 02-August-2017. So, this issue had been covered in DEA report. On 23-Sep-2024: Corrected previously. As built drawings of the single storied Finished Goods store, single storied Generator Building & Dining Space was accepted from ALLIANCE on 02-Aug-2017. On 03-Jul-2025: Corrected previously. | (within 6 months) | Corrected
Initial Inspection |  | 7 | Roof drainage to be assessed to remove water ponding. | Building engineer to review the roof drainage and implement an appropriate drainage system that will prevent water ponding on the roof. | Done | Sep 2 2015 | On 4 Aug 2016 : Drainage system has been improved ; slope has been provided on roof. However factory is required to monitor the drainage system regularly On 16/10/2017:Corrected from previous follow-up report. Water ponding was not observed on rooftop. On 18-April-2018: This issue was corrected from previous inspection. On 08-May-19: Corrected from previous inspection. On 20-Dec-2020: Corrected from previous follow up inspection of Accord. Water ponding was not observed on rooftop. On 23-Sep-2024: Corrected previously. During inspection, no water ponding was found on roof. On 03-Jul-2025: Corrected previously. Water ponding was not observed. | (within 6 months) | Corrected
Initial Inspection |  | 8 | It is noted that an additional to the structure is planned at the south east corner. Any proposed additions to the existing building structure should be reviewed by building engineer. | If any additions to the building structure are proposed, the building engineer shall provide caculations showing the structural adequacy of all columns taking into account any additions to the existing structure, the loading plans and as built structure, including insitu concrete strength testing. | Done | Apr 15 2017 | On 4 Aug 2016 : During inspection the south east corner structure was found under construction. Factory has incorporated the design drawings with DEA. DEA is under review in Alliance. On 16/10/2017:Factory has submitted Design ,drawing of south east corner structure with DEA .DEA has been accepted by ALLIANCE on August 2 ,2017 .As per DEA verification no discrepancy was observed for factory building. On 18-April-2018: This issue was corrected from previous inspection. On 08-May-19: Corrected from previous inspection. On 20-Dec-2020: Corrected from previous follow up inspection of Accord. No additional structure was found on the south east corner of the existing building. On 23-Sep-2024: Corrected previously. During inspection, no horizontal or vertical extension was found. On 03-Jul-2025: Corrected previously. Horizontal/vertical expansion was not observed. | (within 6 months) | Corrected
Initial Inspection |  | 9 | In consistencies between the drawings and the constructed building. | Building engineer to check, collect information and produce accurate and fully complete as-built documentation. | Done | Apr 15 2017 | On 4 Aug 2016 : As built drawings has prepared and incorporated in DEA. DEA has been submitted to Alliance on 4th Feb, 2016 and is under review now. On 16/10/2017:DEA has been accepted by ALLIANCE on August 2 ,2017 . Retrofitting works for factory building was completed . On 18-April-2018: This issue was corrected from previous inspection. On 08-May-19: Corrected from previous inspection. On 20-Dec-2020: Corrected from previous follow up inspection of Accord. As built drawings were found prepared as a part of DEA. Factory management got DEA acceptance from Alliance for these structures on 02-August-2017 and also got DEA re-acceptance for main building from RSC on 02-July-2020. On 23-Sep-2024: Corrected previously. As built drawings of Main factory building have been prepared as part of DEA which was re-accepted from RSC on 02-Jul-2020. On 03-Jul-2025: Corrected previously. | (within 6 months) | Corrected
Follow Up Inspection |  | 10 | Design check required for the vertical escape ladders on the façades. | Building Engineer to provide calculations for the design of these ladders to confirm that their load carrying capacity is adequate. Connections to the building and overall detailing also needs to be reviewed. | Done | Apr 15 2017 | On 4 Aug 2016 : During inspection no calculation has been provided for the vertical escape ladder. Factory is required to submit immediately the calculations for the design of these ladders to confirm their adequacy. On 16/10/2017: No calculation of vertical escape ladders was found during inspection . Factory authority informed that they will demolish the escape ladders . On 18-April-2018: Factory has demolish the escape ladders. On 08-May-19: Corrected from previous inspection. The escape stair was not found during inspection. On 20-Dec-2020: Corrected from previous follow up inspection of Accord. During inspection escape stair was not found . On 23-Sep-2024: Corrected previously. Factory has removed vertical escape ladders. On 03-Jul-2025: Corrected previously. Escape ladder was removed from the façades. | (within 6 months) | Corrected
Follow Up Inspection |  | 11 | Dampness found on 4th floor beam and wall | Building engineer to investigate cause of damp and carry out any necessary repairs as advised by Engineer. | Done | May 30 2018 | On 21-April-22018: Dampness on beam and wall was observed during inspection. Building engineer to investigate cause of damp and carry out any necessary repairs as advised by Engineer. On 08-May-19: Dampness was not found on the exterior wall and beam. On 20-Dec-2020: Corrected from previous follow up inspection of Accord. During inspection dampness was not found . On 23-Sep-2024: Corrected previously. During inspection, no dampness was found. On 03-Jul-2025: Corrected previously. Further dampness was not found. | (within 6 weeks) | Corrected

## Fire
Date
03-Feb-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.T.S. Apparels Limited, 414, Kochakuri, Talirchala,, Mouchak,Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-04-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Hazardous materials / flammable liquid storage area is not separated by fire-rated construction (openings, non-rated doors, penetrations). Located on the ground floor in close proximity to storage areas. | Separate the hazardous materials / flammable liquid storage room by a minimum 2- hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Done | May 12 2016 | On 22/06/16: Corrected. Fire door has been installed. Penetrations have been sealed. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected as per previous follow-up inspection. On 11/07/2017: Corrected as per previous follow-up. On 20/05/2018: Corrected On 17-12-2018: Corrected as per previous follow-up. On 30/08/2023: Corrected. | Winthin 3 months | Corrected
Initial Inspection |  | 2 | The generator / transformer outbuilding is not separated by firerated construction, both services open to each other. | Separate the generator / transformer room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Done | Dec 23 2015 | On 22/06/16: Corrected. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected as per previous follow-up inspection. On 11/07/2017: Corrected. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | The exit stairs are not separated from work areas on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | We have completed the fire door maintenance work by our internal engineering team now all fire door are fully functional.We already closed the window from stair no-2.. | May 21 2016 | On 30-03-17: Fire door installation work is in progress. All the doors are found in the factory. During inspection all the egress doors were found open. If the factory wants to keep the doors open than they have to use magnetic door holder interfaced with fire alarm control panel. On 11/07/2017: Fire door installation work is still pending at south exit stair (Stair-4). Besides installed fire doors were found open through some external sources. In that case magnetic door hold device shall be installed. South-west exit stair (stair-3) is not separated yet from toilet facilities on each floor. On 20/05/2018: Civil construction for toilet separation has been started. Doors are yet to be interfaced. On 17-12-2018: Fire door has been installed but interfacing with FACP was not working properly on 1st and ground floor. On 30/08/2023: During follow up inspection it was observed that installed fire doors with door accessories (door co-ordinator for double leaf door, panic bar, door closer, etc.) were not functional properly at exit on several floors. The North-East exit stair (Stair-2) enclosures are not separated from the building interior as per RSC Technical Guidelines (Standard) 6.3.1.3. The rating of the exterior wall shall extend 3.05 m (10 ft) beyond the ends of the stair structure. RPO Comments: On 30-Nov-2023, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 4 | Areas used for combustible storage are not separated by firerated construction. Packing and finishing areas are open to production lines on a number of floors | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Done | May 12 2016 | On 22/06/16: Dedicated storage rooms have been found on ground floor where fire doors have been installed. Still fire doors are needed for proper separation in some places. On 1st floor, packing & finishing section very few in-process storages have been found during inspection for which pile dimension area is maintaining. On 2-11-2016: At ground floor undefined storage space was found. Accessories store was unprotected with stair. On 5th January 2017 As action plan of the factory: In Progress. It has found same as it was before follow-up inspection. On 30-03-17: Corrected. No such transient storage areas have been found during the time of inspection. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Refer issue no. 21. | Within 3 months | Corrected
Initial Inspection |  | 5 | Egress doors / gates with locking features are provided at building exits, exit stairs, along egress routes, exit discharge. All gates/doors were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Dec 12 2015 | On 22/06/16: Corrected. No non complaint locking features have been found during 4th follow-up inspection. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected. On 11/07/2017: Corrected. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. During follow-up inspection non-compliant locking features not found at egress path exit doors/gates. | Immediate | Corrected
Initial Inspection |  | 6 | Collapsible gates / sliding doors are provided at building exits, exit stairs, along egress routes, exit discharge throughout all floors. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Done | Dec 12 2015 | On 23/12/2015: Corrected. After 2nd follow-up factory have sent pictures of removing non-compliant gates. On 21/04/2016: Corrected. Sliding doors has been found at dining, washing section and finishing & packing area. Factory has sent the pictures after removing sliding doors after 3rd follow up inspection. On 22/06/16: Corrected. No non complaint gates have been found during 4th follow-up inspection. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected. On 11/07/2017: Corrected. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. Replaced. | Within 1 month | Corrected
Initial Inspection |  | 7 | Inspection, testing, and maintenance for the fire alarm system were not in accordance with NFPA 72 | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Done | Mar 30 2015 | On 23/12/2015: Corrected . Factory is maintaining a checklist as per NFPA 72. On 21/04/2016: Corrected. Factory has maintained the checklist as per ACCORD standard. On 22/06/16: Corrected. Factory is maintaining checklist as per standard. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected as per previous follow-up inspection. On 11/07/2017: Corrected. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected as per previous follow-up. | Design within 6 months, install within 12 months | Corrected
Initial Inspection |  | 8 | The fire alarm system does not appear to provide adequate visual notification coverage. No strobe lighting was identified in the building. Strobes present in boiler and generator outbuildings. | Provide additional notification appliances such that the fire alarmsystem is audible throughout the building in accordance with NFPA 72. | Based on review comments from RSC on 12th December 2025 we are working on updated drawing ,design & documents. We will submit the updated documents to RSC by 15th January 2026 for review & feedback. | May 21 2016 | On 5th January 2017 As action plan of the factory: In Progress. It has found same as it was before follow-up inspection. (Factory has installed the non listed fire alarm equipment. So the (existing) installed fire alarm system is not recognized by the Accord. On 30-03-17: It is found same as it was before. On 11/07/2017: No action has been taken yet for modification work. Design reviewed by ACCORD and was available during the inspection. On 20/05/2018: Installation is underway. Cable laying work is on going. On 17-12-2018: Factory has informed that installation has been almost completed. Testing and commissioning is pending. On 10/10/2021: T&CVI found that the fire alarm and detection system was not approved. See detailed T&CVI Report. On 29/08/2022: T&CVI found that the fire alarm and detection system (FADS) is not approved. See detailed in the T&CVI report. On 30/08/2023: Fire alarm and detection system (FADS) modification work almost completed according to the factory personnel. During follow up inspection the fire alarm control panel (FACP) was not in healthy condition. The factory shall apply for T&CVI immediately after completing modification work. RPO Comments: On 01-FEB-2026 the RSC checked the FADS systems and identified anomalies. The anomalies need to be remediated and reported by 15-SEP-2025. | Within 3 months | In Progress
Initial Inspection |  | 9 | Manual on-off switch is provided for all emergency lighting / exit signage units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | We will close the unsealed penetration with in 31st December-2025. | Mar 30 2015 | On 23/12/15:: Corrected. On 21/04/16: Corrected. Manual on-off switch has not been found during 3rd follow up inspection. On 22/06/16: Corrected. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected. On 11/07/2017: Corrected. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. Removed. | Within 1 month | Corrected
Initial Inspection |  | 10 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Based on review comments from RSC on 25th August 2025 we are working on updated drawing ,design & documents. We already submittted the updated documents to RSC on 30th October 2025 & waiting for feedback. | Mar 30 2015 | On 23/12/2015: Corrected . Factory is maintaining a checklist as per Accord standard. On 21/04/2016: Corrected. Factory has maintained the checklist as per ACCORD standard. On 22/06/16: Corrected. Factory is maintaining checklist as per standard. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected. On 11/07/2017: Corrected. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected as per previous follow-up. | Within 3 months | Corrected
Follow Up Inspection |  | 11 | New finding in 1st follow up: Unsealed Penetrations and openings in all elevetor shafts are located in the fire rated floor/ celling assemblies. | Provide a minimum 2 hours fire rated shaft to separate the elevetor risers from each floor level. | Done | May 21 2016 | On 22/06/16: No action has been taken yet. On 2-11-2016: No action has been taken. On 5th January 2017 As action plan of the factory: In Progress. It has found same as it was before follow-up inspection. On 30-03-17: It is found same as it was before. On 11/07/2017: Factory has installed fire doors but magnetic door hold devices are not installed yet which shall be interfaced with FACP. On 20/05/2018: Corrected. They kept the doors closed. On 17-12-2018: Corrected On 30/08/2023: Corrected. | 3 months | Corrected
Follow Up Inspection |  | 12 | New finding in 1st follow up: Storage was located in exit stair. | Remove all storage from exit stairs and egress paths. | Done | May 4 2016 | On 21/04/2016: Fire alarm control panel, storage and pump has been found underneath of north middle exit stair (stair-1) and south west exit stair (stair-3) On 22/06/16: No action has been taken yet. On 2-11-2016: No action has been taken. On 5th January 2017 As action plan of the factory: In Progress. It has found same as it was before follow-up inspection. On 30-03-17: It is found same as it was before. On 11/07/2017: No action has been taken yet. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. Removed. | Immediate-now | Corrected
Follow Up Inspection |  | 13 | New finding in 1st follow up: The width of egress aisles is less than 36-in. | Provide minimum aisle widths of 36 -in | Done | Mar 30 2015 | On 23/12/2015: Corrected On 21/04/2016: Corrected. 36-inch has been aisles has been provided. On 22/06/16: Corrected. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: In Progress. On 30-03-17: Corrected. On 11/07/2017: Partially corrected. Found improper. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. Provided. | Immediate-now | Corrected
Follow Up Inspection |  | 14 | New finding in 1st follow up: Unsealed penetrations and opening in floors are located in the fire rated floor/ceiling assemblies. | Seal all penetrations and opening in floor/ceiling assemblies to maintain the fire separation | We will close the unsealed penetration with in 31st March-2026. | Mar 30 2015 | On 23/12/2015: Corrected . All the openings and penetrations were sealed. On 21/04/2016: Corrected. Openings and penetrations has not been found during 3rd follow up inspection. On 22/06/16: Corrected. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: In Progress. Expansion joint is not separated by fire rated construction. On 30-03-17: It is found same as it was before. On 11/07/2017: No action has been taken yet. On 20/05/2018: Same as before On 17-12-2018: Corrected. Penetration has been sealed. On 30/08/2023: Issue re-open. During follow-up inspection floor ceiling penetrations were observed throughout the building expansion joint. RPO Comments: On 01-FEB-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | With in the 3 months | In Progress
Follow Up Inspection |  | 15 | New finding in 1st follow up: Store exit discharges at staircase | Provide1.5 hr rated fire door & seal all opening & penetration | Done | Apr 21 2016 | On 23/12/2015: Corrected . Fire separation work was completed as per Accord standard. On 21/04/2016: Corrected. On 22/06/16: Corrected. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: In Progress. On 30-03-17: It is found same as it was before. On 11/07/2017: Found same as it was before. On 20/05/2018: Same as before On 17-12-2018: Corrected. Fire door has been installed for storage room and door was closed during follow up inspection. On 30/08/2023: Corrected. | With in the 3 months | Corrected
Follow Up Inspection |  | 16 | New finding in 2nd follow up: Exit capacity is not adequate for the occupant load. (5th floor). Available exit capacity- 539, existing- 622 | 1. Reduce occupant load to not more than available exit capacity (539 persons maximum) Or 2. Provide additional exits to increase exit capacity. | Done | Jan 10 2016 | On 23/12/2015: New Finding On 21/04/2016: Corrected. Factory has reduced the manpower with in the limit. On 22/06/16: Corrected. Factory has reduced the occupant to 530. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected. Reduced. On 11/07/2017: Corrected. Reduced. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. Reduced. | Immediate | Corrected
Follow Up Inspection |  | 17 | New finding in 2nd follow up: The existing factory building with an occupiable floor greater than 10 m (33 ft) above the finished grade is not protected with an approved standpipe system. Note: Reviewed design was found during follow-up inspection. (from Alliance) | Modify the existing system as per the reviewed design according to NFPA 14. | Based on review comments from RSC on 12th December 2025 we are working on updated drawing ,design & documents. We will submit the updated documents to RSC by 15th January 2026 for review & feedback. | Jun 21 2016 | On 20/05/2018: Installation is underway. On 17-12-2018: Factory has informed that installation has been almost completed. Testing and Commissioning is pending. On 18-Apr-21: Factory wanting time extension till 29-Apr-21. Extended timeline not accepted. On 10/10/2021: T&CVI found that the SUPS (fire pump and standpipe) system was not approved. See detailed T&CVI Report. Comments from RCH: On 12-Feb-22: The factory management asked for a timeline up to April-2022 which is not accepted. The corrective action plan should be completed as per the RSC recommendation with immediate concern. Comments from RCH: On 18-May-2022: The factory management asked for a timeline up to 10-Jun-2022 which is not accepted. The corrective action plan should be completed as per the RSC recommendation with immediate concern. On 29/08/2022: T&CVI found that the standpipe system is not approved. See detailed in the T&CVI report. On 30/08/2023: The standpipe system modification work almost completed according to the factory personnel. The factory shall apply for T&CVI. RPO Comments: On 01-FEB-2026 the RSC checked the SUPS systems and identified anomalies. The anomalies need to be remediated and reported by 10-DEC-2025. | Within 3 months | In Progress
Follow Up Inspection |  | 18 | New finding (3rd follow up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Done | Jun 30 2016 | On 21/04/16: New Finding. On 22/06/16: Corrected. Adequate illumination along the means of egress has been provided. On 2-11-2016: Corrected. On 5th January 2017 As action plan of the factory: Corrected as per previous follow-up inspection. On 30-03-17: Corrected. On 11/07/2017: Corrected as per previous follow-up however it is required to increase the number of lights along aisles. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. | within 01 month | Corrected
Follow Up Inspection |  | 19 | New finding (4th follow up): Assembly occupancy (E4) (prayer room) has been found on 1st floor main building adjacent to production. | Relocate the prayer room to a safe place or provide minimum 2 hours fire rated separation between production & prayer room having minimum 2 direct exit access. | Done | Jun 23 2016 | On 22-6-2016: NEW FINDING On 2-11-2016: Factory has informed about not using it as assembly occupancy. However it wasn’t anticipated On 5th January 2017 As action plan of the factory: In Progress. It has found same as it was before follow-up inspection. On 30-03-17: Corrected. Prayer has been removed. On 11/07/2017: Corrected. Factory has removed the prayer room. On 20/05/2018: Corrected On 17-12-2018: Corrected On 30/08/2023: Corrected. | within 02 months | Corrected
Follow Up Inspection |  | 20 | New finding (5th follow up): Unsealed Penetration was found at hazardousmaterials/chemical store. | Seal all penetrations and opening to maintain the fire separation of 2-hr rating. | We have completed the fire door maintenance work by our internal engineering team now fire door at chemical store fully functional. | Nov 17 2016 | NEW FINDING (5th follow-up) On 5th January 2017 As action plan of the factory: In Progress. Factory has sealed the opening and installed the fire rated door but the door was open during inspection. It was not interfaced with FACP. On 30-03-17: Partially corrected. On 11/07/2017: Partially corrected. Penetration was found towards dryer section from chemical store. On 20/05/2018: In progress. Door has not been interfaced yet. On 17-12-2018: Fire door has been installed but interfacing with FACP was not working properly during follow up inspection. On 30/08/2023: During follow up inspection it was observed that installed fire doors with door accessories (door co-ordinator for double leaf door, panic bar, door closer, etc.) were not functional properly in chemical room. RPO Comments: On 30-Nov-2023, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 15 days | Pending Verification
Follow Up Inspection |  | 21 | New Finding in 8th Follow-up: Areas used for combustible storage are not separated by fire-rated construction | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m | We have orgnised the process goods/running goods storage areas as per the inspection recommendation on the 1st floor. | Aug 11 2017 | New Finding On 20/05/2018: Same as before On 17-12-2018: Corrected. On 30/08/2023: Issue re-open. During follow up inspection it was observed that the process goods/running goods storage areas were not organized as per the inspection recommendation on the 1st floor. RPO Comments: On 30-Nov-2023, the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification

## Electrical
Date
03-Feb-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.T.S. Apparels Limited, 414, Kochakuri, Talirchala,, Mouchak,Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-04-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | HT service cable drawn from pole not protected properly. | HT cable drawn from 11kV pole must be encased in steel pipe or rigid PVC pipe of required size and height of at least 2m above from the ground level to protect the cable from physical damage by moving objects. | Done | Jun 16 2014 | Corrected in previous follow-up inspection. | Within 3 Months | Corrected
Initial Inspection |  | 2 | Transformer guarded with wire mesh fencing. | Construct a separate room for the transformer by constructing barrier (brick) walls (fire rated wall) up to the ceiling; the minimum area of the transformer room should be 10-13 sq. m (according to BNBC 2006, Section-2.6.3). | Done | Jul 9 2014 | Corrected in previous follow-up inspection. | Within 3 Months | Corrected
Initial Inspection |  | 3 | Oil leakage seen on the top (through LT bushings) of transformer. | LT cables should be supported in such a way that there will be no strain on the termination point (LT bushing) to avoid further leakage through bushing. Leakage must be checked during maintenance and repaired as soon as possible. | Done | Jun 9 2014 | Corrected in previous follow-up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 4 | Cable terminated to changeover switch and distribution panel not supported. | Provide covered cable ladder or perforated cable tray to support cables terminated to/from Changeover switch and distribution panel. | Done | Jan 15 2015 | Corrected in previous follow-up inspection. | Within 3 Months | Corrected
Initial Inspection |  | 5 | Wooden switch board mounted on wall and protective devices not encased properly. | Wooden switchboard should be replaced by proper switchboard. Protective devices should be encased in metal casing made of 20 SWG thickness metal sheets. | Done | Jun 12 2014 | Corrected in previous follow-up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 6 | Oil cup below transformer breather kept empty. | Breather oil cup must be filled with transformer oil to the required level as instructed by the manufacturer. | Done | Jan 15 2015 | Corrected in previous follow-up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 7 | Cables carried on cable ladder not properly arranged. | Cables must be aligned and dressed on the cable ladder. Put tags on the cables for easy identification and maintenance. | Done | Jan 15 2015 | Corrected in previous follow-up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 8 | Uncovered cable channels found full of dust and lint deposit inside it. | Clean all the cable channels and put metallic cover on it to make it dust and vermin proof. Establish a routine cleaning program to keep the cable channels neat and clean to void fire hazard. | Done | Jan 15 2015 | Corrected in previous follow-up inspection. | Within 1 Month | Corrected
Initial Inspection |  | 9 | HT Cables drawn from 11kV overhead line not supported firmly to the pole. | HT cable drawn from the 11kV pole must be firmly fixed to the pole with saddle clamps. | Done | Jun 10 2014 | Corrected in previous follow-up inspection. | Within 3 Months | Corrected
Initial Inspection |  | 10 | Cables encased in flexible pipes not protected fully. | Use rigid PVC pipe for surface and exposed wiring throughout its whole length and support them at regular intervals. Use flexible pipe at the bending point only where it is unable to bend the rigid pipe by suitable fittings. | Done | Jan 15 2015 | Corrected in previous follow-up inspection. | Within 1 Month | Corrected
Follow Up Inspection |  | 11 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | Done | May 31 2016 | On 21/04/2016: Inadequate earth size is observed at inspection time. So, this issue is not corrected. New committed timeline is given till 31/05/2016. On 22/06/2016: Not Corrected. On 02/11/2016: Not Corrected. On 05/01/2017: Not Corrected. On 30/03/2017: Not corrected. On 11/07/2017: Not corrected. On 25/10/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 12 | New Finding: MCCBs are not adjusted accordingly. | Adjust all the MCCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Done | May 31 2016 | On 21-04-2016: At inspection time oversized breaker observed. So, this issue not corrected. New committed timeline is given till 31-05-2016. On 22/06/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Done | May 31 2016 | ON 05/10/2017 Factory asked for extended timeline till: 30.10.2017. Timeline extension request is not accepted. On 21/04/2016: SLD has been submitted at Alliance for review. This issue not corrected yet. New committed timeline is given till 31-05-2016. On 22/06/2016: Not Corrected. SLD is not as built. On 02/11/2016: Not Corrected. On 05/01/2017: Not Corrected. On 30/03/2017: Not corrected. On 11/07/2017: Not corrected. On 25/10/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Battery kept on concrete floor. | Use non-flammable case/shelf to store battery. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 15 | New Finding: Cables within flexible conduit laid on floor. | Use a cable tray to ensure adequate support. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Cable without appropriate support. | Provide covered cable ladder or perforated cable tray to support cables. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Cables passing through wall/ floor slab are not protected at the entry/ exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. | Done | Jan 30 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Motor/Pumps are not fixed with base. Motor/Pumps are not earthed properly. | Fix motor/pump with base permanently. Ensure earthing connection for all motor/pumps coil and body. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Panel/ Distribution boxes are inaccessible or can not be opened to perform any maintenance work. | Take necessary initiative thus every panel/ distribution board can be easily accessible. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: Inflammable materials stacked adjacent to electrical panel/ distribution board/ installations. | Inflammable materials must be stacked maintaining a safer (1.5 m apart ) clearance from any electrical installation. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Panel board not fixed at base permanently. | Fix panel at base permanently by nut and bolt. | Done | Jan 20 2016 | Corrected in previous follow-up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 22 | New Finding: Water on floor near to panel board. | Distribution/panel board must be installed at least 2.5 meter away from water tank/sink/ washing unit. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Distribution board/panel is filled with fluffs (lint/dust). | Keep always clean inside all the distribution boards/panels. Seal them properly and ensure adequate ventilation. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Oil level in transformer oil tank is below minimum level. | Ensure minimum oil level in the oil level tank. Check this level periodically. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Neutral wiring done through circuit breaker. | Remove all switch/fuse unit for neutral wiring. Neutral wire must be connected to neutral busbar without any interruption. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Transformer Silica gel is discolored. | Replace silica gel by a new one; or dry it under sun and reuse it, if color regains. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Multiple cables terminated at MCCB terminals/ Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. Multiple cables termination is allowed if all are soldered properly and powering to a single circuit. | Done | Jan 10 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 28 | New Finding: Cables terminated at electrical bus bar/MCCB without cable lugs. | Terminate all the power/earth/neutral cable with proper sized cable lug. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 2 Months | Corrected
Follow Up Inspection |  | 30 | New Finding: Electrical devices installed on inflammable material. | Remove inflammable material and fix all electrical devices on metal base. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Burnt sign observed at breaker's terminal. | Check and replace the burnt breaker. Use single cable for single point termination. | Done | Feb 5 2016 | On 21-04-2016: Although this issue is corrected at 2nd follow-up but burning sign observed at inspection time. So, this issue is not corrected. Need to take immediate action. On 22/06/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Uncovered light inside storage area. | Provide fire rated light cover for lighting fixture inside storage area. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Lightning protections system (LPS) is inadequate for the factory. | Redesign/modify LPS for your factory to increase safety; Factory have to submit LPS design to Accord before starting. | Done | Jun 21 2016 | On 21-04-2016: Factory has LPS drawing but need some changes. Installation process is going on. Need to follow NFPA 780. New committed timeline is given till 21-06-2016. On 22/06/2016: Not Corrected. Drawing need some modification. On 02/11/2016 Not Corrected. On 05/01/2017: Not Corrected. On 30/03/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Earthing for the factory is not at satisfactory level. | Take action to increase earthing protection and keep earth resistance value below 1 ohm. | Done | Jan 14 2016 | Corrected in previous follow-up inspection. | 3 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test. Do it twice in a year and keep the record. | Done | Jan 31 2016 | Corrected in previous follow-up inspection. | 3 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: Hot spots at terminations inside panel. | Find the cause of excessive heat-rise which may be the overloading, loose connection, unbalanced load and others and take action immediately. Thermo graphic scanning for the entire electrical system must be performed on a bi-annual basis and recorded. | Done | May 10 2016 | On 21/04/2016: At inspection time hot spot observed. This issue not corrected. New committed timeline is given till 10-05-2016. On 22/06/2016: Not Corrected. On 02/11/2016: Not Corrected. Hotspots were found inside maximum distribution board. On 05/01/2017: Not corrected. On 30/03/2017: Not corrected. On 11/07/2017: Not corrected. On 25/10/2017: Corrected. Not found this time. | Immediately | Corrected
Follow Up Inspection |  | 37 | New Finding: Insulation resistance test of electrical cable is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Done | May 21 2016 | On 05/01/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Higher rated circuit breakers with lower rated electric cable. | Consult with a qualified electric engineer and ensure electric cables are sized according to capacity of circuit breakers. | Done | Feb 10 2017 | On 05/01/2017: Not Corrected. New timeline is till 10/02/2017. On 30/03/2017: Not corrected. On 11/07/2017: Not corrected. On 25/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Burning sign is seen at the terminal. | Need to check the connected load, check the thermal issue. But need to replace the burnt cable and lugs immediately. | Done | Feb 10 2017 | On 05/01/2017: Not Corrected. New timeline is till 10/02/2017. On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Cables are service are joint (splicing) between terminations. | Existing cables with joints must be spliced using but splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Done | Feb 10 2017 | On 05/01/2017: Not Corrected. New timeline is till 10/02/2017. On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Light in store room/ storage area is uncovered. | Light in store room/storage areas shall be covered. | Done | Dec 15 2016 | On 05/01/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Motor body and metal enclosure has no earth connection. | Ensure earth connection for motor frame and metal enclosures. | Done | Dec 15 2016 | On 05/01/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Inadequate earth cable size connected to generator frame. | Two separate and distinct earth connection must be provided over generator. Generator body must have earth connection with half of phase conductor. | Done | Feb 10 2017 | On 05/01/2017: Not Corrected. 2 earth pits used for 08 generators. Number of earth pits shall be in accordance of system requirement. New timeline is till 10/02/2017. On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Cables are laid on concrete floor inside cable tranches. | cables must be supported on cable ladder and riser with following standard cable laying technique. Cables may be laid in cable trench with covers. | Done | Feb 10 2017 | On 05/01/2017: Not Corrected. New timeline is till 10/02/2017. On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Done | Feb 10 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Outdoor Cable trays are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Done | May 10 2017 | On 30/03/2017: Not Corrected. New timeline is till 10/05/2017. On 11/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Done | Feb 10 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Wiring or extensions to connect equipment/ devices are laid on floors unprotected in flexible PVC. | The cable connection to machines/equipment may be run under the checkered plates (existing) and in trenches or steel conduits. Other options may be to use cable trays and supports to protect from external damages. | Done | Feb 10 2017 | On 30/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Number of earth pits are inadequate for the factory. | Adequate number of earth pits must be ensured for the factory with proper earth lead and earth electrode size as mentioned in BNBC requirements. mixing all together shall be avoided. | Done | Sep 21 2017 | On 05/10/2017 Factory asked for extended timeline till: 30.10.2017. Timeline extension request is not accepted. Issue raised as factory has only 7 tested earth pits for 6 Generators, 1 Transformer and system. On 25/10/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 50 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. | Done | Dec 15 2017 | On 17/12/2018: Corrected. No such issue was found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. |  | Oct 4 2023 | On 28/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | We have increased the space(1.07m) of Transformer room for performing the maintenance work properly.We have submitted revised drawing with updated information in master layout & transformar room layout to RSC for review & approval.We have taken approval from RSC 17th December 2025. | Nov 4 2023 | On 28/02/2024: Not corrected. No progress has been observed. On 03/08/2025: Not corrected. No progress has been observed since the last follow up. Please send as-built and proposed transformer room layout drawing along with master layout (ground floor) of the factory to RSC for the review purposes. RPO Comments: On 01-FEB-2026 the design documents (Transformer layout) have been reviewed and accepted by RSC. The factory management reported the remediation completion based on the accepted design.This item will be verified in the next inspection. | 2 Months | Pending Verification
Follow Up Inspection |  | 53 | New Finding: MCCBs/MCBs are not installed /adjusted per load demand. | All the MCCBs/MCBs must be installed/adjusted as per connected load current; if adjustment is not possible, replacement will be the only way. | This issue also related with with SLD.We already updated SLD with proper load balance &b submitted updated drawing to RSC on 26th October 2025 for review & approval.We got approval from RSC on 01st November 2025. | Oct 4 2023 | On 28/02/2024: Not corrected. Still oversized MCCB/MCB found. Draw as built electrical SLD mentioning all required information and submit to RSC for review. After that do the remediation as per accepted sld. On 03/08/2025: Not corrected. Around 60% progress found but still oversized breakers found in few panels. RPO Comments: On 02-DEC-2025 the design documents (SLD) have been reviewed and accepted by RSC. The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 54 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | We have been submitted updated drawing of SLD to RSC on 26th October 2025 for review & approval.We got approval from RSC on 01st November 2025. | Apr 14 2024 | On 03/08/2025: Not corrected. Factory has not submitted SLD to RSC for review yet. RPO Comments: On 02-DEC-2025 the design documents (SLD) have been reviewed and accepted by RSC. The factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 55 | New Finding: Transformer Oil Test (dielectric strength test) report is unavailable. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | We have taken updated oil test report from concern authority. | Apr 14 2024 | On 03/08/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all using records. | We already started the LOTO procedure at our factory during work & kept record properly | Apr 14 2024 | On 03/08/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: No access to the electrical/control room of the lift poses a fall hazard. | The maintenance and operation area must be free of obstacles and all fall hazards. The floor should be even, and all trench covers must be aligned with the floor level to prevent injuries from uneven heights. | We have covered all open power cable and all trench to aligned with the floor level to prevent injuries from uneven heights. | Sep 3 2025 | RPO Comments: On 01-FEB-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification

## Boiler
Date
03-Feb-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | A.T.S. Apparels Limited, 414, Kochakuri, Talirchala,, Mouchak,Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2022-02-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 3873 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We already installed emergeny stop push switch on the boiler control panel. | Dec 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 7750 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | We already installed emergeny stop push switch on the boiler control panel. | Dec 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 3873 | Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have installed measurement scale in cap mentioned areas. | Dec 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 7750 | Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We have installed measurement scale in cap mentioned areas. | Dec 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 3873 | Necessary technical documents manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | The boiler was installed on 2005 on that time we don’t have any supplier information & manufacturing drawings & calculations like Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation etc report.We had tried to collect it from govt. authority but they have no authority to provide such type of documents to us.However we are trying to collect it. | Jan 30 2025 | Comments on 4-Dec-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments: On 01-FEB-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 6 | BB 5082 | Necessary technical documents manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | This boiler currently is not operatonal due to our factory current working situation .We already informed to Boiler office & taken written approval from them.Documents enclosed for review. | Jan 30 2025 | Comments on 4-Dec-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments: On 02-DEC-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 7750 | Necessary technical documents manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already collected all documents for mentioned boiler. | Jan 30 2025 | Comments on 4-Dec-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments: On 02-DEC-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 3873 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | We have collected Initial certificate from concern authority. | Jan 30 2025 | Comments on 4-Dec-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments: On 01-FEB-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 5082 | Boiler's initial registration certificate was not available on-site during the inspection. | Boiler registration certificate from the government authority which was provided after the installation shall be available on-site during the inspection. | This boiler currently is not operatonal due to our factory current working situation .We already informed to Boiler office & taken written approval from them.Documents enclosed for review. | Jan 30 2025 | Comments on 4-Dec-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments: On 01-FEB-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 3873 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | We have installed safety valve outside the boiler room with proper drainage system. | Nov 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 3873 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. | we have used treated feed water to the boiler before using. | Dec 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 3873 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Boiler gas pipeline properly insulated in side the boiler room. | Nov 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 7750 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | We don’t have any fuel line connection. | Oct 30 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Functional test inspection | 14 | BB 5082 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We will installed steam pressure limit switch at boiler. | Nov 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 15 | BB 3873 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We will installed steam pressure limit switch at boiler. | Nov 15 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 16 | BB 7750 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We already installed water level tripping mechanism at boiler. | Oct 22 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 17 | BB 3873 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler. | The Low Low Water (LLW) level tripping mechanism should be functional. | We already installed water level tripping mechanism at boiler. | Oct 22 2024 | Comments on 4-Dec-24: Will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification